## Cover
Turbine & Gross AEP
Calculator: HybridAEP — Turbine & AEP
Generated: 2026-09-18T20:25:01+00:00 UTC
Purpose
• | Convert the calibrated multi-year 100 m wind resource to turbine hub height, apply a supplied turbine power curve hour by hour, and calculate gross annual energy yield before wake and other losses.
Input data
• | Long-term Wind Resource job #8, linked to the complete calibrated multi-year hourly series.
• | Turbine: Nordex N163/5.X Mode 0, rated 5.700 MW, rotor 163.0 m, hub height 125.0 m.
• | Turbine count: 15; farm rated power: 85.500 MW.
• | Power curve source: Built-in digitized preset: Nordex N163/5.X - Mode 0 - 5.7 MW - HH125 - rho 1.225 ¦ 2001493EN / F008_276_A12_EN Rev. 12 (2024-10-09) ¦ rho=1.225 kg/m3.
• | Ct curve source: Built-in digitized preset: Nordex N163/5.X - Mode 0 - 5.7 MW - HH125 - rho 1.225 ¦ 2001493EN / F008_276_A12_EN Rev. 12 (2024-10-09) ¦ rho=1.225 kg/m3.
• | Built-in curve air density: 1.225 kg/m3; source 2001493EN / F008_276_A12_EN Rev. 12 (2024-10-09).
Method
• | Automatic ERA5 bulk 10–100 m power law: alpha=ln(V100/V10)/ln(100/10)=0.22971; Vhub = V100 × (HH/100)^alpha. This is a bulk reanalysis-profile fallback, not a local measured shear coefficient.
• | Power is linearly interpolated between supplied power-curve points; wind speeds outside the supplied curve range are assigned zero power.
• | Gross hourly farm power = per-turbine power × turbine count.
• | Annual actual AEP is the sum of hourly gross power. A second annual AEP value is normalized to 8760 hours so leap years do not receive a 24-hour statistical advantage.
• | Energy Representative Year is the historical year whose 8760-normalized gross AEP is closest to the median annual gross AEP.
Workbook outputs
• | Annual_AEP: year-by-year gross AEP and capacity factor for every complete calendar year.
• | Power_Curve and optional Ct_Curve: normalized curve tables used by the calculation.
• | Selected_Hourly: chronological gross generation for the selected downstream simulation year.
• | Full multi-year gross generation and the selected-year generation are also retained as compressed CSV datasets on the VPS.
Limitations / use
• | Gross AEP only: no wake loss, electrical loss, availability loss, curtailment, icing, high-wind hysteresis, degradation or other project losses are included.
• | Hub-height conversion uses an explicit power law. The automatic ERA5 alpha is a bulk 10–100 m reanalysis-profile estimate, not a local measured shear coefficient.
• | For HH125, a local profile close to hub height (for example simultaneous 100/150 m mast or LiDAR data) is preferred when available.
• | ERA5 100 m is reanalysis/model data and must not be described as a measurement mast.
• | The historical AEP 10th percentile is shown as a resource-only P90-exceedance proxy; it is not a bankable P90 because model, measurement and loss uncertainties are not included.
• | Power/Ct curve validity depends on the source. OEM/project-specific curves are preferred.
• | The current built-in Nordex preset uses the fixed 1.225 kg/m3 table; hourly air-density correction is not yet applied.
• | For the Nordex preset, document rows from 20.5 to 26.0 m/s are marked as yield/load optimized operation that may not be feasible at all sites.
References
PyWake | https://topfarm.pages.windenergy.dtu.dk/PyWake/
FLORIS | https://nrel.github.io/floris/

## Inputs
Parameter | Value
project_name | Zhytomyr_Vysoke_WPP2
longterm_job_id | 8
turbine_preset_id | nordex_n163_5x_mode0_hh125_rho1225
manufacturer | Nordex
turbine_model | N163/5.X Mode 0
rated_power_kw | 5700
rotor_diameter_m | 163
hub_height_m | 125
turbine_count | 15
shear_method | era5_bulk_10_100
power_curve_text
ct_curve_text
simulation_year | auto_aep

## Summary
Parameter | Value
result_schema_version | 1
project_name | Zhytomyr_Vysoke_WPP2
turbine_preset_id | nordex_n163_5x_mode0_hh125_rho1225
turbine_preset_source_document | 2001493EN / F008_276_A12_EN Rev. 12 (2024-10-09)
fixed_curve_air_density_kg_m3 | 1.225
source_longterm_job_id | 8
source_calibration_job_id | 7
source_period | 2006-2025
manufacturer | Nordex
turbine_model | N163/5.X Mode 0
rated_power_kw | 5700
rotor_diameter_m | 163
hub_height_m | 125
turbine_count | 15
farm_rated_power_mw | 85.5
shear_method | era5_bulk_10_100
shear_alpha | 0.22971
shear_profile_source | ERA5 job #6 bulk mean profile 10–100 m (V10=3.454 m/s, V100=5.861 m/s)
era5_profile_job_id | 6
era5_profile_v10_mps | 3.4535
era5_profile_v100_mps | 5.861
hub_height_factor_from_100m | 1.0526
power_curve_source | Built-in digitized preset: Nordex N163/5.X - Mode 0 - 5.7 MW - HH125 - rho 1.225 ¦ 2001493EN / F008_276_A12_EN Rev. 12 (2024-10-09) ¦ rho=1.225 kg/m3
power_curve_peak_kw | 5700
ct_curve_source | Built-in digitized preset: Nordex N163/5.X - Mode 0 - 5.7 MW - HH125 - rho 1.225 ¦ 2001493EN / F008_276_A12_EN Rev. 12 (2024-10-09) ¦ rho=1.225 kg/m3
complete_aep_years | 20
first_year | 2006
last_year | 2025
mean_gross_aep_8760_gwh | 237.3542
median_gross_aep_8760_gwh | 239.2832
annual_gross_aep_10th_percentile_gwh | 214.8573
annual_gross_aep_90th_percentile_gwh | 255.6551
resource_only_p90_exceedance_proxy_gwh | 214.8573
resource_only_p50_exceedance_proxy_gwh | 239.2832
interannual_gross_aep_variability_pct | 7.4605
energy_representative_year | 2020
wind_representative_year | 2020
selected_simulation_year | 2020
selected_simulation_year_reason | Auto: historical year with 8760-normalized gross AEP closest to the median.
selected_year_gross_aep_gwh | 238.8801
selected_year_gross_capacity_factor_pct | 31.8069
power_curve_path | /data/results/turbine/Zhytomyr_Vysoke_WPP2__Turbine_AEP__job000010__power_curve.csv
ct_curve_path | /data/results/turbine/Zhytomyr_Vysoke_WPP2__Turbine_AEP__job000010__ct_curve.csv
turbine_definition_path | /data/results/turbine/Zhytomyr_Vysoke_WPP2__Turbine_AEP__job000010__turbine_definition.json
multi_year_generation_path | /data/results/turbine/Zhytomyr_Vysoke_WPP2__Turbine_AEP__job000010__gross_generation_all_years.csv.gz
internal_dataset_path | /data/results/turbine/Zhytomyr_Vysoke_WPP2__Turbine_AEP__job000010__gross_generation_2020.csv.gz
internal_dataset_filename | Zhytomyr_Vysoke_WPP2__Turbine_AEP__job000010__gross_generation_2020.csv.gz
source_calibrated_dataset_filename | Zhytomyr_Vysoke_WPP2__Hourly_Wind_Speed_Calibration__job000007__hourly_calibrated.csv.gz

## Power_Curve
wind_speed_mps | power_kw
3 | 48
3.5 | 155
4 | 298
4.5 | 474
5 | 685
5.5 | 936
6 | 1232
6.5 | 1582
7 | 1988
7.5 | 2454
8 | 2983
8.5 | 3546
9 | 4110
9.5 | 4645
10 | 5056
10.5 | 5348
11 | 5539
11.5 | 5652
12 | 5699
12.5 | 5700
13 | 5700
13.5 | 5700
14 | 5700
14.5 | 5700
15 | 5700
15.5 | 5700
16 | 5700
16.5 | 5700
17 | 5700
17.5 | 5700
18 | 5700
18.5 | 5700
19 | 5700
19.5 | 5700
20 | 5700
20.5 | 5586
21 | 5455
21.5 | 5307
22 | 5153
22.5 | 5005
23 | 4856
23.5 | 4708
24 | 4560
24.5 | 4418
25 | 4269
25.5 | 4121
26 | 3973

## Ct_Curve
wind_speed_mps | ct
3 | 0.875
3.5 | 0.867
4 | 0.847
4.5 | 0.83
5 | 0.819
5.5 | 0.813
6 | 0.809
6.5 | 0.807
7 | 0.806
7.5 | 0.797
8 | 0.774
8.5 | 0.743
9 | 0.7
9.5 | 0.651
10 | 0.599
10.5 | 0.547
11 | 0.495
11.5 | 0.445
12 | 0.397
12.5 | 0.353
13 | 0.313
13.5 | 0.279
14 | 0.248
14.5 | 0.22
15 | 0.197
15.5 | 0.178
16 | 0.161
16.5 | 0.147
17 | 0.135
17.5 | 0.125
18 | 0.116
18.5 | 0.109
19 | 0.103
19.5 | 0.098
20 | 0.093
20.5 | 0.086
21 | 0.078
21.5 | 0.071
22 | 0.065
22.5 | 0.059
23 | 0.054
23.5 | 0.049
24 | 0.046
24.5 | 0.042
25 | 0.039
25.5 | 0.036
26 | 0.033

## Annual_AEP
year | hours | mean_ws_100m_mps | mean_hub_ws_mps | gross_aep_actual_gwh | gross_aep_8760_equivalent_gwh | gross_capacity_factor_pct
2006 | 8760 | 5.6827 | 5.9816 | 222.2915 | 222.2915 | 29.6792
2007 | 8760 | 6.0202 | 6.3368 | 253.4214 | 253.4214 | 33.8355
2008 | 8784 | 6.1623 | 6.4864 | 261.0634 | 260.3501 | 34.7606
2009 | 8760 | 5.5876 | 5.8815 | 213.5451 | 213.5451 | 28.5115
2010 | 8760 | 5.696 | 5.9956 | 225.7415 | 225.7415 | 30.1399
2011 | 8760 | 5.6664 | 5.9644 | 215.0031 | 215.0031 | 28.7061
2012 | 8784 | 5.7878 | 6.0922 | 230.9525 | 230.3215 | 30.7514
2013 | 8760 | 5.8829 | 6.1923 | 241.4792 | 241.4792 | 32.2411
2014 | 8760 | 5.6475 | 5.9445 | 217.1236 | 217.1236 | 28.9892
2015 | 8760 | 5.9591 | 6.2725 | 247.9544 | 247.9544 | 33.1056
2016 | 8784 | 5.9256 | 6.2372 | 245.3214 | 244.6512 | 32.6646
2017 | 8760 | 6.2627 | 6.5921 | 274.4623 | 274.4623 | 36.6448
2018 | 8760 | 5.5772 | 5.8706 | 207.2439 | 207.2439 | 27.6702
2019 | 8760 | 5.9538 | 6.267 | 247.7967 | 247.7967 | 33.0846
2020 | 8784 | 5.8562 | 6.1643 | 238.8801 | 238.2275 | 31.8069
2021 | 8760 | 5.7399 | 6.0418 | 224.3954 | 224.3954 | 29.9601
2022 | 8760 | 6.1029 | 6.4238 | 255.1335 | 255.1335 | 34.0641
2023 | 8760 | 6.0052 | 6.321 | 251.915 | 251.915 | 33.6344
2024 | 8784 | 5.843 | 6.1504 | 236.3351 | 235.6893 | 31.468
2025 | 8760 | 5.8599 | 6.1681 | 240.3389 | 240.3389 | 32.0888

## Selected_Hourly
timestamp_utc | wind_speed_100m_mps | hub_height_wind_speed_mps | wind_direction_100m_deg | per_turbine_gross_power_kw | farm_gross_power_kw
2020-01-01 00:00 | 11.8305 | 12.4527 | 306.978 | 5699.9054 | 85498.5807
2020-01-01 01:00 | 11.9603 | 12.5893 | 311.2224 | 5700 | 85500
2020-01-01 02:00 | 11.9608 | 12.5899 | 314.7981 | 5700 | 85500
2020-01-01 03:00 | 12.2514 | 12.8958 | 317.8789 | 5700 | 85500
2020-01-01 04:00 | 12.3082 | 12.9555 | 321.142 | 5700 | 85500
2020-01-01 05:00 | 12.008 | 12.6395 | 324.3786 | 5700 | 85500
2020-01-01 06:00 | 11.5569 | 12.1648 | 329.2677 | 5699.3296 | 85489.9435
2020-01-01 07:00 | 11.2389 | 11.83 | 330.9978 | 5683.018 | 85245.2698
2020-01-01 08:00 | 11.2017 | 11.7909 | 330.0414 | 5679.3433 | 85190.1502
2020-01-01 09:00 | 10.7223 | 11.2863 | 329.52 | 5603.6927 | 84055.3908
2020-01-01 10:00 | 10.4983 | 11.0504 | 325.8394 | 5550.3971 | 83255.9563
2020-01-01 11:00 | 10.1527 | 10.6867 | 325.7815 | 5419.3276 | 81289.9141
2020-01-01 12:00 | 9.8424 | 10.36 | 326.5805 | 5266.2672 | 78994.0087
2020-01-01 13:00 | 9.5669 | 10.0701 | 328.6624 | 5096.9448 | 76454.1715
2020-01-01 14:00 | 8.7323 | 9.1916 | 330.1623 | 4315.0269 | 64725.4035
2020-01-01 15:00 | 8.5324 | 8.9812 | 325.479 | 4088.7374 | 61331.0609
2020-01-01 16:00 | 7.6068 | 8.0069 | 320.6184 | 2990.7335 | 44861.0027
2020-01-01 17:00 | 7.1433 | 7.519 | 317.3021 | 2474.0497 | 37110.7461
2020-01-01 18:00 | 7.0379 | 7.4081 | 313.4929 | 2368.3471 | 35525.2061
2020-01-01 19:00 | 6.4181 | 6.7557 | 301.8849 | 1789.5934 | 26843.9016
2020-01-01 20:00 | 6.6878 | 7.0395 | 292.3159 | 2024.8461 | 30372.6915
2020-01-01 21:00 | 6.9305 | 7.295 | 289.4424 | 2262.9572 | 33944.3579
2020-01-01 22:00 | 6.5821 | 6.9283 | 289.4136 | 1929.7974 | 28946.9605
2020-01-01 23:00 | 6.1154 | 6.4371 | 278.8623 | 1537.9353 | 23069.0291
2020-01-02 00:00 | 6.7835 | 7.1402 | 273.6639 | 2118.7097 | 31780.6451
2020-01-02 01:00 | 7.056 | 7.4271 | 273.952 | 2386.0274 | 35790.4109
2020-01-02 02:00 | 6.7305 | 7.0845 | 274.8051 | 2066.7613 | 31001.4202
2020-01-02 03:00 | 6.4557 | 6.7952 | 274.8517 | 1821.7331 | 27325.9969
2020-01-02 04:00 | 6.4252 | 6.7631 | 275.4854 | 1795.6414 | 26934.6217
2020-01-02 05:00 | 6.4134 | 6.7507 | 275.9959 | 1785.5474 | 26783.211
2020-01-02 06:00 | 6.2275 | 6.555 | 268.4845 | 1626.678 | 24400.1695
2020-01-02 07:00 | 6.4678 | 6.8079 | 267.6134 | 1832.0329 | 27480.4932
2020-01-02 08:00 | 7.1285 | 7.5035 | 269.0054 | 2457.6532 | 36864.7985
2020-01-02 09:00 | 7.7737 | 8.1825 | 279.757 | 3188.5174 | 47827.7615
2020-01-02 10:00 | 7.1608 | 7.5374 | 272.1995 | 2493.5996 | 37403.9939
2020-01-02 11:00 | 6.8131 | 7.1714 | 269.8123 | 2147.7611 | 32216.4167
2020-01-02 12:00 | 6.3929 | 6.7291 | 267.3903 | 1768.0345 | 26520.5177
2020-01-02 13:00 | 6.9965 | 7.3645 | 267.8308 | 2327.6778 | 34915.1663
2020-01-02 14:00 | 7.0687 | 7.4404 | 267.5237 | 2398.4822 | 35977.2326
2020-01-02 15:00 | 7.2556 | 7.6372 | 271.553 | 2599.1235 | 38986.8524
2020-01-02 16:00 | 7.4566 | 7.8487 | 278.2186 | 2822.972 | 42344.5805
2020-01-02 17:00 | 7.7284 | 8.1348 | 283.7373 | 3134.8273 | 47022.4097
2020-01-02 18:00 | 7.8716 | 8.2856 | 289.629 | 3304.6186 | 49569.2791
2020-01-02 19:00 | 7.8505 | 8.2634 | 294.2496 | 3279.6369 | 49194.5532
2020-01-02 20:00 | 7.6829 | 8.087 | 297.5067 | 3080.9483 | 46214.2251
2020-01-02 21:00 | 7.591 | 7.9902 | 297.1502 | 2972.6454 | 44589.6812
2020-01-02 22:00 | 7.4841 | 7.8778 | 297.8772 | 2853.6733 | 42805.0992
2020-01-02 23:00 | 7.3512 | 7.7378 | 300.265 | 2705.6115 | 40584.1724
2020-01-03 00:00 | 7.3226 | 7.7077 | 301.929 | 2673.7594 | 40106.3915
2020-01-03 01:00 | 7.5216 | 7.9172 | 302.402 | 2895.4336 | 43431.5038
2020-01-03 02:00 | 7.7665 | 8.1749 | 304.1315 | 3179.9916 | 47699.8739
2020-01-03 03:00 | 7.8309 | 8.2427 | 307.2052 | 3256.3318 | 48844.9775
2020-01-03 04:00 | 7.6928 | 8.0974 | 308.5232 | 3092.7143 | 46390.7138
2020-01-03 05:00 | 7.3631 | 7.7503 | 308.4815 | 2718.8388 | 40782.5819
2020-01-03 06:00 | 7.0897 | 7.4626 | 307.9591 | 2419.1391 | 36287.0861
2020-01-03 07:00 | 6.6992 | 7.0515 | 308.1295 | 2036.0267 | 30540.4001
2020-01-03 08:00 | 6.2187 | 6.5458 | 305.4886 | 1619.1875 | 24287.8128
2020-01-03 09:00 | 5.6648 | 5.9627 | 301.1812 | 1209.9334 | 18149.0015
2020-01-03 10:00 | 5.0183 | 5.2822 | 303.8325 | 826.6833 | 12400.249
2020-01-03 11:00 | 4.6422 | 4.8863 | 299.367 | 637.0314 | 9555.4716
2020-01-03 12:00 | 4.9001 | 5.1579 | 294.0501 | 764.2488 | 11463.7314
2020-01-03 13:00 | 5.6181 | 5.9135 | 289.7729 | 1180.8114 | 17712.1716
2020-01-03 14:00 | 6.3028 | 6.6342 | 288.6342 | 1691.0071 | 25365.1065
2020-01-03 15:00 | 6.6054 | 6.9528 | 283.8835 | 1949.6837 | 29245.2561
2020-01-03 16:00 | 6.6216 | 6.9699 | 276.897 | 1963.5273 | 29452.9094
2020-01-03 17:00 | 6.8819 | 7.2439 | 271.3502 | 2215.2693 | 33229.0392
2020-01-03 18:00 | 7.5433 | 7.94 | 271.0371 | 2919.5466 | 43793.199
2020-01-03 19:00 | 7.9211 | 8.3377 | 274.1658 | 3363.2089 | 50448.1342
2020-01-03 20:00 | 7.5301 | 7.9261 | 274.9927 | 2904.8553 | 43572.829
2020-01-03 21:00 | 7.7745 | 8.1833 | 277.258 | 3189.4487 | 47841.7309
2020-01-03 22:00 | 7.7491 | 8.1566 | 277.2158 | 3159.3456 | 47390.1839
2020-01-03 23:00 | 7.5064 | 7.9012 | 276.914 | 2878.4643 | 43176.9651
2020-01-04 00:00 | 7.54 | 7.9366 | 275.6318 | 2915.8801 | 43738.2011
2020-01-04 01:00 | 7.3308 | 7.7164 | 272.8037 | 2682.9567 | 40244.3511
2020-01-04 02:00 | 7.1661 | 7.543 | 266.1571 | 2499.5337 | 37493.005
2020-01-04 03:00 | 7.6797 | 8.0836 | 261.5973 | 3077.1442 | 46157.1626
2020-01-04 04:00 | 7.6512 | 8.0537 | 260.5532 | 3043.4245 | 45651.3677
2020-01-04 05:00 | 7.5449 | 7.9417 | 256.3649 | 2921.3062 | 43819.5929
2020-01-04 06:00 | 8.2481 | 8.6819 | 257.2374 | 3751.217 | 56268.2543
2020-01-04 07:00 | 8.5342 | 8.9831 | 260.3125 | 4090.8849 | 61363.2729
2020-01-04 08:00 | 8.6051 | 9.0576 | 260.7813 | 4171.6846 | 62575.2694
2020-01-04 09:00 | 8.9113 | 9.3799 | 261.915 | 4516.5305 | 67747.957
2020-01-04 10:00 | 8.5149 | 8.9627 | 268.5424 | 4067.9337 | 61019.0056
2020-01-04 11:00 | 8.7323 | 9.1916 | 268.552 | 4315.0117 | 64725.1751
2020-01-04 12:00 | 8.7969 | 9.2595 | 273.1234 | 4387.7007 | 65815.5106
2020-01-04 13:00 | 8.5922 | 9.0441 | 278.6368 | 4157.1752 | 62357.6284
2020-01-04 14:00 | 7.838 | 8.2502 | 280.9335 | 3264.7282 | 48970.9237
2020-01-04 15:00 | 7.6004 | 8.0002 | 284.0491 | 2983.2013 | 44748.0189
2020-01-04 16:00 | 7.4234 | 7.8138 | 286.182 | 2786.0078 | 41790.1168
2020-01-04 17:00 | 7.2621 | 7.644 | 286.1718 | 2606.3875 | 39095.8119
2020-01-04 18:00 | 7.0553 | 7.4264 | 283.023 | 2385.4121 | 35781.181
2020-01-04 19:00 | 7.155 | 7.5313 | 282.1916 | 2487.1022 | 37306.5336
2020-01-04 20:00 | 7.0349 | 7.4049 | 286.3677 | 2365.4019 | 35481.028
2020-01-04 21:00 | 6.5128 | 6.8554 | 287.8991 | 1870.5454 | 28058.1808
2020-01-04 22:00 | 5.8667 | 6.1753 | 289.5418 | 1354.7017 | 20320.526
2020-01-04 23:00 | 4.8645 | 5.1203 | 277.368 | 745.3933 | 11180.8994
2020-01-05 00:00 | 5.1388 | 5.409 | 266.1158 | 890.34 | 13355.0994
2020-01-05 01:00 | 5.1513 | 5.4222 | 260.7392 | 896.9568 | 13454.3523
2020-01-05 02:00 | 4.9415 | 5.2014 | 254.1056 | 786.1269 | 11791.9031
2020-01-05 03:00 | 4.8014 | 5.0539 | 249.2391 | 712.0747 | 10681.1202
2020-01-05 04:00 | 4.4738 | 4.7091 | 246.316 | 562.2356 | 8433.5347
2020-01-05 05:00 | 3.6793 | 3.8728 | 240.8627 | 261.6112 | 3924.1683
2020-01-05 06:00 | 3.0064 | 3.1645 | 240.3341 | 83.2063 | 1248.0951
2020-01-05 07:00 | 2.5991 | 2.7358 | 252.6075 | 0 | 0
2020-01-05 08:00 | 2.1539 | 2.2671 | 285.3765 | 0 | 0
2020-01-05 09:00 | 2.4884 | 2.6193 | 327.6624 | 0 | 0
2020-01-05 10:00 | 2.3676 | 2.4921 | 12.7089 | 0 | 0
2020-01-05 11:00 | 2.331 | 2.4536 | 16.4577 | 0 | 0
2020-01-05 12:00 | 2.9692 | 3.1254 | 13.5706 | 74.8283 | 1122.4243
2020-01-05 13:00 | 4.4707 | 4.7058 | 7.738 | 560.8428 | 8412.6422
2020-01-05 14:00 | 6.4399 | 6.7787 | 10.7744 | 1808.267 | 27124.005
2020-01-05 15:00 | 7.3978 | 7.7869 | 10.9564 | 2757.4905 | 41362.3578
2020-01-05 16:00 | 8.0288 | 8.4511 | 6.2593 | 3490.912 | 52363.6796
2020-01-05 17:00 | 8.2987 | 8.7351 | 1.4285 | 3811.2221 | 57168.331
2020-01-05 18:00 | 8.2273 | 8.66 | 358.7254 | 3726.4585 | 55896.8777
2020-01-05 19:00 | 8.1243 | 8.5516 | 356.7484 | 3604.218 | 54063.2695
2020-01-05 20:00 | 8.0006 | 8.4214 | 355.3356 | 3457.4873 | 51862.3093
2020-01-05 21:00 | 7.7686 | 8.1772 | 353.497 | 3182.5438 | 47738.1577
2020-01-05 22:00 | 7.8359 | 8.248 | 347.1559 | 3262.2566 | 48933.8491
2020-01-05 23:00 | 7.5779 | 7.9765 | 347.0211 | 2958.1294 | 44371.9409
2020-01-06 00:00 | 7.3993 | 7.7885 | 344.9354 | 2759.2211 | 41388.3172
2020-01-06 01:00 | 6.7728 | 7.1291 | 344.1041 | 2108.28 | 31624.1998
2020-01-06 02:00 | 6.312 | 6.644 | 342.772 | 1698.9145 | 25483.7172
2020-01-06 03:00 | 5.9699 | 6.2839 | 340.1425 | 1430.7517 | 21461.2757
2020-01-06 04:00 | 6.0098 | 6.3258 | 336.392 | 1460.0922 | 21901.383
2020-01-06 05:00 | 5.645 | 5.9419 | 333.1621 | 1197.5876 | 17963.8135
2020-01-06 06:00 | 5.0601 | 5.3262 | 330.8498 | 848.7719 | 12731.5791
2020-01-06 07:00 | 4.5986 | 4.8404 | 325.5832 | 617.6607 | 9264.9109
2020-01-06 08:00 | 4.4984 | 4.735 | 328.4265 | 573.1701 | 8597.5508
2020-01-06 09:00 | 3.7967 | 3.9964 | 325.956 | 296.9574 | 4454.3608
2020-01-06 10:00 | 3.522 | 3.7072 | 306.1767 | 214.2577 | 3213.8659
2020-01-06 11:00 | 4.5582 | 4.798 | 303.6352 | 599.7385 | 8996.0773
2020-01-06 12:00 | 4.8076 | 5.0604 | 305.1129 | 715.3435 | 10730.1519
2020-01-06 13:00 | 4.5595 | 4.7993 | 305.4342 | 600.315 | 9004.7244
2020-01-06 14:00 | 3.9264 | 4.1329 | 303.3498 | 344.7661 | 5171.491
2020-01-06 15:00 | 3.5603 | 3.7475 | 299.6774 | 225.7974 | 3386.9603
2020-01-06 16:00 | 3.4349 | 3.6156 | 294.7406 | 188.0531 | 2820.7965
2020-01-06 17:00 | 3.6848 | 3.8786 | 285.8896 | 263.289 | 3949.3346
2020-01-06 18:00 | 4.0593 | 4.2727 | 277.4293 | 394.0075 | 5910.1123
2020-01-06 19:00 | 4.2371 | 4.4599 | 274.7042 | 459.8953 | 6898.4289
2020-01-06 20:00 | 4.184 | 4.4041 | 276.1178 | 440.2391 | 6603.5865
2020-01-06 21:00 | 4.0176 | 4.2289 | 272.3833 | 378.5647 | 5678.4706
2020-01-06 22:00 | 4.6877 | 4.9342 | 274.9305 | 657.2368 | 9858.552
2020-01-06 23:00 | 4.5094 | 4.7466 | 270.1047 | 578.0693 | 8671.0392
2020-01-07 00:00 | 4.1304 | 4.3476 | 264.9348 | 420.3636 | 6305.4542
2020-01-07 01:00 | 3.8748 | 4.0786 | 255.1751 | 325.6777 | 4885.1658
2020-01-07 02:00 | 3.8624 | 4.0655 | 243.7027 | 321.0546 | 4815.8193
2020-01-07 03:00 | 4.028 | 4.2399 | 236.986 | 382.4329 | 5736.4937
2020-01-07 04:00 | 3.8982 | 4.1032 | 232.3877 | 334.3294 | 5014.9406
2020-01-07 05:00 | 3.6961 | 3.8904 | 226.6857 | 266.6675 | 4000.0131
2020-01-07 06:00 | 3.8806 | 4.0847 | 225.0781 | 327.8018 | 4917.0264
2020-01-07 07:00 | 4.1072 | 4.3232 | 226.0434 | 411.7563 | 6176.3449
2020-01-07 08:00 | 3.5955 | 3.7846 | 230.2982 | 236.4063 | 3546.0948
2020-01-07 09:00 | 3.2743 | 3.4465 | 243.7793 | 143.5549 | 2153.3241
2020-01-07 10:00 | 3.2681 | 3.4399 | 255.5653 | 142.1492 | 2132.2376
2020-01-07 11:00 | 2.8709 | 3.0219 | 266.6712 | 52.6858 | 790.287
2020-01-07 12:00 | 2.4855 | 2.6162 | 275.9348 | 0 | 0
2020-01-07 13:00 | 2.243 | 2.3609 | 284.8987 | 0 | 0
2020-01-07 14:00 | 2.2824 | 2.4024 | 292.8667 | 0 | 0
2020-01-07 15:00 | 2.426 | 2.5535 | 298.646 | 0 | 0
2020-01-07 16:00 | 2.4568 | 2.586 | 304.8035 | 0 | 0
2020-01-07 17:00 | 2.331 | 2.4536 | 307.3514 | 0 | 0
2020-01-07 18:00 | 1.9465 | 2.0489 | 305.7692 | 0 | 0
2020-01-07 19:00 | 1.7544 | 1.8466 | 300.2671 | 0 | 0
2020-01-07 20:00 | 2.1529 | 2.2662 | 292.4234 | 0 | 0
2020-01-07 21:00 | 2.5486 | 2.6827 | 292.6836 | 0 | 0
2020-01-07 22:00 | 3.6626 | 3.8552 | 288.2358 | 256.597 | 3848.9557
2020-01-07 23:00 | 3.9808 | 4.1902 | 291.5189 | 364.9567 | 5474.3508
2020-01-08 00:00 | 3.469 | 3.6515 | 292.842 | 198.3157 | 2974.7351
2020-01-08 01:00 | 3.0508 | 3.2113 | 283.4509 | 93.2126 | 1398.1896
2020-01-08 02:00 | 2.9913 | 3.1486 | 269.7507 | 79.8026 | 1197.0397
2020-01-08 03:00 | 3.2009 | 3.3692 | 268.4462 | 127.0193 | 1905.2901
2020-01-08 04:00 | 3.4262 | 3.6064 | 266.48 | 185.4173 | 2781.2596
2020-01-08 05:00 | 3.7836 | 3.9825 | 246.5029 | 293.0078 | 4395.1165
2020-01-08 06:00 | 4.5784 | 4.8192 | 228.6996 | 608.6995 | 9130.4918
2020-01-08 07:00 | 5.0019 | 5.265 | 233.8622 | 818.0329 | 12270.4935
2020-01-08 08:00 | 5.0513 | 5.317 | 247.4058 | 844.1179 | 12661.7692
2020-01-08 09:00 | 4.3931 | 4.6241 | 243.678 | 526.3775 | 7895.6618
2020-01-08 10:00 | 4.2771 | 4.5021 | 234.0101 | 474.884 | 7123.2601
2020-01-08 11:00 | 4.5158 | 4.7533 | 236.1875 | 580.8817 | 8713.2248
2020-01-08 12:00 | 4.7132 | 4.9611 | 239.639 | 668.5706 | 10028.559
2020-01-08 13:00 | 5.3985 | 5.6825 | 246.0722 | 1044.0115 | 15660.1729
2020-01-08 14:00 | 6.0975 | 6.4182 | 247.6269 | 1524.7312 | 22870.9677
2020-01-08 15:00 | 6.3985 | 6.735 | 243.8001 | 1772.8183 | 26592.2739
2020-01-08 16:00 | 7.1164 | 7.4907 | 237.0809 | 2445.3586 | 36680.3794
2020-01-08 17:00 | 7.5198 | 7.9153 | 245.1903 | 2893.3765 | 43400.6482
2020-01-08 18:00 | 7.1109 | 7.4849 | 254.9468 | 2439.9158 | 36598.7364
2020-01-08 19:00 | 6.715 | 7.0681 | 248.2224 | 2051.4981 | 30772.4711
2020-01-08 20:00 | 7.0425 | 7.4129 | 240.7472 | 2372.8646 | 35592.9687
2020-01-08 21:00 | 7.3184 | 7.7033 | 243.621 | 2669.0602 | 40035.9025
2020-01-08 22:00 | 7.1176 | 7.4919 | 250.0097 | 2446.4782 | 36697.1732
2020-01-08 23:00 | 7.1977 | 7.5762 | 246.7989 | 2534.6394 | 38019.5912
2020-01-09 00:00 | 7.3904 | 7.7791 | 240.7961 | 2749.271 | 41239.0644
2020-01-09 01:00 | 7.5918 | 7.9911 | 243.6034 | 2973.5481 | 44603.2221
2020-01-09 02:00 | 7.855 | 8.2682 | 252.8852 | 3284.9503 | 49274.2548
2020-01-09 03:00 | 7.6749 | 8.0786 | 254.0241 | 3071.4977 | 46072.4657
2020-01-09 04:00 | 7.6137 | 8.0142 | 263.4646 | 2998.9405 | 44984.1072
2020-01-09 05:00 | 7.0954 | 7.4685 | 262.3015 | 2424.688 | 36370.3201
2020-01-09 06:00 | 7.0312 | 7.401 | 263.2065 | 2361.7283 | 35425.9242
2020-01-09 07:00 | 7.2242 | 7.6042 | 264.3834 | 2564.209 | 38463.1349
2020-01-09 08:00 | 7.0176 | 7.3867 | 273.6694 | 2348.4293 | 35226.4389
2020-01-09 09:00 | 6.859 | 7.2197 | 274.3083 | 2192.8008 | 32892.0124
2020-01-09 10:00 | 6.0807 | 6.4005 | 284.4246 | 1512.3545 | 22685.318
2020-01-09 11:00 | 5.9894 | 6.3044 | 286.5858 | 1445.0549 | 21675.8239
2020-01-09 12:00 | 6.1654 | 6.4897 | 296.123 | 1574.7818 | 23621.727
2020-01-09 13:00 | 5.8626 | 6.1709 | 301.1487 | 1351.6642 | 20274.9625
2020-01-09 14:00 | 5.4711 | 5.7589 | 296.3244 | 1089.2477 | 16338.7154
2020-01-09 15:00 | 5.6205 | 5.9161 | 296.051 | 1182.3083 | 17734.6248
2020-01-09 16:00 | 5.6701 | 5.9683 | 301.3024 | 1213.2196 | 18198.2942
2020-01-09 17:00 | 4.9682 | 5.2295 | 303.7855 | 800.2086 | 12003.1283
2020-01-09 18:00 | 4.0119 | 4.2229 | 304.8379 | 376.4728 | 5647.0924
2020-01-09 19:00 | 3.403 | 3.5819 | 304.9936 | 178.4367 | 2676.5511
2020-01-09 20:00 | 2.621 | 2.7589 | 297.5723 | 0 | 0
2020-01-09 21:00 | 1.8577 | 1.9554 | 273.8206 | 0 | 0
2020-01-09 22:00 | 1.7839 | 1.8777 | 234.8463 | 0 | 0
2020-01-09 23:00 | 2.4747 | 2.6049 | 225.3192 | 0 | 0
2020-01-10 00:00 | 3.0045 | 3.1625 | 209.4258 | 82.783 | 1241.7457
2020-01-10 01:00 | 4.1639 | 4.3829 | 191.4439 | 432.7904 | 6491.856
2020-01-10 02:00 | 5.3135 | 5.593 | 187.177 | 991.0605 | 14865.9071
2020-01-10 03:00 | 5.9438 | 6.2564 | 193.1149 | 1411.5141 | 21172.7112
2020-01-10 04:00 | 6.0517 | 6.3699 | 202.3308 | 1490.9638 | 22364.4575
2020-01-10 05:00 | 6.3814 | 6.717 | 206.8014 | 1758.1957 | 26372.9352
2020-01-10 06:00 | 6.5368 | 6.8806 | 210.8056 | 1891.0267 | 28365.4006
2020-01-10 07:00 | 6.8534 | 7.2138 | 213.9365 | 2187.2632 | 32808.9482
2020-01-10 08:00 | 7.1566 | 7.533 | 218.1016 | 2488.9299 | 37333.9487
2020-01-10 09:00 | 7.0156 | 7.3846 | 224.1366 | 2346.4383 | 35196.5748
2020-01-10 10:00 | 6.0518 | 6.3701 | 221.942 | 1491.0675 | 22366.013
2020-01-10 11:00 | 5.9741 | 6.2883 | 224.981 | 1433.8226 | 21507.3384
2020-01-10 12:00 | 6.0012 | 6.3168 | 229.8181 | 1453.7642 | 21806.4624
2020-01-10 13:00 | 5.8512 | 6.159 | 236.1811 | 1343.267 | 20149.0056
2020-01-10 14:00 | 5.7025 | 6.0024 | 243.3641 | 1233.7019 | 18505.5287
2020-01-10 15:00 | 5.7719 | 6.0755 | 247.1542 | 1284.8505 | 19272.7575
2020-01-10 16:00 | 5.7901 | 6.0946 | 251.0636 | 1298.2221 | 19473.3319
2020-01-10 17:00 | 5.9398 | 6.2522 | 254.0985 | 1408.5411 | 21128.1169
2020-01-10 18:00 | 6.092 | 6.4124 | 255.9133 | 1520.7146 | 22810.7191
2020-01-10 19:00 | 6.5957 | 6.9426 | 256.4593 | 1941.3943 | 29120.9142
2020-01-10 20:00 | 7.2431 | 7.624 | 258.5364 | 2585.2353 | 38778.5296
2020-01-10 21:00 | 7.5885 | 7.9877 | 262.0297 | 2969.9503 | 44549.255
2020-01-10 22:00 | 7.8905 | 8.3055 | 268.185 | 3327.0019 | 49905.0278
2020-01-10 23:00 | 8.3306 | 8.7687 | 269.173 | 3849.1022 | 57736.5332
2020-01-11 00:00 | 8.7151 | 9.1735 | 269.9786 | 4295.6141 | 64434.2117
2020-01-11 01:00 | 8.972 | 9.4438 | 272.5623 | 4584.8963 | 68773.4442
2020-01-11 02:00 | 9.2454 | 9.7316 | 273.4754 | 4835.3937 | 72530.906
2020-01-11 03:00 | 9.4062 | 9.901 | 273.9712 | 4974.584 | 74618.7605
2020-01-11 04:00 | 9.7478 | 10.2605 | 276.0245 | 5208.1253 | 78121.8794
2020-01-11 05:00 | 10.0457 | 10.574 | 279.1674 | 5376.2757 | 80644.1352
2020-01-11 06:00 | 10.0979 | 10.629 | 281.445 | 5397.2759 | 80959.1381
2020-01-11 07:00 | 9.9561 | 10.4797 | 282.9619 | 5336.1547 | 80042.321
2020-01-11 08:00 | 9.6145 | 10.1201 | 283.6522 | 5126.1671 | 76892.5058
2020-01-11 09:00 | 9.4177 | 9.913 | 281.4165 | 4984.4684 | 74767.0257
2020-01-11 10:00 | 9.5351 | 10.0366 | 280.0237 | 5077.4007 | 76161.0111
2020-01-11 11:00 | 9.7202 | 10.2315 | 282.2512 | 5191.1855 | 77867.7822
2020-01-11 12:00 | 9.6941 | 10.204 | 285.0286 | 5175.1343 | 77627.0144
2020-01-11 13:00 | 9.5435 | 10.0454 | 288.3177 | 5082.53 | 76237.9495
2020-01-11 14:00 | 9.1946 | 9.6781 | 292.2805 | 4791.4381 | 71871.5715
2020-01-11 15:00 | 8.8043 | 9.2674 | 298.4048 | 4396.112 | 65941.6806
2020-01-11 16:00 | 8.6685 | 9.1244 | 306.9428 | 4243.0852 | 63646.2778
2020-01-11 17:00 | 8.4632 | 8.9084 | 320.6397 | 4006.6265 | 60099.398
2020-01-11 18:00 | 9.1633 | 9.6453 | 344.3245 | 4764.429 | 71466.4349
2020-01-11 19:00 | 9.2874 | 9.7759 | 2.1066 | 4871.7672 | 73076.5075
2020-01-11 20:00 | 7.477 | 7.8703 | 7.6135 | 2845.7776 | 42686.6634
2020-01-11 21:00 | 7.4418 | 7.8332 | 1.638 | 2806.5324 | 42097.9863
2020-01-11 22:00 | 6.8584 | 7.2191 | 355.8117 | 2192.2337 | 32883.5049
2020-01-11 23:00 | 5.2861 | 5.5641 | 353.8976 | 973.9323 | 14608.9844
2020-01-12 00:00 | 4.5012 | 4.738 | 344.2463 | 574.423 | 8616.3448
2020-01-12 01:00 | 5.9618 | 6.2753 | 328.463 | 1424.734 | 21371.0093
2020-01-12 02:00 | 6.1488 | 6.4722 | 320.3149 | 1562.5488 | 23438.2324
2020-01-12 03:00 | 5.7326 | 6.0341 | 319.4674 | 1255.8805 | 18838.2075
2020-01-12 04:00 | 4.7753 | 5.0264 | 314.0513 | 698.2622 | 10473.9328
2020-01-12 05:00 | 4.412 | 4.6441 | 297.222 | 534.8001 | 8022.0017
2020-01-12 06:00 | 4.7537 | 5.0037 | 289.5003 | 686.8621 | 10302.9316
2020-01-12 07:00 | 4.7267 | 4.9753 | 279.5037 | 674.5941 | 10118.911
2020-01-12 08:00 | 5.1929 | 5.466 | 272.8817 | 918.9288 | 13783.9327
2020-01-12 09:00 | 5.3443 | 5.6253 | 267.7992 | 1010.2003 | 15153.0046
2020-01-12 10:00 | 5.0292 | 5.2937 | 253.9782 | 832.4486 | 12486.7295
2020-01-12 11:00 | 5.9333 | 6.2453 | 253.263 | 1403.7404 | 21056.1066
2020-01-12 12:00 | 6.2268 | 6.5543 | 252.2589 | 1626.108 | 24391.6202
2020-01-12 13:00 | 6.5763 | 6.9222 | 251.015 | 1924.8144 | 28872.2166
2020-01-12 14:00 | 6.2927 | 6.6237 | 240.1156 | 1682.4149 | 25236.2236
2020-01-12 15:00 | 7.0311 | 7.4009 | 236.8944 | 2361.6571 | 35424.8562
2020-01-12 16:00 | 7.5975 | 7.9971 | 236.8358 | 2979.9301 | 44698.951
2020-01-12 17:00 | 8.09 | 8.5155 | 238.7332 | 3563.4724 | 53452.0867
2020-01-12 18:00 | 8.5065 | 8.9539 | 244.2402 | 4058.0068 | 60870.1023
2020-01-12 19:00 | 8.7736 | 9.2351 | 247.9816 | 4361.5336 | 65423.0045
2020-01-12 20:00 | 9.0213 | 9.4957 | 246.9617 | 4640.4507 | 69606.7602
2020-01-12 21:00 | 9.426 | 9.9218 | 248.3937 | 4991.721 | 74875.8146
2020-01-12 22:00 | 9.2348 | 9.7205 | 251.0178 | 4826.274 | 72394.11
2020-01-12 23:00 | 9.4279 | 9.9237 | 252.4573 | 4993.292 | 74899.3794
2020-01-13 00:00 | 9.3773 | 9.8705 | 253.4584 | 4949.539 | 74243.0845
2020-01-13 01:00 | 9.3823 | 9.8757 | 255.1454 | 4953.8349 | 74307.523
2020-01-13 02:00 | 9.4024 | 9.8969 | 256.925 | 4971.241 | 74568.6156
2020-01-13 03:00 | 9.3864 | 9.8801 | 257.2021 | 4957.4303 | 74361.4545
2020-01-13 04:00 | 9.5108 | 10.011 | 263.5307 | 5062.4355 | 75936.5332
2020-01-13 05:00 | 9.6178 | 10.1237 | 266.8402 | 5128.2187 | 76923.28
2020-01-13 06:00 | 9.8631 | 10.3818 | 272.3165 | 5278.9992 | 79184.9875
2020-01-13 07:00 | 9.9578 | 10.4816 | 276.7001 | 5337.2358 | 80058.5371
2020-01-13 08:00 | 9.8797 | 10.3994 | 279.6191 | 5289.2234 | 79338.3514
2020-01-13 09:00 | 9.812 | 10.3281 | 280.6678 | 5247.5906 | 78713.8595
2020-01-13 10:00 | 7.9998 | 8.4206 | 281.2114 | 3456.5919 | 51848.8786
2020-01-13 11:00 | 8.5771 | 9.0282 | 286.8905 | 4140.1385 | 62102.0776
2020-01-13 12:00 | 8.199 | 8.6303 | 289.8267 | 3692.9414 | 55394.1207
2020-01-13 13:00 | 7.5126 | 7.9077 | 289.5476 | 2885.3356 | 43280.0343
2020-01-13 14:00 | 7.0504 | 7.4212 | 284.382 | 2380.56 | 35708.3998
2020-01-13 15:00 | 7.0375 | 7.4076 | 281.5291 | 2367.917 | 35518.7547
2020-01-13 16:00 | 6.5196 | 6.8625 | 279.5088 | 1876.3745 | 28145.6174
2020-01-13 17:00 | 6.136 | 6.4587 | 271.6708 | 1553.0716 | 23296.0733
2020-01-13 18:00 | 6.1795 | 6.5045 | 263.6961 | 1585.6746 | 23785.1187
2020-01-13 19:00 | 6.3941 | 6.7304 | 261.9556 | 1769.0507 | 26535.7605
2020-01-13 20:00 | 6.3345 | 6.6677 | 262.4899 | 1718.1448 | 25772.1716
2020-01-13 21:00 | 6.1187 | 6.4405 | 263.0085 | 1540.3529 | 23105.2937
2020-01-13 22:00 | 5.6632 | 5.9611 | 260.9718 | 1208.9583 | 18134.374
2020-01-13 23:00 | 5.5388 | 5.8301 | 253.0307 | 1131.4193 | 16971.2899
2020-01-14 00:00 | 5.6505 | 5.9477 | 250.4817 | 1201.0288 | 18015.4324
2020-01-14 01:00 | 5.6797 | 5.9784 | 248.9922 | 1219.2296 | 18288.4437
2020-01-14 02:00 | 5.8265 | 6.133 | 248.131 | 1325.0838 | 19876.2572
2020-01-14 03:00 | 5.6917 | 5.991 | 246.7193 | 1226.688 | 18400.3194
2020-01-14 04:00 | 5.5704 | 5.8633 | 247.9285 | 1151.1013 | 17266.519
2020-01-14 05:00 | 5.6416 | 5.9383 | 251.2859 | 1195.4558 | 17931.8364
2020-01-14 06:00 | 5.7742 | 6.0779 | 252.4816 | 1286.5577 | 19298.3648
2020-01-14 07:00 | 5.8319 | 6.1386 | 253.7492 | 1329.0261 | 19935.3915
2020-01-14 08:00 | 5.4249 | 5.7102 | 256.6877 | 1060.4408 | 15906.6126
2020-01-14 09:00 | 5.0704 | 5.3371 | 254.5044 | 854.2183 | 12813.2743
2020-01-14 10:00 | 4.053 | 4.2661 | 257.4655 | 391.6815 | 5875.223
2020-01-14 11:00 | 2.9725 | 3.1288 | 255.5733 | 75.5678 | 1133.5176
2020-01-14 12:00 | 2.3888 | 2.5144 | 250.4252 | 0 | 0
2020-01-14 13:00 | 1.7458 | 1.8376 | 247.0662 | 0 | 0
2020-01-14 14:00 | 1.2596 | 1.3259 | 241.7045 | 0 | 0
2020-01-14 15:00 | 1.6133 | 1.6981 | 202.3409 | 0 | 0
2020-01-14 16:00 | 2.7147 | 2.8575 | 182.4824 | 0 | 0
2020-01-14 17:00 | 3.781 | 3.9799 | 177.0966 | 292.2375 | 4383.5626
2020-01-14 18:00 | 4.9049 | 5.1628 | 174.2323 | 766.7437 | 11501.1557
2020-01-14 19:00 | 5.4167 | 5.7016 | 179.7564 | 1055.3632 | 15830.4485
2020-01-14 20:00 | 5.382 | 5.665 | 193.4839 | 1033.6958 | 15505.4372
2020-01-14 21:00 | 5.8744 | 6.1833 | 195.2626 | 1360.329 | 20404.9343
2020-01-14 22:00 | 5.8622 | 6.1706 | 194.4635 | 1351.3972 | 20270.9576
2020-01-14 23:00 | 6.0418 | 6.3595 | 198.2951 | 1483.6743 | 22255.1149
2020-01-15 00:00 | 6.8799 | 7.2417 | 195.1993 | 2213.2725 | 33199.0869
2020-01-15 01:00 | 7.1713 | 7.5484 | 197.7334 | 2505.232 | 37578.4797
2020-01-15 02:00 | 7.2782 | 7.661 | 199.4044 | 2624.2923 | 39364.3848
2020-01-15 03:00 | 7.7822 | 8.1915 | 198.911 | 3198.6253 | 47979.3798
2020-01-15 04:00 | 8.0166 | 8.4382 | 199.829 | 3476.4655 | 52146.9822
2020-01-15 05:00 | 7.8808 | 8.2953 | 204.6602 | 3315.5223 | 49732.8343
2020-01-15 06:00 | 7.2226 | 7.6024 | 210.5253 | 2562.3759 | 38435.6386
2020-01-15 07:00 | 7.2257 | 7.6057 | 205.1539 | 2565.8104 | 38487.1553
2020-01-15 08:00 | 7.3085 | 7.6929 | 203.908 | 2658.0927 | 39871.3903
2020-01-15 09:00 | 6.0899 | 6.4101 | 208.7815 | 1519.1006 | 22786.5094
2020-01-15 10:00 | 5.749 | 6.0513 | 199.4908 | 1267.9214 | 19018.8216
2020-01-15 11:00 | 6.0308 | 6.348 | 193.2503 | 1475.607 | 22134.1055
2020-01-15 12:00 | 6.5761 | 6.922 | 190.5537 | 1924.6259 | 28869.3881
2020-01-15 13:00 | 7.0105 | 7.3792 | 188.8591 | 2341.4272 | 35121.4079
2020-01-15 14:00 | 7.6137 | 8.0141 | 191.6175 | 2998.8947 | 44983.4202
2020-01-15 15:00 | 8.0615 | 8.4855 | 195.9571 | 3529.6774 | 52945.1603
2020-01-15 16:00 | 8.5907 | 9.0425 | 195.7567 | 4155.5124 | 62332.6863
2020-01-15 17:00 | 8.8003 | 9.2631 | 196.7769 | 4391.5298 | 65872.9465
2020-01-15 18:00 | 8.5072 | 8.9546 | 199.8693 | 4058.8344 | 60882.5159
2020-01-15 19:00 | 8.1376 | 8.5656 | 202.5316 | 3620.0366 | 54300.5483
2020-01-15 20:00 | 7.9302 | 8.3473 | 203.5038 | 3374.0639 | 50610.9586
2020-01-15 21:00 | 7.6229 | 8.0238 | 205.8044 | 3009.8349 | 45147.5231
2020-01-15 22:00 | 6.6152 | 6.9631 | 205.1872 | 1958.0237 | 29370.3552
2020-01-15 23:00 | 6.828 | 7.1871 | 203.2893 | 2162.3697 | 32435.5459
2020-01-16 00:00 | 6.6554 | 7.0054 | 201.8309 | 1993.0718 | 29896.0766
2020-01-16 01:00 | 6.5065 | 6.8487 | 198.4826 | 1865.1117 | 27976.6748
2020-01-16 02:00 | 6.8425 | 7.2024 | 200.1286 | 2176.6648 | 32649.9713
2020-01-16 03:00 | 6.829 | 7.1882 | 204.5999 | 2163.3918 | 32450.8769
2020-01-16 04:00 | 6.5565 | 6.9014 | 208.464 | 1907.9016 | 28618.5237
2020-01-16 05:00 | 6.4891 | 6.8304 | 210.7525 | 1850.2757 | 27754.1357
2020-01-16 06:00 | 6.3943 | 6.7306 | 209.8535 | 1769.2128 | 26538.1926
2020-01-16 07:00 | 6.7457 | 7.1005 | 217.1813 | 2081.6744 | 31225.1162
2020-01-16 08:00 | 6.4093 | 6.7464 | 223.9668 | 1782.0861 | 26731.2912
2020-01-16 09:00 | 6.074 | 6.3935 | 229.3108 | 1507.4354 | 22611.5317
2020-01-16 10:00 | 5.8094 | 6.1149 | 236.2316 | 1312.4427 | 19686.6398
2020-01-16 11:00 | 5.7212 | 6.0221 | 243.8425 | 1247.4865 | 18712.2973
2020-01-16 12:00 | 5.6287 | 5.9247 | 248.0579 | 1187.421 | 17811.3147
2020-01-16 13:00 | 5.0052 | 5.2684 | 238.3928 | 819.755 | 12296.3245
2020-01-16 14:00 | 5.7642 | 6.0674 | 231.4916 | 1279.1903 | 19187.855
2020-01-16 15:00 | 6.5431 | 6.8873 | 238.3956 | 1896.4678 | 28447.0176
2020-01-16 16:00 | 6.6853 | 7.0369 | 252.0473 | 2022.369 | 30335.5344
2020-01-16 17:00 | 6.6268 | 6.9754 | 265.6815 | 1967.9983 | 29519.974
2020-01-16 18:00 | 6.5454 | 6.8897 | 278.3487 | 1898.4046 | 28476.069
2020-01-16 19:00 | 6.5296 | 6.8731 | 291.7208 | 1884.9296 | 28273.9437
2020-01-16 20:00 | 6.1947 | 6.5206 | 301.8083 | 1598.687 | 23980.3051
2020-01-16 21:00 | 5.9022 | 6.2126 | 307.0605 | 1380.8002 | 20712.0035
2020-01-16 22:00 | 6.3956 | 6.7319 | 308.0277 | 1770.336 | 26555.0401
2020-01-16 23:00 | 6.4089 | 6.746 | 314.5084 | 1781.7567 | 26726.3511
2020-01-17 00:00 | 6.2655 | 6.595 | 322.5755 | 1659.1738 | 24887.6074
2020-01-17 01:00 | 6.4568 | 6.7964 | 328.9616 | 1822.647 | 27339.7046
2020-01-17 02:00 | 6.0733 | 6.3927 | 332.9383 | 1506.9115 | 22603.6731
2020-01-17 03:00 | 5.3639 | 5.646 | 334.595 | 1022.4281 | 15336.4215
2020-01-17 04:00 | 4.5851 | 4.8262 | 336.9309 | 611.6576 | 9174.8642
2020-01-17 05:00 | 3.9898 | 4.1997 | 336.5586 | 368.2907 | 5524.361
2020-01-17 06:00 | 4.115 | 4.3314 | 334.6173 | 414.65 | 6219.75
2020-01-17 07:00 | 3.7549 | 3.9523 | 329.045 | 284.3709 | 4265.5632
2020-01-17 08:00 | 2.6963 | 2.8381 | 309.0246 | 0 | 0
2020-01-17 09:00 | 2.2931 | 2.4137 | 294.1857 | 0 | 0
2020-01-17 10:00 | 2.1461 | 2.259 | 305.7456 | 0 | 0
2020-01-17 11:00 | 1.7828 | 1.8766 | 315.0992 | 0 | 0
2020-01-17 12:00 | 1.3315 | 1.4016 | 331.9872 | 0 | 0
2020-01-17 13:00 | 0.93571 | 0.98492 | 339.6492 | 0 | 0
2020-01-17 14:00 | 0.58379 | 0.6145 | 311.7654 | 0 | 0
2020-01-17 15:00 | 0.48041 | 0.50568 | 321.4334 | 0 | 0
2020-01-17 16:00 | 0.24247 | 0.25522 | 260.6669 | 0 | 0
2020-01-17 17:00 | 0.91796 | 0.96624 | 197.9606 | 0 | 0
2020-01-17 18:00 | 1.5811 | 1.6643 | 184.429 | 0 | 0
2020-01-17 19:00 | 2.1653 | 2.2792 | 172.7828 | 0 | 0
2020-01-17 20:00 | 2.8222 | 2.9706 | 166.8677 | 0 | 0
2020-01-17 21:00 | 3.5029 | 3.6872 | 173.3555 | 208.529 | 3127.9348
2020-01-17 22:00 | 3.5474 | 3.7339 | 194.4144 | 221.9025 | 3328.5379
2020-01-17 23:00 | 4.0441 | 4.2568 | 194.0485 | 388.3919 | 5825.8782
2020-01-18 00:00 | 4.0909 | 4.3061 | 183.9621 | 405.7416 | 6086.1245
2020-01-18 01:00 | 4.3321 | 4.56 | 173.5637 | 499.3034 | 7489.5512
2020-01-18 02:00 | 4.5977 | 4.8395 | 170.0285 | 617.2668 | 9259.0017
2020-01-18 03:00 | 5.1549 | 5.426 | 173.181 | 898.864 | 13482.9603
2020-01-18 04:00 | 5.4549 | 5.7418 | 178.2197 | 1079.1183 | 16186.7739
2020-01-18 05:00 | 5.8504 | 6.1581 | 178.3587 | 1342.6528 | 20139.7917
2020-01-18 06:00 | 5.8488 | 6.1564 | 176.4607 | 1341.5148 | 20122.7225
2020-01-18 07:00 | 6.2516 | 6.5804 | 178.7407 | 1647.2996 | 24709.4944
2020-01-18 08:00 | 5.9479 | 6.2607 | 181.4434 | 1414.5218 | 21217.8272
2020-01-18 09:00 | 5.5871 | 5.8809 | 183.6917 | 1161.5005 | 17422.5078
2020-01-18 10:00 | 4.6006 | 4.8426 | 190.2204 | 618.5785 | 9278.6768
2020-01-18 11:00 | 4.3462 | 4.5748 | 193.1961 | 505.5575 | 7583.3625
2020-01-18 12:00 | 4.0319 | 4.2439 | 190.7481 | 383.8609 | 5757.9129
2020-01-18 13:00 | 3.7858 | 3.9849 | 183.4506 | 293.6833 | 4405.249
2020-01-18 14:00 | 4.4942 | 4.7306 | 174.8959 | 571.3008 | 8569.5125
2020-01-18 15:00 | 5.3804 | 5.6634 | 176.5443 | 1032.7233 | 15490.8495
2020-01-18 16:00 | 5.7423 | 6.0444 | 180.1419 | 1263.0512 | 18945.7686
2020-01-18 17:00 | 5.7674 | 6.0707 | 185.3375 | 1281.4979 | 19222.468
2020-01-18 18:00 | 5.7451 | 6.0473 | 190.7749 | 1265.0971 | 18976.456
2020-01-18 19:00 | 5.4751 | 5.7631 | 196.7972 | 1091.7445 | 16376.1679
2020-01-18 20:00 | 4.9323 | 5.1917 | 195.6935 | 781.227 | 11718.4051
2020-01-18 21:00 | 4.7712 | 5.0221 | 196.531 | 696.0908 | 10441.3621
2020-01-18 22:00 | 3.3123 | 3.4866 | 203.2936 | 152.1234 | 2281.8511
2020-01-18 23:00 | 2.8598 | 3.0102 | 199.8396 | 50.1855 | 752.7821
2020-01-19 00:00 | 2.6413 | 2.7802 | 194.4687 | 0 | 0
2020-01-19 01:00 | 2.421 | 2.5483 | 181.6823 | 0 | 0
2020-01-19 02:00 | 2.7405 | 2.8847 | 188.0779 | 0 | 0
2020-01-19 03:00 | 2.6296 | 2.7679 | 187.9472 | 0 | 0
2020-01-19 04:00 | 2.885 | 3.0367 | 184.648 | 55.8594 | 837.8906
2020-01-19 05:00 | 3.1891 | 3.3569 | 188.9541 | 124.3725 | 1865.5873
2020-01-19 06:00 | 2.8392 | 2.9885 | 194.5239 | 0 | 0
2020-01-19 07:00 | 2.479 | 2.6094 | 197.732 | 0 | 0
2020-01-19 08:00 | 2.1037 | 2.2143 | 192.9171 | 0 | 0
2020-01-19 09:00 | 1.93 | 2.0316 | 190.7293 | 0 | 0
2020-01-19 10:00 | 1.595 | 1.6789 | 208.3913 | 0 | 0
2020-01-19 11:00 | 1.2169 | 1.281 | 227.7208 | 0 | 0
2020-01-19 12:00 | 0.87535 | 0.92139 | 261.268 | 0 | 0
2020-01-19 13:00 | 0.6504 | 0.6846 | 315.0646 | 0 | 0
2020-01-19 14:00 | 0.77292 | 0.81357 | 350.1998 | 0 | 0
2020-01-19 15:00 | 1.2328 | 1.2976 | 356.7693 | 0 | 0
2020-01-19 16:00 | 1.5718 | 1.6544 | 4.6742 | 0 | 0
2020-01-19 17:00 | 1.5577 | 1.6397 | 12.3857 | 0 | 0
2020-01-19 18:00 | 1.166 | 1.2273 | 14.6411 | 0 | 0
2020-01-19 19:00 | 1.194 | 1.2568 | 354.5359 | 0 | 0
2020-01-19 20:00 | 1.8078 | 1.9029 | 347.2692 | 0 | 0
2020-01-19 21:00 | 2.1088 | 2.2197 | 339.7201 | 0 | 0
2020-01-19 22:00 | 3.1202 | 3.2843 | 329.8245 | 108.8309 | 1632.4638
2020-01-19 23:00 | 4.3989 | 4.6302 | 335.4777 | 528.9626 | 7934.4392
2020-01-20 00:00 | 3.9421 | 4.1494 | 340.1122 | 350.5842 | 5258.7629
2020-01-20 01:00 | 3.8719 | 4.0756 | 341.6884 | 324.6058 | 4869.087
2020-01-20 02:00 | 4.0551 | 4.2684 | 345.0258 | 392.4709 | 5887.0637
2020-01-20 03:00 | 3.5197 | 3.7048 | 338.5539 | 213.5818 | 3203.7269
2020-01-20 04:00 | 3.97 | 4.1788 | 333.4837 | 360.9244 | 5413.8666
2020-01-20 05:00 | 4.0513 | 4.2644 | 324.6707 | 391.0547 | 5865.8211
2020-01-20 06:00 | 4.4002 | 4.6316 | 320.3657 | 529.5279 | 7942.9192
2020-01-20 07:00 | 4.0724 | 4.2866 | 307.9202 | 398.8944 | 5983.4163
2020-01-20 08:00 | 4.3407 | 4.569 | 305.1498 | 503.1283 | 7546.924
2020-01-20 09:00 | 4.905 | 5.163 | 307.4937 | 766.8141 | 11502.2108
2020-01-20 10:00 | 5.5186 | 5.8089 | 314.9979 | 1118.8429 | 16782.643
2020-01-20 11:00 | 5.2097 | 5.4837 | 306.256 | 927.7951 | 13916.9258
2020-01-20 12:00 | 5.9972 | 6.3126 | 304.6649 | 1450.8446 | 21762.6686
2020-01-20 13:00 | 6.9046 | 7.2678 | 307.4885 | 2237.5488 | 33563.2315
2020-01-20 14:00 | 6.9577 | 7.3236 | 306.7286 | 2289.6206 | 34344.3095
2020-01-20 15:00 | 7.2743 | 7.6569 | 305.7155 | 2619.9687 | 39299.53
2020-01-20 16:00 | 7.2796 | 7.6624 | 305.0843 | 2625.8567 | 39387.8504
2020-01-20 17:00 | 7.353 | 7.7397 | 304.297 | 2707.5809 | 40613.7129
2020-01-20 18:00 | 7.5982 | 7.9979 | 301.6338 | 2980.7339 | 44711.009
2020-01-20 19:00 | 7.7665 | 8.1749 | 299.191 | 3179.9934 | 47699.9008
2020-01-20 20:00 | 7.9262 | 8.3431 | 296.4197 | 3369.3593 | 50540.3902
2020-01-20 21:00 | 8.1594 | 8.5885 | 292.8537 | 3645.842 | 54687.6303
2020-01-20 22:00 | 8.5229 | 8.9712 | 288.8576 | 4077.4641 | 61161.962
2020-01-20 23:00 | 9.1686 | 9.6508 | 289.0519 | 4768.9386 | 71534.0791
2020-01-21 00:00 | 9.415 | 9.9101 | 291.4777 | 4982.1322 | 74731.9827
2020-01-21 01:00 | 9.3021 | 9.7913 | 289.1503 | 4884.4437 | 73266.6554
2020-01-21 02:00 | 9.4425 | 9.9391 | 288.5599 | 5005.9538 | 75089.307
2020-01-21 03:00 | 9.8232 | 10.3399 | 289.737 | 5254.4764 | 78817.1455
2020-01-21 04:00 | 10.2029 | 10.7395 | 290.9282 | 5439.5068 | 81592.6022
2020-01-21 05:00 | 10.2316 | 10.7698 | 288.4688 | 5451.0542 | 81765.8131
2020-01-21 06:00 | 10.2495 | 10.7886 | 283.5723 | 5458.2308 | 81873.4619
2020-01-21 07:00 | 10.3605 | 10.9054 | 281.6757 | 5502.8676 | 82543.0144
2020-01-21 08:00 | 9.536 | 10.0375 | 278.163 | 5077.9218 | 76168.8267
2020-01-21 09:00 | 10.2116 | 10.7487 | 281.1047 | 5442.9859 | 81644.788
2020-01-21 10:00 | 9.7013 | 10.2115 | 280.5802 | 5179.5238 | 77692.8568
2020-01-21 11:00 | 10.662 | 11.2228 | 284.0099 | 5589.3556 | 83840.3337
2020-01-21 12:00 | 10.6415 | 11.2012 | 284.8756 | 5584.4672 | 83767.0078
2020-01-21 13:00 | 11.702 | 12.3175 | 286.8805 | 5699.635 | 85494.5247
2020-01-21 14:00 | 11.8866 | 12.5118 | 288.0846 | 5700 | 85500
2020-01-21 15:00 | 12.3534 | 13.0031 | 289.4813 | 5700 | 85500
2020-01-21 16:00 | 12.4102 | 13.0629 | 291.9275 | 5700 | 85500
2020-01-21 17:00 | 12.2216 | 12.8644 | 291.7301 | 5700 | 85500
2020-01-21 18:00 | 12.5455 | 13.2053 | 293.0957 | 5700 | 85500
2020-01-21 19:00 | 12.6251 | 13.2891 | 299.0934 | 5700 | 85500
2020-01-21 20:00 | 12.0993 | 12.7356 | 297.206 | 5700 | 85500
2020-01-21 21:00 | 11.7685 | 12.3874 | 297.4232 | 5699.7748 | 85496.6222
2020-01-21 22:00 | 11.1561 | 11.7428 | 297.3658 | 5674.8278 | 85122.4176
2020-01-21 23:00 | 10.551 | 11.1059 | 293.7566 | 5562.9284 | 83443.9266
2020-01-22 00:00 | 10.3033 | 10.8452 | 289.2814 | 5479.8482 | 82197.7237
2020-01-22 01:00 | 10.5272 | 11.0809 | 285.0505 | 5557.278 | 83359.1695
2020-01-22 02:00 | 10.6329 | 11.1922 | 281.7569 | 5582.427 | 83736.4056
2020-01-22 03:00 | 10.7791 | 11.346 | 277.6128 | 5617.1951 | 84257.9268
2020-01-22 04:00 | 10.9055 | 11.479 | 276.7863 | 5647.261 | 84708.9156
2020-01-22 05:00 | 11.0846 | 11.6675 | 276.7801 | 5667.7489 | 85016.2338
2020-01-22 06:00 | 11.7352 | 12.3524 | 276.0937 | 5699.7049 | 85495.5735
2020-01-22 07:00 | 12.1057 | 12.7424 | 276.5049 | 5700 | 85500
2020-01-22 08:00 | 12.3557 | 13.0056 | 276.2375 | 5700 | 85500
2020-01-22 09:00 | 12.0982 | 12.7345 | 275.8677 | 5700 | 85500
2020-01-22 10:00 | 10.8947 | 11.4677 | 275.8349 | 5644.7088 | 84670.6315
2020-01-22 11:00 | 11.5753 | 12.1841 | 278.4863 | 5699.3682 | 85490.5224
2020-01-22 12:00 | 11.1048 | 11.6888 | 278.2032 | 5669.7478 | 85046.2168
2020-01-22 13:00 | 10.7091 | 11.2723 | 276.3472 | 5600.5474 | 84008.2112
2020-01-22 14:00 | 13.3842 | 14.0882 | 286.642 | 5700 | 85500
2020-01-22 15:00 | 12.5193 | 13.1778 | 289.093 | 5700 | 85500
2020-01-22 16:00 | 12.2538 | 12.8983 | 290.1916 | 5700 | 85500
2020-01-22 17:00 | 11.9652 | 12.5945 | 292.2786 | 5700 | 85500
2020-01-22 18:00 | 12.3727 | 13.0235 | 298.9558 | 5700 | 85500
2020-01-22 19:00 | 12.7607 | 13.4319 | 310.7697 | 5700 | 85500
2020-01-22 20:00 | 13.0474 | 13.7336 | 321.2083 | 5700 | 85500
2020-01-22 21:00 | 12.1143 | 12.7514 | 324.6756 | 5700 | 85500
2020-01-22 22:00 | 11.4915 | 12.0959 | 323.362 | 5699.1919 | 85487.8783
2020-01-22 23:00 | 11.1722 | 11.7598 | 318.8827 | 5676.4219 | 85146.3285
2020-01-23 00:00 | 11.366 | 11.9638 | 317.1806 | 5695.5967 | 85433.9501
2020-01-23 01:00 | 11.4782 | 12.0819 | 317.9686 | 5699.1639 | 85487.4582
2020-01-23 02:00 | 11.6261 | 12.2376 | 318.2865 | 5699.4752 | 85492.1285
2020-01-23 03:00 | 11.7425 | 12.3601 | 318.8788 | 5699.7202 | 85495.8027
2020-01-23 04:00 | 12.0147 | 12.6466 | 321.466 | 5700 | 85500
2020-01-23 05:00 | 12.411 | 13.0637 | 325.8266 | 5700 | 85500
2020-01-23 06:00 | 11.8131 | 12.4344 | 326.885 | 5699.8688 | 85498.0326
2020-01-23 07:00 | 11.471 | 12.0743 | 324.4893 | 5699.1486 | 85487.2283
2020-01-23 08:00 | 10.5846 | 11.1413 | 320.1824 | 5570.923 | 83563.8443
2020-01-23 09:00 | 13.5624 | 14.2757 | 323.7361 | 5700 | 85500
2020-01-23 10:00 | 12.1707 | 12.8108 | 317.5418 | 5700 | 85500
2020-01-23 11:00 | 12.5348 | 13.1941 | 315.3685 | 5700 | 85500
2020-01-23 12:00 | 12.3554 | 13.0052 | 313.2285 | 5700 | 85500
2020-01-23 13:00 | 10.5709 | 11.1269 | 309.2499 | 5567.672 | 83515.0806
2020-01-23 14:00 | 10.7748 | 11.3415 | 309.6915 | 5616.1738 | 84242.6069
2020-01-23 15:00 | 10.5234 | 11.0769 | 308.2939 | 5556.3819 | 83345.7284
2020-01-23 16:00 | 10.26 | 10.7996 | 307.8465 | 5462.4398 | 81936.5967
2020-01-23 17:00 | 9.7095 | 10.2202 | 306.3 | 5184.5936 | 77768.9034
2020-01-23 18:00 | 9.1666 | 9.6487 | 301.963 | 4767.2164 | 71508.2453
2020-01-23 19:00 | 8.8712 | 9.3378 | 298.3743 | 4471.4314 | 67071.4715
2020-01-23 20:00 | 8.4853 | 8.9316 | 294.9558 | 4032.8766 | 60493.149
2020-01-23 21:00 | 8.3435 | 8.7823 | 290.3178 | 3864.4171 | 57966.2565
2020-01-23 22:00 | 7.7858 | 8.1953 | 292.2151 | 3202.9021 | 48043.5313
2020-01-23 23:00 | 7.3517 | 7.7384 | 281.1705 | 2706.1798 | 40592.6963
2020-01-24 00:00 | 7.3776 | 7.7656 | 271.9612 | 2735.0084 | 41025.1256
2020-01-24 01:00 | 7.6913 | 8.0958 | 268.0149 | 3090.9026 | 46363.5389
2020-01-24 02:00 | 8.2089 | 8.6406 | 268.21 | 3704.6108 | 55569.1614
2020-01-24 03:00 | 8.4762 | 8.922 | 267.2594 | 4021.9844 | 60329.7655
2020-01-24 04:00 | 8.6006 | 9.053 | 264.1487 | 4166.6835 | 62500.2527
2020-01-24 05:00 | 9.0557 | 9.532 | 265.4814 | 4671.2653 | 70068.9797
2020-01-24 06:00 | 9.2969 | 9.7859 | 269.7937 | 4880.0001 | 73200.0018
2020-01-24 07:00 | 8.8357 | 9.3004 | 270.5443 | 4431.3992 | 66470.9884
2020-01-24 08:00 | 8.5833 | 9.0347 | 266.5042 | 4147.1765 | 62207.6476
2020-01-24 09:00 | 9.4141 | 9.9092 | 269.6307 | 4981.3797 | 74720.6958
2020-01-24 10:00 | 8.0824 | 8.5075 | 267.0785 | 3554.4907 | 53317.36
2020-01-24 11:00 | 8.0555 | 8.4791 | 267.3573 | 3522.5195 | 52837.7919
2020-01-24 12:00 | 8.0662 | 8.4904 | 265.2995 | 3535.2236 | 53028.3535
2020-01-24 13:00 | 8.2864 | 8.7222 | 262.4406 | 3796.6492 | 56949.7379
2020-01-24 14:00 | 9.0677 | 9.5446 | 262.3635 | 4681.6666 | 70224.9992
2020-01-24 15:00 | 9.5636 | 10.0666 | 263.741 | 5094.8707 | 76423.0598
2020-01-24 16:00 | 9.6845 | 10.1938 | 266.2788 | 5169.2075 | 77538.1131
2020-01-24 17:00 | 9.6528 | 10.1604 | 270.1254 | 5149.7011 | 77245.516
2020-01-24 18:00 | 9.6588 | 10.1668 | 273.639 | 5153.3943 | 77300.9147
2020-01-24 19:00 | 9.7091 | 10.2197 | 276.4457 | 5184.3288 | 77764.9327
2020-01-24 20:00 | 9.6733 | 10.1821 | 279.0069 | 5162.3207 | 77434.8109
2020-01-24 21:00 | 9.5072 | 10.0073 | 279.9282 | 5060.2376 | 75903.5633
2020-01-24 22:00 | 8.7813 | 9.2431 | 277.4086 | 4370.135 | 65552.0251
2020-01-24 23:00 | 8.843 | 9.308 | 278.2572 | 4439.6097 | 66594.1462
2020-01-25 00:00 | 9.0527 | 9.5288 | 277.5353 | 4668.7146 | 70030.7188
2020-01-25 01:00 | 9.0742 | 9.5514 | 275.9351 | 4687.2674 | 70309.011
2020-01-25 02:00 | 8.9707 | 9.4425 | 277.8156 | 4583.4914 | 68752.3703
2020-01-25 03:00 | 9.0157 | 9.4899 | 279.8856 | 4634.1996 | 69512.9935
2020-01-25 04:00 | 8.7848 | 9.2468 | 279.0167 | 4374.0889 | 65611.3336
2020-01-25 05:00 | 8.9118 | 9.3805 | 278.756 | 4517.1648 | 67757.4716
2020-01-25 06:00 | 8.8983 | 9.3663 | 278.6153 | 4501.964 | 67529.4597
2020-01-25 07:00 | 8.9059 | 9.3743 | 278.6704 | 4510.4519 | 67656.7792
2020-01-25 08:00 | 8.4202 | 8.8631 | 278.4095 | 3955.5452 | 59333.1786
2020-01-25 09:00 | 8.4424 | 8.8864 | 277.4878 | 3981.868 | 59728.0197
2020-01-25 10:00 | 7.9722 | 8.3915 | 280.5596 | 3423.8604 | 51357.9057
2020-01-25 11:00 | 7.7427 | 8.1499 | 280.1012 | 3151.8105 | 47277.1571
2020-01-25 12:00 | 8.2605 | 8.695 | 281.803 | 3765.9486 | 56489.2297
2020-01-25 13:00 | 7.9488 | 8.3668 | 278.7001 | 3396.0427 | 50940.6406
2020-01-25 14:00 | 8.0779 | 8.5028 | 280.0568 | 3549.1569 | 53237.3531
2020-01-25 15:00 | 8.3377 | 8.7762 | 285.2049 | 3857.5447 | 57863.1704
2020-01-25 16:00 | 8.2368 | 8.67 | 288.6715 | 3737.7393 | 56066.09
2020-01-25 17:00 | 8.1345 | 8.5623 | 292.8392 | 3616.2675 | 54244.0127
2020-01-25 18:00 | 7.7998 | 8.21 | 296.0415 | 3219.4505 | 48291.7574
2020-01-25 19:00 | 7.4286 | 7.8193 | 295.8184 | 2791.8656 | 41877.9838
2020-01-25 20:00 | 7.1077 | 7.4815 | 295.4349 | 2436.7982 | 36551.9731
2020-01-25 21:00 | 6.8238 | 7.1827 | 294.267 | 2158.2614 | 32373.9217
2020-01-25 22:00 | 6.574 | 6.9198 | 293.2249 | 1922.8494 | 28842.7405
2020-01-25 23:00 | 6.474 | 6.8145 | 292.3065 | 1837.4028 | 27561.0415
2020-01-26 00:00 | 6.1588 | 6.4827 | 289.5574 | 1569.8953 | 23548.4288
2020-01-26 01:00 | 5.7314 | 6.0329 | 288.1102 | 1255.0077 | 18825.1155
2020-01-26 02:00 | 5.6214 | 5.917 | 285.636 | 1182.8902 | 17743.3535
2020-01-26 03:00 | 5.4289 | 5.7145 | 284.3941 | 1062.965 | 15944.4751
2020-01-26 04:00 | 5.1544 | 5.4254 | 283.3703 | 898.5726 | 13478.5893
2020-01-26 05:00 | 4.9973 | 5.2601 | 279.7301 | 815.5705 | 12233.5573
2020-01-26 06:00 | 4.5956 | 4.8373 | 280.2786 | 616.3291 | 9244.9365
2020-01-26 07:00 | 4.0898 | 4.3049 | 279.8014 | 405.3141 | 6079.7117
2020-01-26 08:00 | 3.2898 | 3.4628 | 275.6618 | 147.0393 | 2205.5899
2020-01-26 09:00 | 2.7816 | 2.9278 | 258.278 | 0 | 0
2020-01-26 10:00 | 3.622 | 3.8125 | 243.397 | 244.3693 | 3665.5395
2020-01-26 11:00 | 4.1964 | 4.4171 | 243.7759 | 444.8247 | 6672.3701
2020-01-26 12:00 | 4.6821 | 4.9284 | 245.6779 | 654.774 | 9821.6103
2020-01-26 13:00 | 4.7904 | 5.0423 | 243.4774 | 706.2444 | 10593.6655
2020-01-26 14:00 | 4.6693 | 4.9149 | 238.4439 | 649.0838 | 9736.2572
2020-01-26 15:00 | 4.5613 | 4.8012 | 235.6525 | 601.1192 | 9016.7875
2020-01-26 16:00 | 4.5854 | 4.8266 | 230.5848 | 611.8243 | 9177.3652
2020-01-26 17:00 | 4.9878 | 5.2502 | 226.794 | 810.5876 | 12158.8145
2020-01-26 18:00 | 5.5605 | 5.8529 | 227.0129 | 1144.9229 | 17173.8439
2020-01-26 19:00 | 6.1032 | 6.4242 | 229.2979 | 1528.9327 | 22933.9903
2020-01-26 20:00 | 6.0428 | 6.3606 | 232.6743 | 1484.4264 | 22266.3955
2020-01-26 21:00 | 5.8795 | 6.1887 | 234.7029 | 1364.1027 | 20461.5402
2020-01-26 22:00 | 5.7779 | 6.0818 | 233.1395 | 1289.2724 | 19339.086
2020-01-26 23:00 | 5.7483 | 6.0506 | 232.0322 | 1267.4112 | 19011.168
2020-01-27 00:00 | 5.7191 | 6.0199 | 229.3578 | 1245.952 | 18689.2804
2020-01-27 01:00 | 5.7539 | 6.0566 | 228.7194 | 1271.5895 | 19073.8424
2020-01-27 02:00 | 5.6382 | 5.9348 | 227.7925 | 1193.3955 | 17900.9323
2020-01-27 03:00 | 5.3421 | 5.6231 | 225.8713 | 1008.8567 | 15132.8503
2020-01-27 04:00 | 5.4494 | 5.736 | 224.1008 | 1075.7002 | 16135.5034
2020-01-27 05:00 | 5.5224 | 5.8128 | 227.8052 | 1121.1781 | 16817.6721
2020-01-27 06:00 | 5.1338 | 5.4038 | 227.5674 | 887.7087 | 13315.6298
2020-01-27 07:00 | 4.9622 | 5.2232 | 224.3169 | 797.0591 | 11955.8868
2020-01-27 08:00 | 4.7952 | 5.0474 | 223.289 | 708.7837 | 10631.7558
2020-01-27 09:00 | 4.0038 | 4.2144 | 225.4757 | 373.4612 | 5601.9176
2020-01-27 10:00 | 3.1837 | 3.3511 | 216.1942 | 123.1443 | 1847.1638
2020-01-27 11:00 | 3.1187 | 3.2827 | 210.533 | 108.4989 | 1627.4841
2020-01-27 12:00 | 3.3321 | 3.5074 | 205.8702 | 157.1108 | 2356.6617
2020-01-27 13:00 | 3.97 | 4.1788 | 200.9775 | 360.9398 | 5414.0972
2020-01-27 14:00 | 5.0529 | 5.3186 | 207.5025 | 844.9622 | 12674.433
2020-01-27 15:00 | 5.9502 | 6.2632 | 212.2733 | 1416.2188 | 21243.2823
2020-01-27 16:00 | 6.1012 | 6.4221 | 219.2271 | 1527.4956 | 22912.4341
2020-01-27 17:00 | 6.2768 | 6.6069 | 227.755 | 1668.8113 | 25032.1702
2020-01-27 18:00 | 6.2304 | 6.558 | 234.906 | 1629.1239 | 24436.8579
2020-01-27 19:00 | 6.0398 | 6.3574 | 239.8963 | 1482.1946 | 22232.9183
2020-01-27 20:00 | 5.957 | 6.2703 | 245.2207 | 1421.2073 | 21318.1088
2020-01-27 21:00 | 5.8474 | 6.155 | 251.34 | 1340.4822 | 20107.2329
2020-01-27 22:00 | 5.3754 | 5.6581 | 252.0356 | 1029.6065 | 15444.0976
2020-01-27 23:00 | 5.1313 | 5.4012 | 255.87 | 886.3972 | 13295.9581
2020-01-28 00:00 | 4.8127 | 5.0659 | 256.1536 | 718.0614 | 10770.9206
2020-01-28 01:00 | 4.6359 | 4.8797 | 251.2727 | 634.2401 | 9513.6014
2020-01-28 02:00 | 4.7768 | 5.028 | 251.3168 | 699.0751 | 10486.1258
2020-01-28 03:00 | 4.3884 | 4.6192 | 257.0366 | 524.3234 | 7864.851
2020-01-28 04:00 | 3.7946 | 3.9941 | 260.3175 | 296.3229 | 4444.8442
2020-01-28 05:00 | 3.3954 | 3.5739 | 257.5667 | 176.1479 | 2642.2179
2020-01-28 06:00 | 3.0418 | 3.2018 | 248.0855 | 91.1817 | 1367.7256
2020-01-28 07:00 | 2.7762 | 2.9222 | 227.6718 | 0 | 0
2020-01-28 08:00 | 2.7099 | 2.8525 | 202.2855 | 0 | 0
2020-01-28 09:00 | 2.1582 | 2.2717 | 177.7155 | 0 | 0
2020-01-28 10:00 | 2.6404 | 2.7793 | 152.5482 | 0 | 0
2020-01-28 11:00 | 3.3782 | 3.5559 | 150.2949 | 170.9924 | 2564.8859
2020-01-28 12:00 | 4.1486 | 4.3668 | 151.5399 | 427.1151 | 6406.7258
2020-01-28 13:00 | 4.9269 | 5.186 | 154.78 | 778.3772 | 11675.6586
2020-01-28 14:00 | 6.1269 | 6.4492 | 158.4473 | 1546.4319 | 23196.4788
2020-01-28 15:00 | 7.0982 | 7.4715 | 160.852 | 2427.4653 | 36411.9794
2020-01-28 16:00 | 7.3876 | 7.7762 | 165.5946 | 2746.2032 | 41193.0481
2020-01-28 17:00 | 7.3865 | 7.775 | 171.4612 | 2744.9079 | 41173.6192
2020-01-28 18:00 | 7.3853 | 7.7737 | 177.4549 | 2743.6275 | 41154.4124
2020-01-28 19:00 | 7.4925 | 7.8866 | 180.4907 | 2863.0291 | 42945.4362
2020-01-28 20:00 | 7.5849 | 7.9838 | 177.763 | 2965.9006 | 44488.5094
2020-01-28 21:00 | 7.5604 | 7.9581 | 174.5924 | 2938.632 | 44079.4802
2020-01-28 22:00 | 7.0649 | 7.4365 | 175.2052 | 2394.7802 | 35921.7023
2020-01-28 23:00 | 7.1068 | 7.4805 | 173.1721 | 2435.8552 | 36537.8286
2020-01-29 00:00 | 7.4206 | 7.8109 | 166.1041 | 2782.9353 | 41744.0293
2020-01-29 01:00 | 7.6278 | 8.029 | 162.8245 | 3015.6589 | 45234.8831
2020-01-29 02:00 | 7.6309 | 8.0322 | 162.3687 | 3019.2542 | 45288.8132
2020-01-29 03:00 | 7.7664 | 8.1749 | 157.8279 | 3179.9237 | 47698.8549
2020-01-29 04:00 | 7.8968 | 8.3121 | 154.3998 | 3334.3985 | 50015.9773
2020-01-29 05:00 | 7.9766 | 8.3961 | 158.9771 | 3429.0514 | 51435.7704
2020-01-29 06:00 | 7.7786 | 8.1877 | 160.6365 | 3194.399 | 47915.9845
2020-01-29 07:00 | 7.3112 | 7.6957 | 162.6703 | 2661.0536 | 39915.8038
2020-01-29 08:00 | 6.7256 | 7.0793 | 163.2365 | 2061.909 | 30928.6352
2020-01-29 09:00 | 6.6639 | 7.0144 | 174.1458 | 2001.397 | 30020.9552
2020-01-29 10:00 | 5.4823 | 5.7706 | 202.5617 | 1096.2225 | 16443.3368
2020-01-29 11:00 | 4.8915 | 5.1487 | 234.9086 | 759.6572 | 11394.8583
2020-01-29 12:00 | 5.4228 | 5.708 | 270.5683 | 1059.1312 | 15886.9684
2020-01-29 13:00 | 6.5621 | 6.9072 | 283.1282 | 1912.632 | 28689.4807
2020-01-29 14:00 | 8.5222 | 8.9704 | 287.1413 | 4076.6278 | 61149.4173
2020-01-29 15:00 | 9.3939 | 9.8879 | 289.9567 | 4963.8824 | 74458.2356
2020-01-29 16:00 | 9.6963 | 10.2062 | 283.7331 | 5176.4417 | 77646.6252
2020-01-29 17:00 | 9.5102 | 10.0103 | 282.3681 | 5062.0386 | 75930.5793
2020-01-29 18:00 | 9.4638 | 9.9616 | 279.8219 | 5024.4176 | 75366.2641
2020-01-29 19:00 | 9.4704 | 9.9685 | 276.5585 | 5030.0944 | 75451.4155
2020-01-29 20:00 | 9.2639 | 9.7511 | 273.9335 | 4851.3928 | 72770.8923
2020-01-29 21:00 | 9.0048 | 9.4784 | 271.7344 | 4621.9229 | 69328.8438
2020-01-29 22:00 | 9.2743 | 9.7621 | 270.3871 | 4860.4064 | 72906.0955
2020-01-29 23:00 | 9.6492 | 10.1567 | 275.3963 | 5147.4884 | 77212.326
2020-01-30 00:00 | 9.9501 | 10.4734 | 276.8949 | 5332.4515 | 79986.7722
2020-01-30 01:00 | 10.3566 | 10.9013 | 277.3529 | 5501.2804 | 82519.2067
2020-01-30 02:00 | 10.9017 | 11.4751 | 277.3571 | 5646.3769 | 84695.6534
2020-01-30 03:00 | 11.2691 | 11.8618 | 278.6413 | 5686.0052 | 85290.078
2020-01-30 04:00 | 11.2356 | 11.8266 | 281.2002 | 5682.6966 | 85240.4494
2020-01-30 05:00 | 10.8428 | 11.4131 | 281.5347 | 5632.357 | 84485.3547
2020-01-30 06:00 | 10.7524 | 11.3179 | 280.649 | 5610.8564 | 84162.8457
2020-01-30 07:00 | 10.9203 | 11.4946 | 279.7565 | 5650.7798 | 84761.6976
2020-01-30 08:00 | 10.9696 | 11.5466 | 278.0846 | 5656.3798 | 84845.6966
2020-01-30 09:00 | 10.9298 | 11.5046 | 277.3143 | 5652.436 | 84786.5396
2020-01-30 10:00 | 12.0005 | 12.6317 | 279.0839 | 5700 | 85500
2020-01-30 11:00 | 11.5916 | 12.2012 | 283.8085 | 5699.4024 | 85491.0367
2020-01-30 12:00 | 10.6696 | 11.2308 | 285.9783 | 5591.1584 | 83867.3762
2020-01-30 13:00 | 10.0373 | 10.5652 | 284.8719 | 5372.9065 | 80593.5975
2020-01-30 14:00 | 9.7973 | 10.3126 | 283.461 | 5238.538 | 78578.0699
2020-01-30 15:00 | 9.9003 | 10.421 | 282.9124 | 5301.8547 | 79527.8202
2020-01-30 16:00 | 9.8235 | 10.3402 | 283.6498 | 5254.6767 | 78820.15
2020-01-30 17:00 | 10.0481 | 10.5766 | 285.4525 | 5377.25 | 80658.7506
2020-01-30 18:00 | 10.4512 | 11.0009 | 288.5467 | 5539.1945 | 83087.917
2020-01-30 19:00 | 9.7636 | 10.2771 | 286.1398 | 5217.846 | 78267.6903
2020-01-30 20:00 | 8.9353 | 9.4053 | 281.9863 | 4543.6586 | 68154.8784
2020-01-30 21:00 | 8.3435 | 8.7823 | 278.2158 | 3864.4843 | 57967.2639
2020-01-30 22:00 | 7.452 | 7.8439 | 270.0521 | 2817.8311 | 42267.4659
2020-01-30 23:00 | 7.2525 | 7.6339 | 260.0227 | 2595.6991 | 38935.4864
2020-01-31 00:00 | 7.1744 | 7.5518 | 251.0718 | 2508.7772 | 37631.6574
2020-01-31 01:00 | 7.3596 | 7.7466 | 242.9991 | 2714.9498 | 40724.2463
2020-01-31 02:00 | 7.5666 | 7.9646 | 233.7888 | 2945.5253 | 44182.8796
2020-01-31 03:00 | 7.6703 | 8.0737 | 229.7463 | 3066.0017 | 45990.0248
2020-01-31 04:00 | 7.906 | 8.3219 | 233.2875 | 3345.4113 | 50181.1697
2020-01-31 05:00 | 8.1678 | 8.5974 | 235.768 | 3655.8776 | 54838.1642
2020-01-31 06:00 | 8.1466 | 8.5751 | 234.236 | 3630.6915 | 54460.3728
2020-01-31 07:00 | 8.1058 | 8.5321 | 233.1422 | 3582.2203 | 53733.3045
2020-01-31 08:00 | 8.2773 | 8.7126 | 230.1551 | 3785.8621 | 56787.9319
2020-01-31 09:00 | 9.0128 | 9.4868 | 225.3904 | 4630.8657 | 69462.9856
2020-01-31 10:00 | 7.5087 | 7.9036 | 213.9754 | 2881.0586 | 43215.8783
2020-01-31 11:00 | 7.6697 | 8.0731 | 206.2544 | 3065.3102 | 45979.6528
2020-01-31 12:00 | 8.3588 | 8.7985 | 207.8844 | 3882.6797 | 58240.1961
2020-01-31 13:00 | 8.8522 | 9.3178 | 209.8905 | 4450.037 | 66750.5549
2020-01-31 14:00 | 8.64 | 9.0944 | 207.1457 | 4211.0414 | 63165.6207
2020-01-31 15:00 | 8.3684 | 8.8085 | 215.2403 | 3894.0096 | 58410.144
2020-01-31 16:00 | 7.8269 | 8.2386 | 228.4496 | 3251.641 | 48774.6146
2020-01-31 17:00 | 7.3642 | 7.7515 | 247.8124 | 2720.1168 | 40801.7515
2020-01-31 18:00 | 6.8584 | 7.2191 | 269.1767 | 2192.1896 | 32882.8433
2020-01-31 19:00 | 6.152 | 6.4756 | 274.0244 | 1564.9237 | 23473.8549
2020-01-31 20:00 | 6.8575 | 7.2182 | 275.9624 | 2191.348 | 32870.2205
2020-01-31 21:00 | 6.7007 | 7.0531 | 280.8249 | 2037.493 | 30562.3957
2020-01-31 22:00 | 6.3556 | 6.6899 | 278.3608 | 1736.2033 | 26043.0491
2020-01-31 23:00 | 6.7831 | 7.1398 | 281.4866 | 2118.3024 | 31774.5363
2020-02-01 00:00 | 7.0213 | 7.3906 | 290.0804 | 2352.0351 | 35280.5267
2020-02-01 01:00 | 7.1733 | 7.5505 | 300.2269 | 2507.4621 | 37611.9309
2020-02-01 02:00 | 7.0548 | 7.4259 | 308.2961 | 2384.9118 | 35773.6768
2020-02-01 03:00 | 6.7274 | 7.0812 | 313.549 | 2063.7097 | 30955.6461
2020-02-01 04:00 | 6.223 | 6.5503 | 316.5698 | 1622.8682 | 24343.0227
2020-02-01 05:00 | 5.4608 | 5.748 | 318.4413 | 1082.8431 | 16242.6471
2020-02-01 06:00 | 4.9402 | 5.2001 | 319.8667 | 785.4404 | 11781.6055
2020-02-01 07:00 | 4.4532 | 4.6874 | 315.3493 | 553.0919 | 8296.3784
2020-02-01 08:00 | 3.8389 | 4.0408 | 303.6934 | 312.3623 | 4685.4351
2020-02-01 09:00 | 3.7909 | 3.9903 | 290.046 | 295.2334 | 4428.5005
2020-02-01 10:00 | 3.8503 | 4.0528 | 285.1779 | 316.5858 | 4748.787
2020-02-01 11:00 | 4.3533 | 4.5822 | 288.4871 | 508.7059 | 7630.5878
2020-02-01 12:00 | 4.8756 | 5.132 | 285.9959 | 751.2824 | 11269.2362
2020-02-01 13:00 | 4.7948 | 5.047 | 267.0574 | 708.5787 | 10628.6798
2020-02-01 14:00 | 5.2765 | 5.554 | 245.4605 | 967.974 | 14519.6102
2020-02-01 15:00 | 6.1238 | 6.4459 | 235.4714 | 1544.1071 | 23161.6064
2020-02-01 16:00 | 6.9434 | 7.3086 | 231.8073 | 2275.6136 | 34134.2034
2020-02-01 17:00 | 7.7256 | 8.1319 | 230.5496 | 3131.5709 | 46973.564
2020-02-01 18:00 | 8.1561 | 8.5851 | 233.8818 | 3641.9742 | 54629.6128
2020-02-01 19:00 | 8.5598 | 9.01 | 236.7829 | 4120.7402 | 61811.1034
2020-02-01 20:00 | 9.1568 | 9.6384 | 240.3151 | 4758.7773 | 71381.6588
2020-02-01 21:00 | 9.2413 | 9.7274 | 244.1908 | 4831.9081 | 72478.6215
2020-02-01 22:00 | 8.5701 | 9.0208 | 246.5444 | 4132.2944 | 61984.416
2020-02-01 23:00 | 8.414 | 8.8565 | 243.758 | 3948.1363 | 59222.0449
2020-02-02 00:00 | 8.853 | 9.3186 | 240.9903 | 4450.9236 | 66763.8537
2020-02-02 01:00 | 9.3522 | 9.8441 | 238.1591 | 4927.8359 | 73917.5386
2020-02-02 02:00 | 9.6692 | 10.1778 | 234.3072 | 5159.8239 | 77397.3588
2020-02-02 03:00 | 10.0161 | 10.5429 | 229.6684 | 5364.3788 | 80465.6824
2020-02-02 04:00 | 10.4089 | 10.9564 | 227.7359 | 5522.3441 | 82835.1613
2020-02-02 05:00 | 10.6873 | 11.2494 | 229.6405 | 5595.3701 | 83930.5521
2020-02-02 06:00 | 10.7918 | 11.3594 | 236.5158 | 5620.2165 | 84303.2478
2020-02-02 07:00 | 10.6836 | 11.2455 | 243.5169 | 5594.4932 | 83917.3985
2020-02-02 08:00 | 10.3686 | 10.914 | 251.7813 | 5506.1383 | 82592.0749
2020-02-02 09:00 | 10.4007 | 10.9477 | 263.9291 | 5519.0316 | 82785.4734
2020-02-02 10:00 | 9.8929 | 10.4133 | 273.2684 | 5297.3396 | 79460.0939
2020-02-02 11:00 | 9.4337 | 9.9299 | 274.059 | 4998.3437 | 74975.1558
2020-02-02 12:00 | 10.0117 | 10.5382 | 275.0427 | 5362.6084 | 80439.1254
2020-02-02 13:00 | 10.6543 | 11.2147 | 276.3352 | 5587.5116 | 83812.6742
2020-02-02 14:00 | 10.3999 | 10.9469 | 277.8188 | 5518.6987 | 82780.4799
2020-02-02 15:00 | 9.8502 | 10.3683 | 275.9923 | 5271.0735 | 79066.1024
2020-02-02 16:00 | 9.8261 | 10.3428 | 272.3877 | 5256.2234 | 78843.3511
2020-02-02 17:00 | 10.0427 | 10.5708 | 265.6653 | 5375.0636 | 80625.9542
2020-02-02 18:00 | 10.6644 | 11.2253 | 264.1025 | 5589.9265 | 83848.8968
2020-02-02 19:00 | 10.9627 | 11.5393 | 265.3021 | 5655.6926 | 84835.3892
2020-02-02 20:00 | 11.2699 | 11.8627 | 267.2248 | 5686.0924 | 85291.3864
2020-02-02 21:00 | 11.0646 | 11.6466 | 268.3911 | 5665.778 | 84986.6694
2020-02-02 22:00 | 11.2328 | 11.8236 | 270.0292 | 5682.4174 | 85236.2612
2020-02-02 23:00 | 10.8423 | 11.4126 | 270.9855 | 5632.2433 | 84483.6498
2020-02-03 00:00 | 10.1389 | 10.6722 | 275.6716 | 5413.773 | 81206.5955
2020-02-03 01:00 | 9.14 | 9.6207 | 279.6021 | 4744.2141 | 71163.211
2020-02-03 02:00 | 8.0733 | 8.4979 | 284.1914 | 3543.63 | 53154.4507
2020-02-03 03:00 | 6.9332 | 7.2978 | 282.2671 | 2265.5672 | 33983.508
2020-02-03 04:00 | 6.1077 | 6.429 | 275.2332 | 1532.2776 | 22984.1641
2020-02-03 05:00 | 6.0503 | 6.3685 | 271.4067 | 1489.9595 | 22349.393
2020-02-03 06:00 | 6.7729 | 7.1291 | 280.0418 | 2108.2907 | 31624.3603
2020-02-03 07:00 | 7.185 | 7.5629 | 292.8257 | 2520.5511 | 37808.2667
2020-02-03 08:00 | 6.9421 | 7.3072 | 300.3618 | 2274.3529 | 34115.2933
2020-02-03 09:00 | 6.9245 | 7.2887 | 302.0218 | 2257.0389 | 33855.5839
2020-02-03 10:00 | 7.3612 | 7.7483 | 297.2228 | 2716.7498 | 40751.2472
2020-02-03 11:00 | 8.006 | 8.4271 | 293.0427 | 3463.9113 | 51958.6702
2020-02-03 12:00 | 8.5404 | 8.9895 | 293.7763 | 4098.1944 | 61472.916
2020-02-03 13:00 | 9.0791 | 9.5567 | 296.358 | 4691.5739 | 70373.6082
2020-02-03 14:00 | 9.2842 | 9.7725 | 297.8845 | 4868.9569 | 73034.3528
2020-02-03 15:00 | 8.8436 | 9.3087 | 298.7943 | 4440.3254 | 66604.8809
2020-02-03 16:00 | 8.9869 | 9.4596 | 299.2494 | 4601.7723 | 69026.5842
2020-02-03 17:00 | 9.2594 | 9.7464 | 298.9628 | 4847.5022 | 72712.5331
2020-02-03 18:00 | 9.4523 | 9.9495 | 298.0724 | 5014.4717 | 75217.0752
2020-02-03 19:00 | 9.3255 | 9.816 | 297.3453 | 4904.7129 | 73570.6941
2020-02-03 20:00 | 9.0267 | 9.5015 | 294.5117 | 4646.1921 | 69692.881
2020-02-03 21:00 | 8.8789 | 9.3459 | 289.914 | 4480.0832 | 67201.2478
2020-02-03 22:00 | 8.7185 | 9.177 | 287.9724 | 4299.4094 | 64491.1411
2020-02-03 23:00 | 8.5298 | 8.9784 | 284.5767 | 4085.6704 | 61285.0565
2020-02-04 00:00 | 8.8618 | 9.3279 | 282.5117 | 4460.8235 | 66912.3526
2020-02-04 01:00 | 8.3486 | 8.7877 | 281.5836 | 3870.5678 | 58058.5175
2020-02-04 02:00 | 7.617 | 8.0176 | 278.3702 | 3002.8242 | 45042.3626
2020-02-04 03:00 | 6.8218 | 7.1806 | 273.0811 | 2156.3066 | 32344.5985
2020-02-04 04:00 | 7.1739 | 7.5512 | 264.5978 | 2508.2216 | 37623.3233
2020-02-04 05:00 | 6.62 | 6.9682 | 255.3258 | 1962.1733 | 29432.5997
2020-02-04 06:00 | 5.8111 | 6.1168 | 240.9497 | 1313.7444 | 19706.1653
2020-02-04 07:00 | 5.552 | 5.844 | 228.988 | 1139.6715 | 17095.0728
2020-02-04 08:00 | 4.4074 | 4.6392 | 213.2753 | 532.7235 | 7990.853
2020-02-04 09:00 | 3.7799 | 3.9787 | 196.8234 | 291.916 | 4378.7407
2020-02-04 10:00 | 4.1149 | 4.3313 | 183.6656 | 414.6174 | 6219.2605
2020-02-04 11:00 | 5.3721 | 5.6546 | 181.9282 | 1027.5433 | 15413.1488
2020-02-04 12:00 | 5.5508 | 5.8427 | 188.1898 | 1138.8819 | 17083.2279
2020-02-04 13:00 | 5.1971 | 5.4704 | 194.1154 | 921.1418 | 13817.1267
2020-02-04 14:00 | 4.0591 | 4.2725 | 172.3648 | 393.9351 | 5909.0266
2020-02-04 15:00 | 4.5019 | 4.7387 | 159.7016 | 574.7191 | 8620.786
2020-02-04 16:00 | 4.6353 | 4.8791 | 158.9721 | 633.9617 | 9509.4251
2020-02-04 17:00 | 4.5045 | 4.7415 | 149.0345 | 575.8978 | 8638.4667
2020-02-04 18:00 | 4.0403 | 4.2528 | 135.0115 | 387.0022 | 5805.0332
2020-02-04 19:00 | 4.0201 | 4.2315 | 100.0799 | 379.491 | 5692.3644
2020-02-04 20:00 | 5.0719 | 5.3387 | 73.1445 | 855.0032 | 12825.0486
2020-02-04 21:00 | 5.8572 | 6.1652 | 63.4042 | 1347.6486 | 20214.7285
2020-02-04 22:00 | 7.2636 | 7.6456 | 60.1631 | 2608.0246 | 39120.369
2020-02-04 23:00 | 8.0051 | 8.4261 | 60.7602 | 3462.8094 | 51942.1415
2020-02-05 00:00 | 8.9483 | 9.419 | 56.4298 | 4558.2833 | 68374.2501
2020-02-05 01:00 | 9.6905 | 10.2002 | 54.4351 | 5172.9048 | 77593.5718
2020-02-05 02:00 | 10.2869 | 10.828 | 54.0121 | 5473.2849 | 82099.273
2020-02-05 03:00 | 10.7488 | 11.3141 | 50.7368 | 5609.9834 | 84149.7503
2020-02-05 04:00 | 11.2198 | 11.8099 | 46.8471 | 5681.1328 | 85216.9914
2020-02-05 05:00 | 11.8909 | 12.5163 | 44.2294 | 5700 | 85500
2020-02-05 06:00 | 12.1105 | 12.7474 | 42.0439 | 5700 | 85500
2020-02-05 07:00 | 12.2423 | 12.8861 | 38.5559 | 5700 | 85500
2020-02-05 08:00 | 11.253 | 11.8448 | 30.2193 | 5684.4137 | 85266.2048
2020-02-05 09:00 | 11.6037 | 12.2139 | 28.9415 | 5699.4279 | 85491.4185
2020-02-05 10:00 | 11.4645 | 12.0675 | 33.42 | 5699.135 | 85487.0246
2020-02-05 11:00 | 11.083 | 11.6659 | 29.5078 | 5667.5905 | 85013.858
2020-02-05 12:00 | 10.8562 | 11.4271 | 24.8196 | 5635.5334 | 84533.0006
2020-02-05 13:00 | 10.5472 | 11.1019 | 19.2381 | 5562.0285 | 83430.4272
2020-02-05 14:00 | 10.1496 | 10.6834 | 13.8255 | 5418.0516 | 81270.7738
2020-02-05 15:00 | 10.6742 | 11.2356 | 11.9931 | 5592.254 | 83883.8098
2020-02-05 16:00 | 11.3107 | 11.9056 | 12.6057 | 5690.123 | 85351.8451
2020-02-05 17:00 | 11.3087 | 11.9035 | 14.402 | 5689.9273 | 85348.91
2020-02-05 18:00 | 10.155 | 10.6891 | 13.9072 | 5420.2218 | 81303.3266
2020-02-05 19:00 | 9.6579 | 10.1658 | 12.3667 | 5152.8399 | 77292.5983
2020-02-05 20:00 | 9.4743 | 9.9726 | 11.4994 | 5033.4609 | 75501.9128
2020-02-05 21:00 | 8.974 | 9.446 | 10.9922 | 4587.2578 | 68808.8669
2020-02-05 22:00 | 8.4087 | 8.851 | 8.2234 | 3941.9047 | 59128.5702
2020-02-05 23:00 | 7.3983 | 7.7874 | 6.1884 | 2758.052 | 41370.7798
2020-02-06 00:00 | 7.1549 | 7.5312 | 356.412 | 2487.0297 | 37305.4458
2020-02-06 01:00 | 7.5288 | 7.9248 | 347.908 | 2903.4652 | 43551.9785
2020-02-06 02:00 | 7.527 | 7.9229 | 343.3473 | 2901.4139 | 43521.2089
2020-02-06 03:00 | 6.7374 | 7.0917 | 335.7867 | 2073.5056 | 31102.5847
2020-02-06 04:00 | 6.5561 | 6.9009 | 322.7088 | 1907.531 | 28612.9644
2020-02-06 05:00 | 6.2448 | 6.5733 | 311.0873 | 1641.5018 | 24622.5265
2020-02-06 06:00 | 5.7409 | 6.0429 | 293.0023 | 1262.0159 | 18930.2381
2020-02-06 07:00 | 6.0882 | 6.4084 | 275.3641 | 1517.8515 | 22767.7722
2020-02-06 08:00 | 6.2337 | 6.5616 | 273.139 | 1632.0147 | 24480.2209
2020-02-06 09:00 | 7.1545 | 7.5308 | 276.0338 | 2486.5776 | 37298.664
2020-02-06 10:00 | 7.9988 | 8.4195 | 277.9202 | 3455.3346 | 51830.0194
2020-02-06 11:00 | 8.8167 | 9.2804 | 283.5834 | 4410.0671 | 66151.0065
2020-02-06 12:00 | 9.3385 | 9.8297 | 283.3254 | 4915.9947 | 73739.9211
2020-02-06 13:00 | 9.8015 | 10.317 | 280.675 | 5241.1173 | 78616.76
2020-02-06 14:00 | 9.2708 | 9.7584 | 279.7791 | 4857.3731 | 72860.5972
2020-02-06 15:00 | 9.8749 | 10.3943 | 286.1223 | 5286.2773 | 79294.1595
2020-02-06 16:00 | 9.882 | 10.4018 | 291.8037 | 5290.6411 | 79359.617
2020-02-06 17:00 | 9.5481 | 10.0503 | 297.6924 | 5085.3799 | 76280.698
2020-02-06 18:00 | 9.0117 | 9.4856 | 304.0294 | 4629.64 | 69444.5993
2020-02-06 19:00 | 8.7491 | 9.2093 | 313.5117 | 4333.9199 | 65008.7991
2020-02-06 20:00 | 8.8946 | 9.3624 | 330.6599 | 4497.7429 | 67466.1433
2020-02-06 21:00 | 10.367 | 10.9122 | 351.6082 | 5505.4699 | 82582.0481
2020-02-06 22:00 | 10.4356 | 10.9845 | 354.6076 | 5533.0817 | 82996.225
2020-02-06 23:00 | 10.7363 | 11.301 | 354.159 | 5607.023 | 84105.3454
2020-02-07 00:00 | 10.5909 | 11.1479 | 353.1433 | 5572.4306 | 83586.4596
2020-02-07 01:00 | 9.499 | 9.9986 | 351.5808 | 5054.8374 | 75822.5611
2020-02-07 02:00 | 8.9456 | 9.4161 | 350.336 | 4555.2279 | 68328.418
2020-02-07 03:00 | 8.4846 | 8.9308 | 347.3309 | 4031.9624 | 60479.4355
2020-02-07 04:00 | 8.2397 | 8.6731 | 341.1805 | 3741.228 | 56118.4198
2020-02-07 05:00 | 8.197 | 8.6282 | 334.2658 | 3690.5552 | 55358.3281
2020-02-07 06:00 | 8.3959 | 8.8375 | 328.9788 | 3926.6466 | 58899.6983
2020-02-07 07:00 | 7.9513 | 8.3695 | 326.18 | 3399.032 | 50985.4795
2020-02-07 08:00 | 8.49 | 8.9365 | 328.7593 | 4038.3527 | 60575.291
2020-02-07 09:00 | 10.7384 | 11.3032 | 341.6564 | 5607.5126 | 84112.6887
2020-02-07 10:00 | 8.7278 | 9.1869 | 335.7332 | 4309.9464 | 64649.1954
2020-02-07 11:00 | 9.0406 | 9.5161 | 331.3868 | 4658.2479 | 69873.718
2020-02-07 12:00 | 9.6283 | 10.1347 | 335.3617 | 5134.6679 | 77020.0184
2020-02-07 13:00 | 10.343 | 10.887 | 341.3223 | 5495.8203 | 82437.3049
2020-02-07 14:00 | 11.0689 | 11.651 | 346.2519 | 5666.1964 | 84992.9454
2020-02-07 15:00 | 10.5482 | 11.1029 | 349.1405 | 5562.2645 | 83433.9669
2020-02-07 16:00 | 9.9015 | 10.4223 | 352.8585 | 5302.607 | 79539.1051
2020-02-07 17:00 | 9.3321 | 9.8229 | 355.3925 | 4910.4243 | 73656.3644
2020-02-07 18:00 | 8.7473 | 9.2073 | 355.0107 | 4331.8427 | 64977.6408
2020-02-07 19:00 | 8.4411 | 8.8851 | 352.2632 | 3980.3771 | 59705.657
2020-02-07 20:00 | 8.1785 | 8.6087 | 348.9018 | 3668.5606 | 55028.4092
2020-02-07 21:00 | 7.9925 | 8.4129 | 343.8881 | 3447.9085 | 51718.6277
2020-02-07 22:00 | 8.8374 | 9.3022 | 344.1014 | 4433.3788 | 66500.6821
2020-02-07 23:00 | 8.5122 | 8.9599 | 342.9023 | 4064.7243 | 60970.8651
2020-02-08 00:00 | 7.8678 | 8.2816 | 340.6989 | 3300.0608 | 49500.9125
2020-02-08 01:00 | 7.315 | 7.6997 | 336.0428 | 2665.2718 | 39979.077
2020-02-08 02:00 | 7.3987 | 7.7878 | 331.9222 | 2758.4846 | 41377.2688
2020-02-08 03:00 | 7.0029 | 7.3712 | 327.7104 | 2333.9811 | 35009.7171
2020-02-08 04:00 | 7.2146 | 7.594 | 326.2465 | 2553.4834 | 38302.2514
2020-02-08 05:00 | 6.7002 | 7.0526 | 320.7052 | 2036.9834 | 30554.7515
2020-02-08 06:00 | 6.72 | 7.0734 | 317.7998 | 2056.4113 | 30846.1693
2020-02-08 07:00 | 6.5823 | 6.9285 | 313.6259 | 1929.9584 | 28949.376
2020-02-08 08:00 | 5.843 | 6.1503 | 308.6212 | 1337.2196 | 20058.2943
2020-02-08 09:00 | 6.0702 | 6.3894 | 304.0316 | 1504.5946 | 22568.9187
2020-02-08 10:00 | 5.7888 | 6.0933 | 301.376 | 1297.3013 | 19459.5201
2020-02-08 11:00 | 5.8299 | 6.1366 | 293.2319 | 1327.5927 | 19913.8903
2020-02-08 12:00 | 6.421 | 6.7587 | 288.2891 | 1792.0347 | 26880.5208
2020-02-08 13:00 | 6.6816 | 7.033 | 283.1307 | 2018.7312 | 30280.9676
2020-02-08 14:00 | 6.4851 | 6.8262 | 275.4427 | 1846.8671 | 27703.0066
2020-02-08 15:00 | 6.6127 | 6.9605 | 275.9727 | 1955.9014 | 29338.5204
2020-02-08 16:00 | 6.3922 | 6.7284 | 278.6334 | 1767.4904 | 26512.3553
2020-02-08 17:00 | 6.214 | 6.5408 | 281.8966 | 1615.1523 | 24227.2843
2020-02-08 18:00 | 6.0195 | 6.3361 | 284.7151 | 1467.2898 | 22009.3473
2020-02-08 19:00 | 5.5228 | 5.8133 | 288.6369 | 1121.4565 | 16821.847
2020-02-08 20:00 | 5.1256 | 5.3952 | 289.8061 | 883.3932 | 13250.8981
2020-02-08 21:00 | 4.7724 | 5.0234 | 291.6795 | 696.7346 | 10451.0196
2020-02-08 22:00 | 4.3799 | 4.6103 | 294.9296 | 520.5414 | 7808.1214
2020-02-08 23:00 | 4.4729 | 4.7082 | 294.6725 | 561.8534 | 8427.8007
2020-02-09 00:00 | 4.1236 | 4.3405 | 295.9288 | 417.8429 | 6267.6439
2020-02-09 01:00 | 3.6696 | 3.8626 | 296.2329 | 258.7019 | 3880.5288
2020-02-09 02:00 | 3.5432 | 3.7296 | 288.8307 | 220.6639 | 3309.9584
2020-02-09 03:00 | 3.3315 | 3.5068 | 279.5213 | 156.9335 | 2354.0031
2020-02-09 04:00 | 3.2726 | 3.4447 | 273.0336 | 143.1649 | 2147.4731
2020-02-09 05:00 | 3.5406 | 3.7268 | 265.8131 | 219.8718 | 3298.0766
2020-02-09 06:00 | 3.4171 | 3.5969 | 255.9466 | 182.7032 | 2740.5478
2020-02-09 07:00 | 3.1538 | 3.3197 | 242.6452 | 116.4127 | 1746.1903
2020-02-09 08:00 | 2.769 | 2.9147 | 232.6837 | 0 | 0
2020-02-09 09:00 | 2.7855 | 2.932 | 225.9506 | 0 | 0
2020-02-09 10:00 | 2.6608 | 2.8008 | 218.8009 | 0 | 0
2020-02-09 11:00 | 3.1629 | 3.3293 | 209.9326 | 118.4685 | 1777.0278
2020-02-09 12:00 | 3.9524 | 4.1603 | 200.6836 | 354.4282 | 5316.4234
2020-02-09 13:00 | 4.6069 | 4.8492 | 193.7744 | 621.3764 | 9320.6466
2020-02-09 14:00 | 5.2084 | 5.4823 | 187.2653 | 927.1223 | 13906.8347
2020-02-09 15:00 | 6.625 | 6.9734 | 184.5591 | 1966.4035 | 29496.053
2020-02-09 16:00 | 8.049 | 8.4724 | 182.8933 | 3514.8875 | 52723.3123
2020-02-09 17:00 | 8.5514 | 9.0012 | 187.2791 | 4111.2391 | 61668.5859
2020-02-09 18:00 | 8.7598 | 9.2205 | 191.6532 | 4345.9642 | 65189.4636
2020-02-09 19:00 | 9.1781 | 9.6609 | 192.2354 | 4777.2333 | 71658.5001
2020-02-09 20:00 | 9.4352 | 9.9314 | 194.1009 | 4999.6402 | 74994.603
2020-02-09 21:00 | 9.4638 | 9.9615 | 196.3154 | 5024.3866 | 75365.7985
2020-02-09 22:00 | 9.7931 | 10.3082 | 194.7447 | 5235.9696 | 78539.544
2020-02-09 23:00 | 10.2364 | 10.7748 | 191.1822 | 5452.9663 | 81794.4947
2020-02-10 00:00 | 10.7715 | 11.338 | 189.0385 | 5615.384 | 84230.7603
2020-02-10 01:00 | 11.3722 | 11.9703 | 187.2745 | 5696.2089 | 85443.1337
2020-02-10 02:00 | 11.5394 | 12.1463 | 188.7103 | 5699.2926 | 85489.3897
2020-02-10 03:00 | 11.9855 | 12.6159 | 188.0422 | 5700 | 85500
2020-02-10 04:00 | 12.6794 | 13.3463 | 189.1014 | 5700 | 85500
2020-02-10 05:00 | 13.4221 | 14.1281 | 188.6911 | 5700 | 85500
2020-02-10 06:00 | 13.3328 | 14.034 | 190.7729 | 5700 | 85500
2020-02-10 07:00 | 13.6172 | 14.3334 | 191.7068 | 5700 | 85500
2020-02-10 08:00 | 12.9837 | 13.6666 | 184.2632 | 5700 | 85500
2020-02-10 09:00 | 12.3686 | 13.0191 | 193.228 | 5700 | 85500
2020-02-10 10:00 | 11.6705 | 12.2843 | 192.1043 | 5699.5685 | 85493.5279
2020-02-10 11:00 | 11.2703 | 11.863 | 189.7354 | 5686.123 | 85291.8453
2020-02-10 12:00 | 11.6148 | 12.2256 | 185.8797 | 5699.4513 | 85491.7693
2020-02-10 13:00 | 13.4343 | 14.1409 | 189.6396 | 5700 | 85500
2020-02-10 14:00 | 13.4588 | 14.1666 | 185.1131 | 5700 | 85500
2020-02-10 15:00 | 13.6068 | 14.3225 | 189.9253 | 5700 | 85500
2020-02-10 16:00 | 13.6009 | 14.3162 | 198.1484 | 5700 | 85500
2020-02-10 17:00 | 12.697 | 13.3648 | 207.0443 | 5700 | 85500
2020-02-10 18:00 | 11.9981 | 12.6291 | 213.1719 | 5700 | 85500
2020-02-10 19:00 | 10.8518 | 11.4225 | 212.5649 | 5634.4861 | 84517.2915
2020-02-10 20:00 | 10.1202 | 10.6525 | 209.3133 | 5406.2394 | 81093.5912
2020-02-10 21:00 | 9.9199 | 10.4417 | 207.0606 | 5313.943 | 79709.1448
2020-02-10 22:00 | 9.9635 | 10.4875 | 210.7622 | 5340.7154 | 80110.7305
2020-02-10 23:00 | 10.6016 | 11.1592 | 218.2165 | 5574.9866 | 83624.7984
2020-02-11 00:00 | 10.392 | 10.9386 | 229.8512 | 5515.5312 | 82732.9678
2020-02-11 01:00 | 10.8015 | 11.3696 | 245.5338 | 5622.5187 | 84337.7809
2020-02-11 02:00 | 10.5566 | 11.1118 | 257.7612 | 5564.2652 | 83463.9786
2020-02-11 03:00 | 9.6759 | 10.1848 | 261.1302 | 5163.9374 | 77459.0612
2020-02-11 04:00 | 9.7226 | 10.234 | 263.2133 | 5192.6534 | 77889.8009
2020-02-11 05:00 | 8.9421 | 9.4124 | 263.5246 | 4551.2777 | 68269.1648
2020-02-11 06:00 | 7.5763 | 7.9747 | 255.5224 | 2956.2627 | 44343.9403
2020-02-11 07:00 | 7.5878 | 7.9869 | 244.7083 | 2969.1238 | 44536.8571
2020-02-11 08:00 | 6.5409 | 6.885 | 234.6862 | 1894.5918 | 28418.8765
2020-02-11 09:00 | 6.4571 | 6.7967 | 231.472 | 1822.9336 | 27344.0039
2020-02-11 10:00 | 6.4702 | 6.8105 | 225.8242 | 1834.1389 | 27512.0841
2020-02-11 11:00 | 6.6793 | 7.0306 | 208.8797 | 2016.5298 | 30247.9471
2020-02-11 12:00 | 7.6326 | 8.0341 | 200.2934 | 3021.3498 | 45320.2473
2020-02-11 13:00 | 8.9119 | 9.3806 | 203.4514 | 4517.2289 | 67758.4332
2020-02-11 14:00 | 9.4282 | 9.924 | 214.4404 | 4993.5565 | 74903.348
2020-02-11 15:00 | 8.9695 | 9.4413 | 217.0158 | 4582.1477 | 68732.2156
2020-02-11 16:00 | 7.9739 | 8.3933 | 221.0771 | 3425.843 | 51387.6457
2020-02-11 17:00 | 7.6171 | 8.0178 | 233.3553 | 3002.9868 | 45044.8019
2020-02-11 18:00 | 7.835 | 8.2471 | 260.615 | 3261.1811 | 48917.7159
2020-02-11 19:00 | 9.2844 | 9.7727 | 286.9604 | 4869.1499 | 73037.2488
2020-02-11 20:00 | 9.747 | 10.2596 | 293.1077 | 5207.6273 | 78114.4101
2020-02-11 21:00 | 9.1063 | 9.5852 | 289.4938 | 4715.04 | 70725.5993
2020-02-11 22:00 | 8.9085 | 9.3771 | 292.5412 | 4513.4794 | 67702.1917
2020-02-11 23:00 | 8.1951 | 8.6261 | 286.1309 | 3688.2369 | 55323.5531
2020-02-12 00:00 | 8.5245 | 8.9729 | 282.1824 | 4079.4044 | 61191.066
2020-02-12 01:00 | 8.9172 | 9.3862 | 280.5289 | 4523.2134 | 67848.2016
2020-02-12 02:00 | 9.1755 | 9.6581 | 278.7062 | 4774.9321 | 71623.9808
2020-02-12 03:00 | 9.429 | 9.9249 | 278.1285 | 4994.2967 | 74914.4504
2020-02-12 04:00 | 9.7868 | 10.3015 | 279.697 | 5232.0978 | 78481.4669
2020-02-12 05:00 | 9.6836 | 10.1929 | 281.0117 | 5168.6487 | 77529.73
2020-02-12 06:00 | 9.4871 | 9.9861 | 278.8874 | 5044.5921 | 75668.8816
2020-02-12 07:00 | 9.4869 | 9.9859 | 278.9859 | 5044.3781 | 75665.6716
2020-02-12 08:00 | 8.8241 | 9.2882 | 277.6496 | 4418.36 | 66275.4007
2020-02-12 09:00 | 9.4861 | 9.9851 | 279.066 | 5043.7156 | 75655.7339
2020-02-12 10:00 | 7.1033 | 7.4769 | 274.4615 | 2432.4321 | 36486.4808
2020-02-12 11:00 | 7.5222 | 7.9178 | 273.6592 | 2896.0455 | 43440.6828
2020-02-12 12:00 | 7.9828 | 8.4026 | 270.5681 | 3436.3673 | 51545.5088
2020-02-12 13:00 | 8.4961 | 8.9429 | 270.3935 | 4045.5877 | 60683.8151
2020-02-12 14:00 | 9.5444 | 10.0464 | 274.8962 | 5083.0759 | 76246.1384
2020-02-12 15:00 | 8.719 | 9.1776 | 279.1352 | 4300.0227 | 64500.3406
2020-02-12 16:00 | 8.6518 | 9.1068 | 274.4515 | 4224.2661 | 63363.9921
2020-02-12 17:00 | 9.4028 | 9.8973 | 272.6106 | 4971.5789 | 74573.684
2020-02-12 18:00 | 9.5607 | 10.0635 | 274.4404 | 5093.105 | 76396.5755
2020-02-12 19:00 | 9.7186 | 10.2297 | 275.987 | 5190.1422 | 77852.1323
2020-02-12 20:00 | 9.3038 | 9.7931 | 277.2177 | 4885.9233 | 73288.8501
2020-02-12 21:00 | 8.7915 | 9.2539 | 273.806 | 4381.6215 | 65724.322
2020-02-12 22:00 | 9.1457 | 9.6267 | 273.3969 | 4749.139 | 71237.0857
2020-02-12 23:00 | 9.3016 | 9.7908 | 273.6088 | 4884.0643 | 73260.9643
2020-02-13 00:00 | 8.8662 | 9.3325 | 274.8234 | 4465.7644 | 66986.466
2020-02-13 01:00 | 8.4289 | 8.8722 | 272.314 | 3965.8957 | 59488.4353
2020-02-13 02:00 | 8.6654 | 9.1211 | 268.255 | 4239.6122 | 63594.1824
2020-02-13 03:00 | 8.6995 | 9.157 | 267.4263 | 4277.9997 | 64169.9951
2020-02-13 04:00 | 8.8731 | 9.3398 | 266.5793 | 4473.5887 | 67103.8309
2020-02-13 05:00 | 8.6832 | 9.1399 | 266.9436 | 4259.6523 | 63894.7844
2020-02-13 06:00 | 8.2834 | 8.7191 | 266.0313 | 3793.1535 | 56897.3022
2020-02-13 07:00 | 8.2989 | 8.7354 | 269.652 | 3811.5118 | 57172.6764
2020-02-13 08:00 | 8.4587 | 8.9035 | 275.5448 | 4001.1945 | 60017.9168
2020-02-13 09:00 | 7.9341 | 8.3514 | 274.6407 | 3378.6743 | 50680.1141
2020-02-13 10:00 | 8.4732 | 8.9188 | 278.7159 | 4018.4024 | 60276.0363
2020-02-13 11:00 | 10.5255 | 11.0791 | 288.5068 | 5556.8813 | 83353.2197
2020-02-13 12:00 | 9.5703 | 10.0736 | 292.9363 | 5098.9792 | 76484.6875
2020-02-13 13:00 | 8.6433 | 9.0979 | 289.6747 | 4214.7305 | 63220.9575
2020-02-13 14:00 | 8.3551 | 8.7946 | 282.8009 | 3878.2586 | 58173.8787
2020-02-13 15:00 | 7.9157 | 8.332 | 279.9829 | 3356.8588 | 50352.8814
2020-02-13 16:00 | 7.4183 | 7.8084 | 275.7602 | 2780.3212 | 41704.8183
2020-02-13 17:00 | 7.3411 | 7.7272 | 267.0203 | 2694.3482 | 40415.2224
2020-02-13 18:00 | 7.6219 | 8.0228 | 260.6771 | 3008.6797 | 45130.1959
2020-02-13 19:00 | 7.8657 | 8.2793 | 258.2713 | 3297.5453 | 49463.179
2020-02-13 20:00 | 7.6725 | 8.0761 | 257.1974 | 3068.661 | 46029.9155
2020-02-13 21:00 | 7.0397 | 7.41 | 254.1125 | 2370.1117 | 35551.6754
2020-02-13 22:00 | 7.1874 | 7.5654 | 245.2493 | 2523.2223 | 37848.3344
2020-02-13 23:00 | 7.5562 | 7.9537 | 238.4235 | 2933.9646 | 44009.4692
2020-02-14 00:00 | 7.3643 | 7.7516 | 236.478 | 2720.1882 | 40802.8228
2020-02-14 01:00 | 6.6283 | 6.9769 | 230.9269 | 1969.2201 | 29538.301
2020-02-14 02:00 | 6.3986 | 6.7352 | 219.2616 | 1772.959 | 26594.3849
2020-02-14 03:00 | 6.3049 | 6.6365 | 207.8082 | 1692.8342 | 25392.5128
2020-02-14 04:00 | 6.5106 | 6.853 | 195.2486 | 1868.6686 | 28030.0297
2020-02-14 05:00 | 7.0033 | 7.3717 | 185.3699 | 2334.3803 | 35015.7051
2020-02-14 06:00 | 7.3455 | 7.7319 | 175.706 | 2699.3071 | 40489.6058
2020-02-14 07:00 | 7.4368 | 7.828 | 177.8363 | 2800.9791 | 42014.6869
2020-02-14 08:00 | 7.4031 | 7.7924 | 179.069 | 2763.4003 | 41451.0044
2020-02-14 09:00 | 6.3462 | 6.68 | 176.3028 | 1728.154 | 25922.3105
2020-02-14 10:00 | 6.1436 | 6.4667 | 175.8516 | 1558.6917 | 23380.3757
2020-02-14 11:00 | 5.7927 | 6.0973 | 173.3361 | 1300.1373 | 19502.0602
2020-02-14 12:00 | 5.4723 | 5.7602 | 170.1806 | 1090.0092 | 16350.1376
2020-02-14 13:00 | 5.6453 | 5.9422 | 163.9194 | 1197.7941 | 17966.9121
2020-02-14 14:00 | 6.2917 | 6.6226 | 151.3107 | 1681.5725 | 25223.5881
2020-02-14 15:00 | 7.0169 | 7.386 | 147.7698 | 2347.7477 | 35216.2159
2020-02-14 16:00 | 7.5265 | 7.9223 | 149.9862 | 2900.8415 | 43512.623
2020-02-14 17:00 | 7.4603 | 7.8526 | 156.4932 | 2827.0856 | 42406.2843
2020-02-14 18:00 | 7.0272 | 7.3968 | 165.1402 | 2357.8346 | 35367.5189
2020-02-14 19:00 | 6.1931 | 6.5188 | 172.6134 | 1597.2484 | 23958.7264
2020-02-14 20:00 | 5.5724 | 5.8655 | 181.3296 | 1152.3681 | 17285.5214
2020-02-14 21:00 | 5.3126 | 5.592 | 190.9427 | 990.4918 | 14857.3775
2020-02-14 22:00 | 4.5393 | 4.778 | 196.5038 | 591.3169 | 8869.7537
2020-02-14 23:00 | 4.1236 | 4.3405 | 214.2749 | 417.8412 | 6267.6183
2020-02-15 00:00 | 3.7542 | 3.9516 | 237.7342 | 284.1687 | 4262.5307
2020-02-15 01:00 | 3.7982 | 3.998 | 261.821 | 297.4275 | 4461.4124
2020-02-15 02:00 | 4.2368 | 4.4596 | 282.4801 | 459.7902 | 6896.8533
2020-02-15 03:00 | 4.7329 | 4.9818 | 296.0586 | 677.3331 | 10159.9966
2020-02-15 04:00 | 5.0984 | 5.3665 | 306.4464 | 868.9813 | 13034.7201
2020-02-15 05:00 | 4.9431 | 5.203 | 313.2488 | 786.9239 | 11803.8592
2020-02-15 06:00 | 4.412 | 4.6441 | 317.3441 | 534.7911 | 8021.866
2020-02-15 07:00 | 4.1454 | 4.3635 | 319.2028 | 425.9363 | 6389.0438
2020-02-15 08:00 | 3.9287 | 4.1353 | 321.9314 | 345.6269 | 5184.404
2020-02-15 09:00 | 3.4774 | 3.6602 | 322.306 | 200.8294 | 3012.4404
2020-02-15 10:00 | 3.6709 | 3.864 | 319.7764 | 259.1003 | 3886.5051
2020-02-15 11:00 | 3.6088 | 3.7986 | 319.4028 | 240.3894 | 3605.8407
2020-02-15 12:00 | 4.4237 | 4.6564 | 317.1699 | 539.9999 | 8099.9978
2020-02-15 13:00 | 5.2267 | 5.5016 | 320.6431 | 936.9395 | 14054.0921
2020-02-15 14:00 | 5.0133 | 5.277 | 328.0687 | 824.0297 | 12360.4457
2020-02-15 15:00 | 4.1771 | 4.3968 | 332.6732 | 437.6674 | 6565.0115
2020-02-15 16:00 | 3.9011 | 4.1063 | 332.4636 | 335.4005 | 5031.0068
2020-02-15 17:00 | 3.898 | 4.103 | 324.9717 | 334.2633 | 5013.9488
2020-02-15 18:00 | 3.9925 | 4.2025 | 320.6699 | 369.2658 | 5538.9867
2020-02-15 19:00 | 3.8996 | 4.1047 | 319.414 | 334.8602 | 5022.9036
2020-02-15 20:00 | 3.7164 | 3.9119 | 318.6933 | 272.8069 | 4092.103
2020-02-15 21:00 | 3.3062 | 3.4801 | 312.337 | 150.7365 | 2261.0479
2020-02-15 22:00 | 3.0936 | 3.2563 | 294.2287 | 102.8551 | 1542.827
2020-02-15 23:00 | 3.411 | 3.5904 | 288.6624 | 180.8568 | 2712.8521
2020-02-16 00:00 | 3.0881 | 3.2505 | 283.1537 | 101.6147 | 1524.2206
2020-02-16 01:00 | 2.5859 | 2.7219 | 270.6606 | 0 | 0
2020-02-16 02:00 | 2.2649 | 2.384 | 245.3306 | 0 | 0
2020-02-16 03:00 | 2.7391 | 2.8832 | 214.1411 | 0 | 0
2020-02-16 04:00 | 3.4152 | 3.5948 | 206.067 | 182.1094 | 2731.6413
2020-02-16 05:00 | 3.6698 | 3.8628 | 214.6535 | 258.7527 | 3881.2911
2020-02-16 06:00 | 4.3548 | 4.5838 | 212.0641 | 509.3703 | 7640.5539
2020-02-16 07:00 | 5.2526 | 5.5289 | 195.6604 | 953.1153 | 14296.7295
2020-02-16 08:00 | 6.2457 | 6.5742 | 203.961 | 1642.2124 | 24633.1857
2020-02-16 09:00 | 6.9159 | 7.2796 | 200.0117 | 2248.5936 | 33728.9047
2020-02-16 10:00 | 7.3888 | 7.7774 | 195.427 | 2747.4923 | 41212.3839
2020-02-16 11:00 | 7.7408 | 8.1479 | 196.0829 | 3149.5207 | 47242.8109
2020-02-16 12:00 | 8.3926 | 8.834 | 196.0505 | 3922.7814 | 58841.7212
2020-02-16 13:00 | 8.5064 | 8.9538 | 194.622 | 4057.8935 | 60868.403
2020-02-16 14:00 | 7.7719 | 8.1806 | 192.5137 | 3186.3967 | 47795.95
2020-02-16 15:00 | 8.6497 | 9.1046 | 188.845 | 4221.9245 | 63328.8673
2020-02-16 16:00 | 9.9219 | 10.4437 | 188.5589 | 5315.1236 | 79726.8536
2020-02-16 17:00 | 10.2803 | 10.821 | 193.7308 | 5470.6125 | 82059.188
2020-02-16 18:00 | 9.426 | 9.9218 | 205.3945 | 4991.6988 | 74875.4823
2020-02-16 19:00 | 9.0085 | 9.4823 | 209.3273 | 4626.0343 | 69390.5146
2020-02-16 20:00 | 9.5165 | 10.017 | 205.3292 | 5065.9143 | 75988.7138
2020-02-16 21:00 | 10.191 | 10.727 | 202.0965 | 5434.7177 | 81520.765
2020-02-16 22:00 | 10.8811 | 11.4534 | 202.3637 | 5641.4645 | 84621.9677
2020-02-16 23:00 | 11.1419 | 11.7279 | 198.7992 | 5673.4237 | 85101.3555
2020-02-17 00:00 | 11.2719 | 11.8647 | 198.6124 | 5686.2854 | 85294.2816
2020-02-17 01:00 | 11.3654 | 11.9632 | 199.9134 | 5695.5389 | 85433.0833
2020-02-17 02:00 | 11.3128 | 11.9077 | 197.8333 | 5690.3284 | 85354.9256
2020-02-17 03:00 | 10.9049 | 11.4785 | 197.6566 | 5647.1387 | 84707.0802
2020-02-17 04:00 | 10.7833 | 11.3505 | 201.3145 | 5618.2083 | 84273.1241
2020-02-17 05:00 | 10.8578 | 11.4289 | 202.7988 | 5635.9216 | 84538.8247
2020-02-17 06:00 | 10.6088 | 11.1668 | 202.6542 | 5576.6864 | 83650.2955
2020-02-17 07:00 | 10.7687 | 11.3351 | 202.6803 | 5614.7381 | 84221.0719
2020-02-17 08:00 | 8.8038 | 9.2668 | 206.1208 | 4395.4874 | 65932.3106
2020-02-17 09:00 | 8.1694 | 8.5991 | 206.2743 | 3657.783 | 54866.7447
2020-02-17 10:00 | 7.1916 | 7.5698 | 205.0581 | 2527.8992 | 37918.4885
2020-02-17 11:00 | 6.9102 | 7.2736 | 205.2321 | 2243.0114 | 33645.1709
2020-02-17 12:00 | 6.7826 | 7.1394 | 209.4933 | 2117.8779 | 31768.1681
2020-02-17 13:00 | 6.5734 | 6.9191 | 207.953 | 1922.29 | 28834.3507
2020-02-17 14:00 | 6.9841 | 7.3514 | 204.2111 | 2315.509 | 34732.6357
2020-02-17 15:00 | 7.5888 | 7.9879 | 204.1536 | 2970.2046 | 44553.0689
2020-02-17 16:00 | 8.1675 | 8.597 | 204.746 | 3655.4471 | 54831.7071
2020-02-17 17:00 | 8.4257 | 8.8689 | 207.3536 | 3962.0912 | 59431.3678
2020-02-17 18:00 | 8.0714 | 8.4959 | 216.4942 | 3541.4027 | 53121.0405
2020-02-17 19:00 | 7.8412 | 8.2536 | 218.191 | 3268.5648 | 49028.4718
2020-02-17 20:00 | 7.4602 | 7.8525 | 220.5433 | 2826.9811 | 42404.7169
2020-02-17 21:00 | 7.0319 | 7.4017 | 224.6255 | 2362.38 | 35435.6999
2020-02-17 22:00 | 6.4886 | 6.8299 | 227.1743 | 1849.8617 | 27747.9248
2020-02-17 23:00 | 5.7982 | 6.1031 | 236.641 | 1304.178 | 19562.6706
2020-02-18 00:00 | 5.2034 | 5.4771 | 238.8282 | 924.5104 | 13867.656
2020-02-18 01:00 | 4.9506 | 5.211 | 230.3407 | 790.9312 | 11863.9687
2020-02-18 02:00 | 4.7699 | 5.0207 | 228.1934 | 695.4162 | 10431.2423
2020-02-18 03:00 | 4.7805 | 5.0319 | 228.268 | 701.0034 | 10515.0507
2020-02-18 04:00 | 4.8588 | 5.1144 | 229.0978 | 742.416 | 11136.2393
2020-02-18 05:00 | 5.9038 | 6.2143 | 245.7211 | 1382.0423 | 20730.6347
2020-02-18 06:00 | 5.3523 | 5.6338 | 246.5015 | 1015.2379 | 15228.5687
2020-02-18 07:00 | 5.5858 | 5.8796 | 246.1907 | 1160.7217 | 17410.8249
2020-02-18 08:00 | 5.0662 | 5.3327 | 258.5983 | 851.9998 | 12779.9965
2020-02-18 09:00 | 5.4494 | 5.736 | 268.9125 | 1075.6931 | 16135.3966
2020-02-18 10:00 | 5.7834 | 6.0875 | 266.3188 | 1293.2819 | 19399.2281
2020-02-18 11:00 | 6.1987 | 6.5247 | 271.7715 | 1602.0861 | 24031.2921
2020-02-18 12:00 | 6.7136 | 7.0667 | 279.2403 | 2050.1934 | 30752.9008
2020-02-18 13:00 | 7.0036 | 7.372 | 286.1589 | 2334.6582 | 35019.873
2020-02-18 14:00 | 6.6958 | 7.048 | 289.341 | 2032.6998 | 30490.4973
2020-02-18 15:00 | 6.4149 | 6.7523 | 285.7868 | 1786.8811 | 26803.2158
2020-02-18 16:00 | 6.9145 | 7.2782 | 276.2215 | 2247.2685 | 33709.0281
2020-02-18 17:00 | 7.8843 | 8.299 | 274.5929 | 3319.6191 | 49794.287
2020-02-18 18:00 | 8.3546 | 8.7941 | 276.8854 | 3877.6901 | 58165.3521
2020-02-18 19:00 | 8.4964 | 8.9432 | 277.316 | 4045.9488 | 60689.2324
2020-02-18 20:00 | 8.6093 | 9.0621 | 276.7991 | 4176.4993 | 62647.4897
2020-02-18 21:00 | 8.589 | 9.0408 | 276.4183 | 4153.6278 | 62304.4176
2020-02-18 22:00 | 8.7509 | 9.2112 | 277.1365 | 4335.947 | 65039.2048
2020-02-18 23:00 | 8.7986 | 9.2614 | 279.1948 | 4389.657 | 65844.8554
2020-02-19 00:00 | 8.6519 | 9.1069 | 282.493 | 4224.4045 | 63366.0677
2020-02-19 01:00 | 8.2877 | 8.7236 | 285.0213 | 3798.1648 | 56972.4726
2020-02-19 02:00 | 7.9567 | 8.3752 | 284.1799 | 3405.4613 | 51081.9199
2020-02-19 03:00 | 7.6873 | 8.0916 | 281.3738 | 3086.1519 | 46292.279
2020-02-19 04:00 | 7.4755 | 7.8686 | 278.298 | 2844.0305 | 42660.4581
2020-02-19 05:00 | 7.4344 | 7.8254 | 274.3484 | 2798.2947 | 41974.4211
2020-02-19 06:00 | 7.2606 | 7.6425 | 270.3682 | 2604.785 | 39071.7754
2020-02-19 07:00 | 6.8534 | 7.2138 | 267.0204 | 2187.3069 | 32809.6032
2020-02-19 08:00 | 5.6558 | 5.9533 | 268.8911 | 1204.3602 | 18065.4025
2020-02-19 09:00 | 5.286 | 5.564 | 273.4064 | 973.9139 | 14608.7078
2020-02-19 10:00 | 5.0721 | 5.3389 | 275.6803 | 855.1273 | 12826.9088
2020-02-19 11:00 | 4.9664 | 5.2276 | 273.1077 | 799.2393 | 11988.5891
2020-02-19 12:00 | 4.6975 | 4.9446 | 270.2252 | 661.6126 | 9924.1883
2020-02-19 13:00 | 4.6365 | 4.8803 | 271.7545 | 634.488 | 9517.3194
2020-02-19 14:00 | 4.0614 | 4.275 | 264.5357 | 394.8063 | 5922.0944
2020-02-19 15:00 | 3.7376 | 3.9342 | 251.261 | 279.1884 | 4187.8261
2020-02-19 16:00 | 3.7716 | 3.97 | 240.5312 | 289.4107 | 4341.1612
2020-02-19 17:00 | 3.973 | 4.182 | 235.1735 | 362.0587 | 5430.8801
2020-02-19 18:00 | 4.1749 | 4.3945 | 225.7591 | 436.8572 | 6552.8573
2020-02-19 19:00 | 4.7902 | 5.0421 | 209.6747 | 706.1486 | 10592.2296
2020-02-19 20:00 | 5.8597 | 6.1678 | 201.6938 | 1349.486 | 20242.2896
2020-02-19 21:00 | 6.3874 | 6.7234 | 201.1124 | 1763.3956 | 26450.9333
2020-02-19 22:00 | 6.4118 | 6.7491 | 210.5344 | 1784.2318 | 26763.4769
2020-02-19 23:00 | 5.9545 | 6.2677 | 213.1935 | 1419.3714 | 21290.5711
2020-02-20 00:00 | 5.4533 | 5.7401 | 215.7049 | 1078.1287 | 16171.9306
2020-02-20 01:00 | 5.0578 | 5.3238 | 216.9364 | 847.5497 | 12713.2452
2020-02-20 02:00 | 4.9369 | 5.1965 | 211.3252 | 783.6649 | 11754.9731
2020-02-20 03:00 | 5.1865 | 5.4593 | 202.2669 | 915.5725 | 13733.5877
2020-02-20 04:00 | 5.3549 | 5.6365 | 198.456 | 1016.8021 | 15252.0322
2020-02-20 05:00 | 5.2969 | 5.5755 | 197.4351 | 980.7088 | 14710.6319
2020-02-20 06:00 | 5.1859 | 5.4586 | 198.9637 | 915.2174 | 13728.2604
2020-02-20 07:00 | 4.7567 | 5.0068 | 200.4616 | 688.4284 | 10326.4263
2020-02-20 08:00 | 3.6765 | 3.8699 | 196.4111 | 260.7815 | 3911.7231
2020-02-20 09:00 | 3.3257 | 3.5006 | 195.1599 | 155.1647 | 2327.4706
2020-02-20 10:00 | 2.6605 | 2.8004 | 200.5075 | 0 | 0
2020-02-20 11:00 | 2.0556 | 2.1637 | 191.1137 | 0 | 0
2020-02-20 12:00 | 1.8314 | 1.9278 | 184.2137 | 0 | 0
2020-02-20 13:00 | 1.6401 | 1.7263 | 172.5164 | 0 | 0
2020-02-20 14:00 | 1.5093 | 1.5887 | 161.9627 | 0 | 0
2020-02-20 15:00 | 1.6379 | 1.7241 | 161.5323 | 0 | 0
2020-02-20 16:00 | 1.6143 | 1.6992 | 166.4825 | 0 | 0
2020-02-20 17:00 | 1.6588 | 1.746 | 174.4817 | 0 | 0
2020-02-20 18:00 | 1.7076 | 1.7974 | 177.8804 | 0 | 0
2020-02-20 19:00 | 1.7563 | 1.8487 | 184.4661 | 0 | 0
2020-02-20 20:00 | 1.4033 | 1.4771 | 194.0627 | 0 | 0
2020-02-20 21:00 | 0.90508 | 0.95268 | 206.6713 | 0 | 0
2020-02-20 22:00 | 0.61215 | 0.64435 | 277.5945 | 0 | 0
2020-02-20 23:00 | 1.076 | 1.1325 | 315.6872 | 0 | 0
2020-02-21 00:00 | 1.142 | 1.202 | 332.9604 | 0 | 0
2020-02-21 01:00 | 0.70572 | 0.74284 | 24.2026 | 0 | 0
2020-02-21 02:00 | 1.0778 | 1.1345 | 103.4171 | 0 | 0
2020-02-21 03:00 | 1.753 | 1.8452 | 138.2416 | 0 | 0
2020-02-21 04:00 | 2.6067 | 2.7438 | 158.4804 | 0 | 0
2020-02-21 05:00 | 3.3012 | 3.4748 | 177.3592 | 149.6103 | 2244.1539
2020-02-21 06:00 | 3.5927 | 3.7817 | 189.0584 | 235.5643 | 3533.4652
2020-02-21 07:00 | 3.3766 | 3.5541 | 189.4767 | 170.4854 | 2557.2809
2020-02-21 08:00 | 2.4542 | 2.5832 | 191.4692 | 0 | 0
2020-02-21 09:00 | 3.5012 | 3.6853 | 195.1672 | 207.9946 | 3119.9193
2020-02-21 10:00 | 4.6139 | 4.8565 | 178.2726 | 624.4633 | 9366.95
2020-02-21 11:00 | 5.4416 | 5.7278 | 175.92 | 1070.8481 | 16062.7218
2020-02-21 12:00 | 5.1797 | 5.4522 | 178.1027 | 911.9848 | 13679.7715
2020-02-21 13:00 | 5.0724 | 5.3392 | 178.2619 | 855.27 | 12829.0504
2020-02-21 14:00 | 4.8393 | 5.0939 | 177.1294 | 732.119 | 10981.7855
2020-02-21 15:00 | 4.6894 | 4.9361 | 177.0144 | 658.0187 | 9870.2807
2020-02-21 16:00 | 4.6754 | 4.9213 | 174.0655 | 651.7964 | 9776.9464
2020-02-21 17:00 | 4.7194 | 4.9676 | 174.7626 | 671.3316 | 10069.9738
2020-02-21 18:00 | 4.693 | 4.9398 | 180.5485 | 659.6044 | 9894.0653
2020-02-21 19:00 | 4.5721 | 4.8125 | 185.4545 | 605.8874 | 9088.3114
2020-02-21 20:00 | 4.1889 | 4.4092 | 189.9022 | 442.0427 | 6630.64
2020-02-21 21:00 | 3.924 | 4.1304 | 188.1903 | 343.9095 | 5158.6428
2020-02-21 22:00 | 3.4511 | 3.6326 | 186.6766 | 192.9334 | 2894.0011
2020-02-21 23:00 | 3.2824 | 3.455 | 184.2867 | 145.3689 | 2180.5331
2020-02-22 00:00 | 3.1648 | 3.3313 | 191.6213 | 118.8895 | 1783.3422
2020-02-22 01:00 | 2.9104 | 3.0635 | 202.9671 | 61.586 | 923.7902
2020-02-22 02:00 | 2.6328 | 2.7712 | 211.1404 | 0 | 0
2020-02-22 03:00 | 2.6487 | 2.788 | 209.3272 | 0 | 0
2020-02-22 04:00 | 2.7891 | 2.9358 | 203.9861 | 0 | 0
2020-02-22 05:00 | 3.2427 | 3.4133 | 202.4482 | 136.4372 | 2046.5586
2020-02-22 06:00 | 3.095 | 3.2578 | 213.3138 | 103.1761 | 1547.6418
2020-02-22 07:00 | 2.4139 | 2.5409 | 218.2643 | 0 | 0
2020-02-22 08:00 | 2.7244 | 2.8677 | 202.9503 | 0 | 0
2020-02-22 09:00 | 3.2803 | 3.4528 | 200.6525 | 144.8992 | 2173.4873
2020-02-22 10:00 | 3.6297 | 3.8206 | 207.5784 | 246.6867 | 3700.301
2020-02-22 11:00 | 4.7083 | 4.9559 | 221.1187 | 666.3966 | 9995.9489
2020-02-22 12:00 | 5.4512 | 5.7379 | 228.8373 | 1076.8126 | 16152.1886
2020-02-22 13:00 | 6.1304 | 6.4528 | 231.2458 | 1548.9416 | 23234.1241
2020-02-22 14:00 | 6.4205 | 6.7582 | 231.6157 | 1791.6567 | 26874.851
2020-02-22 15:00 | 6.6668 | 7.0174 | 236.7422 | 2004.2394 | 30063.5903
2020-02-22 16:00 | 6.4929 | 6.8344 | 221.9368 | 1853.5123 | 27802.6838
2020-02-22 17:00 | 7.3027 | 7.6868 | 212.5597 | 2651.6299 | 39774.4481
2020-02-22 18:00 | 8.6012 | 9.0536 | 208.2401 | 4167.3453 | 62510.1794
2020-02-22 19:00 | 9.0549 | 9.5312 | 214.5113 | 4670.6278 | 70059.4171
2020-02-22 20:00 | 9.318 | 9.8081 | 214.5254 | 4898.2354 | 73473.5303
2020-02-22 21:00 | 9.9927 | 10.5183 | 212.3176 | 5354.9919 | 80324.8787
2020-02-22 22:00 | 10.7994 | 11.3673 | 216.019 | 5622.0198 | 84330.297
2020-02-22 23:00 | 11.0697 | 11.6519 | 219.7957 | 5666.2744 | 84994.1159
2020-02-23 00:00 | 11.2087 | 11.7982 | 222.6566 | 5680.0315 | 85200.472
2020-02-23 01:00 | 11.1298 | 11.7152 | 224.7193 | 5672.2272 | 85083.4081
2020-02-23 02:00 | 11.5452 | 12.1524 | 230.3454 | 5699.3049 | 85489.5733
2020-02-23 03:00 | 11.4318 | 12.0331 | 243.192 | 5699.0661 | 85485.992
2020-02-23 04:00 | 11.1463 | 11.7325 | 250.8088 | 5673.8556 | 85107.8333
2020-02-23 05:00 | 11.2072 | 11.7966 | 252.2283 | 5679.8838 | 85198.2571
2020-02-23 06:00 | 11.5498 | 12.1573 | 254.161 | 5699.3145 | 85489.7177
2020-02-23 07:00 | 11.5554 | 12.1632 | 257.7608 | 5699.3263 | 85489.8945
2020-02-23 08:00 | 10.2472 | 10.7862 | 254.6322 | 5457.3112 | 81859.6684
2020-02-23 09:00 | 11.955 | 12.5838 | 263.4594 | 5700 | 85500
2020-02-23 10:00 | 11.9816 | 12.6118 | 271.5549 | 5700 | 85500
2020-02-23 11:00 | 11.1012 | 11.6851 | 270.0998 | 5669.4003 | 85041.0044
2020-02-23 12:00 | 12.3597 | 13.0097 | 270.5253 | 5700 | 85500
2020-02-23 13:00 | 11.5081 | 12.1134 | 273.5938 | 5699.2268 | 85488.4025
2020-02-23 14:00 | 11.2702 | 11.8629 | 278.8463 | 5686.1163 | 85291.7441
2020-02-23 15:00 | 9.1231 | 9.603 | 276.8874 | 4729.6464 | 70944.6959
2020-02-23 16:00 | 7.8163 | 8.2274 | 267.1158 | 3239.0442 | 48585.6631
2020-02-23 17:00 | 7.2236 | 7.6035 | 257.1344 | 2563.527 | 38452.9055
2020-02-23 18:00 | 6.5518 | 6.8964 | 243.3872 | 1903.8404 | 28557.6056
2020-02-23 19:00 | 6.3511 | 6.6852 | 234.0561 | 1732.3424 | 25985.1359
2020-02-23 20:00 | 6.4275 | 6.7655 | 233.4199 | 1797.591 | 26963.8646
2020-02-23 21:00 | 6.3867 | 6.7227 | 222.9962 | 1762.7973 | 26441.96
2020-02-23 22:00 | 6.2203 | 6.5474 | 210.6158 | 1620.498 | 24307.4707
2020-02-23 23:00 | 6.5943 | 6.9411 | 201.0724 | 1940.1515 | 29102.2732
2020-02-24 00:00 | 7.2391 | 7.6198 | 192.2247 | 2580.7882 | 38711.8225
2020-02-24 01:00 | 8.4817 | 8.9278 | 201.0487 | 4028.5807 | 60428.7102
2020-02-24 02:00 | 8.7034 | 9.1612 | 203.1453 | 4282.4803 | 64237.205
2020-02-24 03:00 | 8.8706 | 9.3371 | 199.4778 | 4470.7321 | 67060.9813
2020-02-24 04:00 | 10.7557 | 11.3214 | 241.0176 | 5611.6355 | 84174.532
2020-02-24 05:00 | 11.2327 | 11.8235 | 280.707 | 5682.4056 | 85236.0838
2020-02-24 06:00 | 14.887 | 15.6699 | 340.8773 | 5700 | 85500
2020-02-24 07:00 | 19.03 | 20.0308 | 351.3039 | 5692.972 | 85394.5799
2020-02-24 08:00 | 15.0023 | 15.7913 | 341.1189 | 5700 | 85500
2020-02-24 09:00 | 14.1302 | 14.8734 | 329.3026 | 5700 | 85500
2020-02-24 10:00 | 11.8612 | 12.4851 | 317.4343 | 5699.9702 | 85499.5526
2020-02-24 11:00 | 11.4465 | 12.0485 | 312.3722 | 5699.0971 | 85486.4565
2020-02-24 12:00 | 11.6744 | 12.2884 | 311.5419 | 5699.5768 | 85493.6515
2020-02-24 13:00 | 12.1624 | 12.8021 | 311.6532 | 5700 | 85500
2020-02-24 14:00 | 11.5359 | 12.1426 | 309.6779 | 5699.2853 | 85489.2795
2020-02-24 15:00 | 12.5676 | 13.2286 | 317.2734 | 5700 | 85500
2020-02-24 16:00 | 12.7682 | 13.4398 | 317.9808 | 5700 | 85500
2020-02-24 17:00 | 12.3684 | 13.0189 | 316.7274 | 5700 | 85500
2020-02-24 18:00 | 11.5555 | 12.1632 | 313.5986 | 5699.3265 | 85489.8969
2020-02-24 19:00 | 10.6258 | 11.1846 | 310.2377 | 5580.7243 | 83710.8643
2020-02-24 20:00 | 9.9053 | 10.4263 | 305.0223 | 5304.9457 | 79574.1862
2020-02-24 21:00 | 9.7982 | 10.3135 | 297.6708 | 5239.0787 | 78586.1802
2020-02-24 22:00 | 9.7577 | 10.271 | 295.1626 | 5214.2372 | 78213.5582
2020-02-24 23:00 | 8.8204 | 9.2843 | 294.0664 | 4414.2175 | 66213.2632
2020-02-25 00:00 | 7.6899 | 8.0944 | 289.5479 | 3089.2778 | 46339.1672
2020-02-25 01:00 | 6.7545 | 7.1097 | 279.8491 | 2090.2749 | 31354.1233
2020-02-25 02:00 | 6.044 | 6.3619 | 269.767 | 1485.3138 | 22279.7074
2020-02-25 03:00 | 5.6694 | 5.9675 | 256.9642 | 1212.7807 | 18191.7109
2020-02-25 04:00 | 6.0073 | 6.3233 | 244.3136 | 1458.2964 | 21874.446
2020-02-25 05:00 | 5.9737 | 6.2879 | 234.3459 | 1433.4982 | 21502.4725
2020-02-25 06:00 | 6.0965 | 6.4172 | 220.6011 | 1524.0258 | 22860.3871
2020-02-25 07:00 | 6.8246 | 7.1836 | 215.0442 | 2159.0996 | 32386.4933
2020-02-25 08:00 | 7.2472 | 7.6284 | 211.4462 | 2589.8205 | 38847.3078
2020-02-25 09:00 | 8.1784 | 8.6085 | 209.402 | 3668.416 | 55026.2396
2020-02-25 10:00 | 8.4106 | 8.853 | 204.4976 | 3944.1396 | 59162.0941
2020-02-25 11:00 | 8.6049 | 9.0575 | 204.7668 | 4171.5375 | 62573.0624
2020-02-25 12:00 | 7.4151 | 7.8051 | 205.0098 | 2776.8175 | 41652.2631
2020-02-25 13:00 | 6.929 | 7.2934 | 205.2439 | 2261.427 | 33921.4047
2020-02-25 14:00 | 7.3653 | 7.7527 | 210.217 | 2721.3142 | 40819.7135
2020-02-25 15:00 | 7.2009 | 7.5797 | 207.6919 | 2538.2998 | 38074.4976
2020-02-25 16:00 | 7.4199 | 7.8102 | 204.4721 | 2782.1833 | 41732.7499
2020-02-25 17:00 | 8.1729 | 8.6028 | 207.231 | 3661.9433 | 54929.149
2020-02-25 18:00 | 8.6355 | 9.0897 | 210.8906 | 4206.0038 | 63090.0563
2020-02-25 19:00 | 8.4788 | 8.9247 | 213.9206 | 4025.1093 | 60376.6393
2020-02-25 20:00 | 8.3373 | 8.7758 | 214.9421 | 3857.1311 | 57856.9662
2020-02-25 21:00 | 8.254 | 8.6881 | 214.2761 | 3758.1557 | 56372.335
2020-02-25 22:00 | 7.166 | 7.5429 | 212.1353 | 2499.3655 | 37490.4821
2020-02-25 23:00 | 6.3995 | 6.7361 | 205.8274 | 1773.7378 | 26606.0668
2020-02-26 00:00 | 6.6153 | 6.9632 | 203.4239 | 1958.1299 | 29371.9487
2020-02-26 01:00 | 6.9763 | 7.3432 | 205.6197 | 2307.8809 | 34618.2133
2020-02-26 02:00 | 7.3765 | 7.7645 | 209.9598 | 2733.8241 | 41007.3614
2020-02-26 03:00 | 7.6145 | 8.0149 | 212.4731 | 2999.8176 | 44997.2634
2020-02-26 04:00 | 7.7107 | 8.1162 | 210.7486 | 3113.8721 | 46708.0817
2020-02-26 05:00 | 7.7823 | 8.1916 | 214.1686 | 3198.6942 | 47980.4132
2020-02-26 06:00 | 7.8754 | 8.2896 | 221.909 | 3309.0538 | 49635.8074
2020-02-26 07:00 | 7.5281 | 7.9241 | 229.3366 | 2902.6793 | 43540.1891
2020-02-26 08:00 | 5.8516 | 6.1594 | 235.7416 | 1343.5742 | 20153.613
2020-02-26 09:00 | 4.9462 | 5.2064 | 245.8817 | 788.5956 | 11828.934
2020-02-26 10:00 | 3.3578 | 3.5344 | 243.9197 | 164.8425 | 2472.6379
2020-02-26 11:00 | 2.8166 | 2.9647 | 234.2171 | 0 | 0
2020-02-26 12:00 | 2.8407 | 2.9902 | 222.2432 | 0 | 0
2020-02-26 13:00 | 2.5811 | 2.7169 | 196.2811 | 0 | 0
2020-02-26 14:00 | 3.0625 | 3.2236 | 157.8227 | 95.8481 | 1437.7219
2020-02-26 15:00 | 4.3519 | 4.5808 | 147.9198 | 508.0856 | 7621.2836
2020-02-26 16:00 | 5.219 | 5.4935 | 144.9923 | 932.7119 | 13990.6789
2020-02-26 17:00 | 6.1075 | 6.4287 | 151.351 | 1532.1246 | 22981.8683
2020-02-26 18:00 | 6.9225 | 7.2865 | 171.4074 | 2255.0565 | 33825.8474
2020-02-26 19:00 | 7.6676 | 8.0709 | 203.8668 | 3062.8454 | 45942.6804
2020-02-26 20:00 | 7.8341 | 8.2461 | 227.2937 | 3260.0861 | 48901.2918
2020-02-26 21:00 | 7.269 | 7.6513 | 236.6308 | 2614.1152 | 39211.7283
2020-02-26 22:00 | 7.0373 | 7.4074 | 247.2886 | 2367.6862 | 35515.2925
2020-02-26 23:00 | 7.5073 | 7.9021 | 260.8636 | 2879.4592 | 43191.8881
2020-02-27 00:00 | 7.1964 | 7.5749 | 270.2337 | 2533.2299 | 37998.4489
2020-02-27 01:00 | 6.9249 | 7.2891 | 279.4879 | 2257.4372 | 33861.5578
2020-02-27 02:00 | 6.6274 | 6.976 | 281.0736 | 1968.4764 | 29527.1456
2020-02-27 03:00 | 6.2824 | 6.6128 | 281.7917 | 1673.5994 | 25103.9911
2020-02-27 04:00 | 5.9666 | 6.2804 | 281.8081 | 1428.2956 | 21424.4342
2020-02-27 05:00 | 5.6375 | 5.934 | 281.9631 | 1192.9194 | 17893.7906
2020-02-27 06:00 | 6.4314 | 6.7697 | 287.1123 | 1801.004 | 27015.0599
2020-02-27 07:00 | 8.2075 | 8.6392 | 298.6969 | 3702.9774 | 55544.6612
2020-02-27 08:00 | 6.8232 | 7.182 | 307.0533 | 2157.6364 | 32364.5455
2020-02-27 09:00 | 5.6615 | 5.9593 | 311.9847 | 1207.9109 | 18118.6632
2020-02-27 10:00 | 6.0197 | 6.3363 | 311.8989 | 1467.3791 | 22010.686
2020-02-27 11:00 | 6.0623 | 6.3811 | 304.1923 | 1498.7994 | 22481.9917
2020-02-27 12:00 | 6.507 | 6.8492 | 301.5828 | 1865.5615 | 27983.4229
2020-02-27 13:00 | 6.8804 | 7.2423 | 306.1242 | 2213.784 | 33206.7605
2020-02-27 14:00 | 7.004 | 7.3723 | 304.3412 | 2335.0218 | 35025.3263
2020-02-27 15:00 | 6.6808 | 7.0322 | 304.3331 | 2018.0005 | 30270.0074
2020-02-27 16:00 | 6.6033 | 6.9506 | 306.8087 | 1947.8799 | 29218.1987
2020-02-27 17:00 | 6.4067 | 6.7437 | 306.9595 | 1779.8792 | 26698.1883
2020-02-27 18:00 | 6.0019 | 6.3176 | 299.5344 | 1454.3109 | 21814.6641
2020-02-27 19:00 | 5.8429 | 6.1502 | 295.141 | 1337.1267 | 20056.9
2020-02-27 20:00 | 5.7715 | 6.075 | 289.9031 | 1284.5047 | 19267.5712
2020-02-27 21:00 | 6.1759 | 6.5007 | 285.2118 | 1582.6024 | 23739.0362
2020-02-27 22:00 | 6.8386 | 7.1982 | 287.3841 | 2172.7539 | 32591.3087
2020-02-27 23:00 | 7.0888 | 7.4617 | 287.9934 | 2418.2665 | 36273.9982
2020-02-28 00:00 | 7.0297 | 7.3994 | 289.488 | 2360.2197 | 35403.2949
2020-02-28 01:00 | 6.7182 | 7.0716 | 289.648 | 2054.7089 | 30820.6342
2020-02-28 02:00 | 6.0971 | 6.4178 | 288.4461 | 1524.4549 | 22866.8236
2020-02-28 03:00 | 5.7424 | 6.0444 | 286.1027 | 1263.0844 | 18946.2654
2020-02-28 04:00 | 5.7049 | 6.005 | 281.0211 | 1235.4993 | 18532.4902
2020-02-28 05:00 | 6.189 | 6.5145 | 275.9644 | 1593.7718 | 23906.5767
2020-02-28 06:00 | 6.1235 | 6.4455 | 274.2156 | 1543.8833 | 23158.2502
2020-02-28 07:00 | 5.4825 | 5.7709 | 273.5919 | 1096.3593 | 16445.3889
2020-02-28 08:00 | 5.4708 | 5.7585 | 272.7696 | 1089.0376 | 16335.5646
2020-02-28 09:00 | 5.5255 | 5.8161 | 269.4864 | 1123.1418 | 16847.1266
2020-02-28 10:00 | 5.3683 | 5.6506 | 265.444 | 1025.1505 | 15377.2581
2020-02-28 11:00 | 5.3902 | 5.6737 | 263.0982 | 1038.8345 | 15582.5175
2020-02-28 12:00 | 5.3909 | 5.6744 | 264.4877 | 1039.2328 | 15588.4917
2020-02-28 13:00 | 4.5735 | 4.8141 | 267.354 | 606.53 | 9097.9501
2020-02-28 14:00 | 3.7928 | 3.9923 | 264.2128 | 295.7921 | 4436.8814
2020-02-28 15:00 | 3.7964 | 3.996 | 258.5168 | 296.8682 | 4453.0237
2020-02-28 16:00 | 4.1109 | 4.3271 | 258.5966 | 413.1454 | 6197.1815
2020-02-28 17:00 | 5.1248 | 5.3943 | 253.3756 | 882.9627 | 13244.4406
2020-02-28 18:00 | 5.7486 | 6.051 | 256.5477 | 1267.6967 | 19015.4502
2020-02-28 19:00 | 5.7822 | 6.0863 | 264.5228 | 1292.4402 | 19386.603
2020-02-28 20:00 | 5.663 | 5.9609 | 268.5712 | 1208.8384 | 18132.5756
2020-02-28 21:00 | 5.4013 | 5.6853 | 275.561 | 1045.7191 | 15685.7859
2020-02-28 22:00 | 5.1405 | 5.4109 | 278.7685 | 891.2659 | 13368.9888
2020-02-28 23:00 | 5.1686 | 5.4404 | 281.9921 | 906.1008 | 13591.5113
2020-02-29 00:00 | 5.5659 | 5.8587 | 284.8774 | 1148.3425 | 17225.1378
2020-02-29 01:00 | 5.9601 | 6.2736 | 289.1979 | 1423.4854 | 21352.2813
2020-02-29 02:00 | 5.9762 | 6.2905 | 288.606 | 1435.346 | 21530.1895
2020-02-29 03:00 | 5.6589 | 5.9565 | 283.4149 | 1206.2553 | 18093.8291
2020-02-29 04:00 | 5.6022 | 5.8968 | 279.2962 | 1170.9338 | 17564.0074
2020-02-29 05:00 | 5.9452 | 6.2579 | 275.1018 | 1412.5422 | 21188.1326
2020-02-29 06:00 | 5.5153 | 5.8053 | 263.7353 | 1116.7605 | 16751.4082
2020-02-29 07:00 | 5.0934 | 5.3613 | 255.7275 | 866.3489 | 12995.2329
2020-02-29 08:00 | 5.8875 | 6.1972 | 261.9775 | 1370.0269 | 20550.4028
2020-02-29 09:00 | 5.9183 | 6.2296 | 261.1528 | 1392.7 | 20890.4994
2020-02-29 10:00 | 5.7626 | 6.0657 | 259.4952 | 1277.9989 | 19169.9835
2020-02-29 11:00 | 6.2682 | 6.5978 | 256.982 | 1661.4309 | 24921.4628
2020-02-29 12:00 | 6.1301 | 6.4525 | 254.5635 | 1548.7598 | 23231.3974
2020-02-29 13:00 | 5.7366 | 6.0383 | 253.3597 | 1258.8156 | 18882.2336
2020-02-29 14:00 | 4.9179 | 5.1765 | 246.7598 | 773.6252 | 11604.3774
2020-02-29 15:00 | 4.1897 | 4.41 | 234.7216 | 442.3347 | 6635.0205
2020-02-29 16:00 | 4.2977 | 4.5237 | 219.1461 | 484.0123 | 7260.1841
2020-02-29 17:00 | 5.1247 | 5.3943 | 202.9602 | 882.9158 | 13243.7377
2020-02-29 18:00 | 6.4701 | 6.8104 | 195.6349 | 1834.0127 | 27510.19
2020-02-29 19:00 | 7.3448 | 7.7311 | 198.4152 | 2698.5191 | 40477.7863
2020-02-29 20:00 | 7.7462 | 8.1537 | 198.2778 | 3156.0151 | 47340.226
2020-02-29 21:00 | 8.131 | 8.5587 | 193.2054 | 3612.16 | 54182.4001
2020-02-29 22:00 | 8.5964 | 9.0485 | 187.7867 | 4161.9218 | 62428.8268
2020-02-29 23:00 | 8.9699 | 9.4417 | 185.5307 | 4582.5731 | 68738.5969
2020-03-01 00:00 | 9.3632 | 9.8556 | 185.0177 | 4937.307 | 74059.6043
2020-03-01 01:00 | 9.5005 | 10.0002 | 186.7962 | 5056.1236 | 75841.8546
2020-03-01 02:00 | 9.4446 | 9.9413 | 188.0057 | 5007.7642 | 75116.4636
2020-03-01 03:00 | 9.2082 | 9.6925 | 189.9395 | 4803.211 | 72048.1656
2020-03-01 04:00 | 9.0613 | 9.5379 | 190.5103 | 4676.1213 | 70141.8201
2020-03-01 05:00 | 9.191 | 9.6744 | 190.1587 | 4788.3612 | 71825.4184
2020-03-01 06:00 | 9.1804 | 9.6632 | 189.7251 | 4779.1733 | 71687.5999
2020-03-01 07:00 | 8.3408 | 8.7795 | 189.5453 | 3861.263 | 57918.9455
2020-03-01 08:00 | 8.2888 | 8.7247 | 192.7098 | 3799.4881 | 56992.3221
2020-03-01 09:00 | 8.1901 | 8.6208 | 194.6263 | 3682.2995 | 55234.4921
2020-03-01 10:00 | 8.5022 | 8.9494 | 192.2246 | 4052.8947 | 60793.4206
2020-03-01 11:00 | 8.7193 | 9.1779 | 193.598 | 4300.3854 | 64505.7804
2020-03-01 12:00 | 8.1685 | 8.5981 | 191.1871 | 3656.643 | 54849.6443
2020-03-01 13:00 | 7.8864 | 8.3012 | 186.3957 | 3322.1787 | 49832.6799
2020-03-01 14:00 | 7.7333 | 8.14 | 180.0825 | 3140.637 | 47109.555
2020-03-01 15:00 | 7.9507 | 8.3689 | 181.1974 | 3398.3538 | 50975.3071
2020-03-01 16:00 | 8.325 | 8.7629 | 183.0765 | 3842.4974 | 57637.4615
2020-03-01 17:00 | 8.5374 | 8.9864 | 185.5448 | 4094.6999 | 61420.499
2020-03-01 18:00 | 8.6982 | 9.1557 | 186.1665 | 4276.6287 | 64149.4299
2020-03-01 19:00 | 9.0296 | 9.5045 | 188.1245 | 4648.6868 | 69730.3019
2020-03-01 20:00 | 9.1491 | 9.6303 | 190.4543 | 4752.0992 | 71281.4877
2020-03-01 21:00 | 9.1322 | 9.6125 | 190.228 | 4737.463 | 71061.9448
2020-03-01 22:00 | 8.7878 | 9.25 | 190.2919 | 4377.5284 | 65662.9253
2020-03-01 23:00 | 8.7704 | 9.2316 | 191.4931 | 4357.8435 | 65367.6529
2020-03-02 00:00 | 8.595 | 9.047 | 190.0764 | 4160.3351 | 62405.0268
2020-03-02 01:00 | 8.4282 | 8.8715 | 184.5782 | 3965.006 | 59475.09
2020-03-02 02:00 | 8.4276 | 8.8709 | 179.4544 | 3964.348 | 59465.2204
2020-03-02 03:00 | 8.6985 | 9.156 | 177.4521 | 4276.8906 | 64153.3583
2020-03-02 04:00 | 8.6692 | 9.1251 | 175.7607 | 4243.8918 | 63658.377
2020-03-02 05:00 | 8.6223 | 9.0758 | 172.6585 | 4191.1322 | 62866.9834
2020-03-02 06:00 | 8.0939 | 8.5196 | 169.5817 | 3568.1082 | 53521.6226
2020-03-02 07:00 | 8.987 | 9.4596 | 170.1764 | 4601.8193 | 69027.2893
2020-03-02 08:00 | 9.2347 | 9.7204 | 170.6311 | 4826.1755 | 72392.632
2020-03-02 09:00 | 8.9339 | 9.4038 | 165.5012 | 4542.0223 | 68130.3346
2020-03-02 10:00 | 9.758 | 10.2712 | 163.2514 | 5214.3865 | 78215.7982
2020-03-02 11:00 | 10.0534 | 10.5821 | 164.1145 | 5379.3699 | 80690.5486
2020-03-02 12:00 | 9.197 | 9.6807 | 154.341 | 4793.5163 | 71902.745
2020-03-02 13:00 | 10.0098 | 10.5362 | 153.2368 | 5361.8386 | 80427.5792
2020-03-02 14:00 | 10.2992 | 10.8409 | 157.8314 | 5478.2362 | 82173.5431
2020-03-02 15:00 | 10.2791 | 10.8197 | 161.5653 | 5470.1314 | 82051.9708
2020-03-02 16:00 | 10.2719 | 10.8121 | 164.3848 | 5467.2204 | 82008.3055
2020-03-02 17:00 | 10.1577 | 10.692 | 166.6711 | 5421.3274 | 81319.9115
2020-03-02 18:00 | 9.7364 | 10.2485 | 172.5361 | 5201.1027 | 78016.5409
2020-03-02 19:00 | 9.2417 | 9.7278 | 182.0192 | 4832.222 | 72483.3296
2020-03-02 20:00 | 9.089 | 9.567 | 194.1499 | 4700.0856 | 70501.2837
2020-03-02 21:00 | 8.823 | 9.287 | 209.014 | 4417.1382 | 66257.0736
2020-03-02 22:00 | 7.9624 | 8.3812 | 224.2345 | 3412.2528 | 51183.7916
2020-03-02 23:00 | 7.3186 | 7.7036 | 242.2883 | 2669.3726 | 40040.5893
2020-03-03 00:00 | 6.1329 | 6.4555 | 251.4125 | 1550.8158 | 23262.2369
2020-03-03 01:00 | 6.106 | 6.4272 | 239.6935 | 1531.0296 | 22965.4437
2020-03-03 02:00 | 7.2938 | 7.6774 | 228.1889 | 2641.6628 | 39624.942
2020-03-03 03:00 | 7.4244 | 7.8149 | 225.2381 | 2787.14 | 41807.0997
2020-03-03 04:00 | 7.6006 | 8.0003 | 222.4844 | 2983.3927 | 44750.8901
2020-03-03 05:00 | 8.0757 | 8.5005 | 219.9704 | 3546.5425 | 53198.1375
2020-03-03 06:00 | 7.4726 | 7.8656 | 216.7702 | 2840.842 | 42612.6298
2020-03-03 07:00 | 7.002 | 7.3703 | 215.3784 | 2333.0802 | 34996.2036
2020-03-03 08:00 | 5.5089 | 5.7986 | 212.0214 | 1112.7658 | 16691.487
2020-03-03 09:00 | 4.4443 | 4.678 | 201.6645 | 549.1261 | 8236.8916
2020-03-03 10:00 | 3.7481 | 3.9453 | 181.5966 | 282.3444 | 4235.1659
2020-03-03 11:00 | 4.1963 | 4.417 | 172.053 | 444.7871 | 6671.8072
2020-03-03 12:00 | 4.8094 | 5.0624 | 164.9793 | 716.3028 | 10744.5421
2020-03-03 13:00 | 5.2303 | 5.5054 | 152.6873 | 939.208 | 14088.1206
2020-03-03 14:00 | 5.5312 | 5.8221 | 138.152 | 1126.6656 | 16899.9834
2020-03-03 15:00 | 6.7102 | 7.0632 | 126.9643 | 2046.875 | 30703.1257
2020-03-03 16:00 | 8.1125 | 8.5392 | 125.4739 | 3590.1919 | 53852.878
2020-03-03 17:00 | 8.6459 | 9.1006 | 128.2572 | 4217.6612 | 63264.9177
2020-03-03 18:00 | 8.3936 | 8.835 | 133.7381 | 3923.9183 | 58858.7746
2020-03-03 19:00 | 7.9954 | 8.4159 | 139.4118 | 3451.2673 | 51769.0095
2020-03-03 20:00 | 7.5696 | 7.9677 | 144.3684 | 2948.854 | 44232.8093
2020-03-03 21:00 | 7.1196 | 7.4941 | 149.3896 | 2448.4783 | 36727.1751
2020-03-03 22:00 | 6.6737 | 7.0247 | 149.0279 | 2011.0405 | 30165.6077
2020-03-03 23:00 | 6.4843 | 6.8253 | 146.9086 | 1846.1836 | 27692.7542
2020-03-04 00:00 | 6.8675 | 7.2287 | 142.6523 | 2201.1569 | 33017.3538
2020-03-04 01:00 | 7.0697 | 7.4415 | 145.3654 | 2399.4936 | 35992.4046
2020-03-04 02:00 | 6.7269 | 7.0807 | 148.8254 | 2063.2426 | 30948.6395
2020-03-04 03:00 | 6.5662 | 6.9115 | 156.828 | 1916.1433 | 28742.1497
2020-03-04 04:00 | 6.1411 | 6.4641 | 162.9157 | 1556.853 | 23352.7953
2020-03-04 05:00 | 5.593 | 5.8872 | 165.2514 | 1165.2086 | 17478.1297
2020-03-04 06:00 | 4.9323 | 5.1917 | 165.0655 | 781.2278 | 11718.4164
2020-03-04 07:00 | 4.2531 | 4.4768 | 161.5985 | 465.8245 | 6987.3668
2020-03-04 08:00 | 4.6128 | 4.8554 | 160.5829 | 623.9798 | 9359.6971
2020-03-04 09:00 | 4.7998 | 5.0523 | 158.4368 | 711.2396 | 10668.5933
2020-03-04 10:00 | 4.8012 | 5.0537 | 154.4805 | 711.9774 | 10679.6606
2020-03-04 11:00 | 4.5193 | 4.757 | 140.7204 | 582.4478 | 8736.7177
2020-03-04 12:00 | 5.2512 | 5.5274 | 134.5061 | 952.238 | 14283.5695
2020-03-04 13:00 | 6.0221 | 6.3388 | 135.7321 | 1469.1722 | 22037.5836
2020-03-04 14:00 | 6.3729 | 6.7081 | 135.093 | 1750.9915 | 26264.8729
2020-03-04 15:00 | 6.7984 | 7.156 | 131.9486 | 2133.3936 | 32000.9041
2020-03-04 16:00 | 7.4134 | 7.8033 | 132.9685 | 2774.8706 | 41623.0594
2020-03-04 17:00 | 7.5713 | 7.9695 | 140.2485 | 2950.7493 | 44261.2393
2020-03-04 18:00 | 7.9813 | 8.4011 | 155.0457 | 3434.592 | 51518.8804
2020-03-04 19:00 | 8.6735 | 9.1297 | 169.3366 | 4248.7657 | 63731.486
2020-03-04 20:00 | 8.913 | 9.3818 | 176.8083 | 4518.5287 | 67777.9302
2020-03-04 21:00 | 8.6975 | 9.1549 | 179.0823 | 4275.7488 | 64136.2319
2020-03-04 22:00 | 8.4285 | 8.8718 | 177.9104 | 3965.3499 | 59480.2492
2020-03-04 23:00 | 8.1576 | 8.5866 | 178.7479 | 3643.722 | 54655.8295
2020-03-05 00:00 | 7.4171 | 7.8072 | 185.7096 | 2779.0079 | 41685.1191
2020-03-05 01:00 | 6.4717 | 6.8121 | 193.2845 | 1835.433 | 27531.4948
2020-03-05 02:00 | 5.5957 | 5.89 | 206.7335 | 1166.8872 | 17503.3076
2020-03-05 03:00 | 4.7235 | 4.9719 | 222.492 | 673.1518 | 10097.2777
2020-03-05 04:00 | 4.3469 | 4.5755 | 241.1016 | 505.8577 | 7587.8652
2020-03-05 05:00 | 3.938 | 4.1451 | 260.1932 | 349.078 | 5236.1701
2020-03-05 06:00 | 2.9917 | 3.1491 | 273.4981 | 79.9039 | 1198.558
2020-03-05 07:00 | 2.3371 | 2.46 | 274.5818 | 0 | 0
2020-03-05 08:00 | 2.1274 | 2.2393 | 261.2733 | 0 | 0
2020-03-05 09:00 | 2.6373 | 2.776 | 260.3544 | 0 | 0
2020-03-05 10:00 | 2.9987 | 3.1564 | 273.2309 | 81.4749 | 1222.1229
2020-03-05 11:00 | 3.2726 | 3.4447 | 282.4703 | 143.1694 | 2147.5416
2020-03-05 12:00 | 3.3464 | 3.5224 | 297.787 | 161.4158 | 2421.2366
2020-03-05 13:00 | 3.1571 | 3.3232 | 309.5022 | 117.163 | 1757.4456
2020-03-05 14:00 | 3.1194 | 3.2834 | 320.9651 | 108.6527 | 1629.7908
2020-03-05 15:00 | 3.1456 | 3.311 | 333.341 | 114.56 | 1718.4
2020-03-05 16:00 | 2.9592 | 3.1148 | 346.3154 | 72.5688 | 1088.5316
2020-03-05 17:00 | 2.7714 | 2.9172 | 1.9556 | 0 | 0
2020-03-05 18:00 | 2.9006 | 3.0532 | 7.433 | 59.3778 | 890.6663
2020-03-05 19:00 | 3.0111 | 3.1694 | 2.1726 | 84.2606 | 1263.9088
2020-03-05 20:00 | 2.9817 | 3.1385 | 344.3787 | 77.6407 | 1164.6111
2020-03-05 21:00 | 3.1632 | 3.3296 | 335.0237 | 118.5313 | 1777.9694
2020-03-05 22:00 | 3.5834 | 3.7718 | 332.3638 | 232.7454 | 3491.1812
2020-03-05 23:00 | 3.7949 | 3.9945 | 328.1331 | 296.417 | 4446.2549
2020-03-06 00:00 | 3.974 | 4.1831 | 331.6232 | 362.4336 | 5436.5044
2020-03-06 01:00 | 3.6477 | 3.8395 | 341.4665 | 252.0976 | 3781.4645
2020-03-06 02:00 | 3.5963 | 3.7855 | 346.289 | 236.6473 | 3549.7102
2020-03-06 03:00 | 3.2312 | 3.4012 | 343.0445 | 133.8519 | 2007.778
2020-03-06 04:00 | 2.8891 | 3.0411 | 340.1275 | 56.7954 | 851.9306
2020-03-06 05:00 | 2.978 | 3.1347 | 328.3209 | 76.8183 | 1152.275
2020-03-06 06:00 | 2.2525 | 2.371 | 333.4322 | 0 | 0
2020-03-06 07:00 | 1.2782 | 1.3454 | 6.9858 | 0 | 0
2020-03-06 08:00 | 0.55895 | 0.58834 | 55.1216 | 0 | 0
2020-03-06 09:00 | 1.092 | 1.1495 | 192.2927 | 0 | 0
2020-03-06 10:00 | 1.0881 | 1.1453 | 191.4494 | 0 | 0
2020-03-06 11:00 | 1.0725 | 1.1289 | 195.7022 | 0 | 0
2020-03-06 12:00 | 1.0545 | 1.11 | 163.5 | 0 | 0
2020-03-06 13:00 | 1.569 | 1.6516 | 138.5929 | 0 | 0
2020-03-06 14:00 | 2.2129 | 2.3293 | 139.9648 | 0 | 0
2020-03-06 15:00 | 2.2269 | 2.344 | 130.7428 | 0 | 0
2020-03-06 16:00 | 2.2433 | 2.3613 | 96.055 | 0 | 0
2020-03-06 17:00 | 2.8718 | 3.0229 | 76.3809 | 52.8973 | 793.4602
2020-03-06 18:00 | 3.666 | 3.8588 | 72.7671 | 257.6176 | 3864.2644
2020-03-06 19:00 | 4.4107 | 4.6426 | 82.8163 | 534.1929 | 8012.893
2020-03-06 20:00 | 4.5962 | 4.8379 | 95.0207 | 616.5962 | 9248.9433
2020-03-06 21:00 | 3.7505 | 3.9478 | 105.4728 | 283.0604 | 4245.9067
2020-03-06 22:00 | 1.722 | 1.8125 | 145.8661 | 0 | 0
2020-03-06 23:00 | 1.1673 | 1.2287 | 156.0986 | 0 | 0
2020-03-07 00:00 | 0.57593 | 0.60622 | 135.0623 | 0 | 0
2020-03-07 01:00 | 0.24088 | 0.25355 | 18.3202 | 0 | 0
2020-03-07 02:00 | 0.73717 | 0.77594 | 1.1018 | 0 | 0
2020-03-07 03:00 | 1.0869 | 1.1441 | 355.8636 | 0 | 0
2020-03-07 04:00 | 1.0239 | 1.0778 | 348.5725 | 0 | 0
2020-03-07 05:00 | 0.877 | 0.92312 | 331.5189 | 0 | 0
2020-03-07 06:00 | 0.56013 | 0.58959 | 24.7408 | 0 | 0
2020-03-07 07:00 | 0.28211 | 0.29695 | 42.7423 | 0 | 0
2020-03-07 08:00 | 0.39748 | 0.41838 | 131.2054 | 0 | 0
2020-03-07 09:00 | 1.2769 | 1.3441 | 163.1118 | 0 | 0
2020-03-07 10:00 | 2.307 | 2.4283 | 172.7138 | 0 | 0
2020-03-07 11:00 | 2.8428 | 2.9923 | 187.7642 | 0 | 0
2020-03-07 12:00 | 2.8779 | 3.0292 | 191.2191 | 54.2555 | 813.8327
2020-03-07 13:00 | 2.7457 | 2.8901 | 186.3645 | 0 | 0
2020-03-07 14:00 | 2.3898 | 2.5155 | 188.2484 | 0 | 0
2020-03-07 15:00 | 1.4914 | 1.5699 | 196.1675 | 0 | 0
2020-03-07 16:00 | 0.76393 | 0.8041 | 199.1751 | 0 | 0
2020-03-07 17:00 | 0.83717 | 0.8812 | 204.5447 | 0 | 0
2020-03-07 18:00 | 1.9454 | 2.0477 | 214.2168 | 0 | 0
2020-03-07 19:00 | 3.003 | 3.161 | 239.8882 | 82.4437 | 1236.6549
2020-03-07 20:00 | 3.8479 | 4.0503 | 266.9213 | 315.7151 | 4735.7266
2020-03-07 21:00 | 4.2954 | 4.5213 | 278.303 | 482.9899 | 7244.8485
2020-03-07 22:00 | 4.4242 | 4.6569 | 298.3165 | 540.1998 | 8102.9964
2020-03-07 23:00 | 4.0135 | 4.2245 | 306.1319 | 377.0386 | 5655.5792
2020-03-08 00:00 | 3.7406 | 3.9374 | 305.2806 | 280.0823 | 4201.2342
2020-03-08 01:00 | 3.6851 | 3.879 | 300.503 | 263.3815 | 3950.7228
2020-03-08 02:00 | 4.1087 | 4.3248 | 300.0538 | 412.3325 | 6184.988
2020-03-08 03:00 | 4.2699 | 4.4944 | 302.3256 | 472.0373 | 7080.5595
2020-03-08 04:00 | 4.2676 | 4.4921 | 306.6713 | 471.2198 | 7068.297
2020-03-08 05:00 | 4.0404 | 4.2529 | 310.6554 | 387.0223 | 5805.335
2020-03-08 06:00 | 3.3922 | 3.5706 | 308.5664 | 175.183 | 2627.7456
2020-03-08 07:00 | 2.3697 | 2.4943 | 308.1029 | 0 | 0
2020-03-08 08:00 | 1.9536 | 2.0563 | 309.2733 | 0 | 0
2020-03-08 09:00 | 1.8892 | 1.9886 | 313.3656 | 0 | 0
2020-03-08 10:00 | 2.6433 | 2.7823 | 320.75 | 0 | 0
2020-03-08 11:00 | 3.2015 | 3.3698 | 318.2719 | 127.1439 | 1907.1585
2020-03-08 12:00 | 3.4734 | 3.6561 | 314.8339 | 199.6364 | 2994.5456
2020-03-08 13:00 | 3.5154 | 3.7003 | 315.4377 | 212.2981 | 3184.4708
2020-03-08 14:00 | 3.5468 | 3.7334 | 319.6964 | 221.7507 | 3326.2605
2020-03-08 15:00 | 3.4241 | 3.6042 | 320.199 | 184.7933 | 2771.8993
2020-03-08 16:00 | 3.7265 | 3.9225 | 315.2279 | 275.845 | 4137.6753
2020-03-08 17:00 | 4.0543 | 4.2675 | 320.5169 | 392.1614 | 5882.4204
2020-03-08 18:00 | 4.1174 | 4.3339 | 328.5217 | 415.5442 | 6233.1633
2020-03-08 19:00 | 4.2116 | 4.4331 | 335.2386 | 450.4602 | 6756.9026
2020-03-08 20:00 | 4.1971 | 4.4178 | 346.9763 | 445.0772 | 6676.1578
2020-03-08 21:00 | 3.9437 | 4.1512 | 354.7696 | 351.2093 | 5268.1398
2020-03-08 22:00 | 4.5901 | 4.8315 | 11.3409 | 613.8906 | 9208.3595
2020-03-08 23:00 | 4.4968 | 4.7333 | 22.3329 | 572.4393 | 8586.5888
2020-03-09 00:00 | 4.7221 | 4.9705 | 31.9168 | 672.5389 | 10088.0834
2020-03-09 01:00 | 4.8902 | 5.1474 | 39.0705 | 758.9761 | 11384.6414
2020-03-09 02:00 | 4.7703 | 5.0212 | 50.1661 | 695.6355 | 10434.5331
2020-03-09 03:00 | 4.8094 | 5.0623 | 60.3023 | 716.2972 | 10744.4575
2020-03-09 04:00 | 4.7622 | 5.0126 | 68.3543 | 691.3468 | 10370.2017
2020-03-09 05:00 | 4.7352 | 4.9843 | 74.1464 | 678.3723 | 10175.5849
2020-03-09 06:00 | 4.2329 | 4.4556 | 87.8521 | 458.3547 | 6875.3198
2020-03-09 07:00 | 4.4524 | 4.6866 | 101.0761 | 552.7319 | 8290.9783
2020-03-09 08:00 | 4.5577 | 4.7974 | 115.6311 | 599.5191 | 8992.7871
2020-03-09 09:00 | 4.484 | 4.7198 | 129.3518 | 566.7608 | 8501.4115
2020-03-09 10:00 | 4.6664 | 4.9118 | 131.2894 | 647.7759 | 9716.6382
2020-03-09 11:00 | 3.8894 | 4.0939 | 141.6318 | 331.0667 | 4966.0001
2020-03-09 12:00 | 2.918 | 3.0715 | 152.7091 | 63.2994 | 949.4911
2020-03-09 13:00 | 3.0647 | 3.2259 | 151.0438 | 96.3472 | 1445.2085
2020-03-09 14:00 | 3.4016 | 3.5805 | 155.1506 | 178.0369 | 2670.5532
2020-03-09 15:00 | 3.294 | 3.4672 | 166.8461 | 147.9889 | 2219.8332
2020-03-09 16:00 | 3.0362 | 3.1959 | 168.6962 | 89.9146 | 1348.7195
2020-03-09 17:00 | 3.0083 | 3.1666 | 175.0068 | 83.6466 | 1254.6984
2020-03-09 18:00 | 2.1804 | 2.2951 | 200.4959 | 0 | 0
2020-03-09 19:00 | 1.7544 | 1.8467 | 243.7001 | 0 | 0
2020-03-09 20:00 | 2.1093 | 2.2203 | 281.7993 | 0 | 0
2020-03-09 21:00 | 3.1001 | 3.2631 | 303.3104 | 104.3089 | 1564.6338
2020-03-09 22:00 | 3.7375 | 3.9341 | 305.2417 | 279.1488 | 4187.2321
2020-03-09 23:00 | 4.9519 | 5.2124 | 313.494 | 791.6136 | 11874.2047
2020-03-10 00:00 | 5.5406 | 5.832 | 320.2394 | 1132.5691 | 16988.5361
2020-03-10 01:00 | 5.5267 | 5.8174 | 327.6917 | 1123.9094 | 16858.6409
2020-03-10 02:00 | 5.6269 | 5.9228 | 334.4767 | 1186.2933 | 17794.3996
2020-03-10 03:00 | 5.7313 | 6.0328 | 334.3198 | 1254.9325 | 18823.9878
2020-03-10 04:00 | 5.656 | 5.9534 | 337.7778 | 1204.4309 | 18066.4639
2020-03-10 05:00 | 5.5865 | 5.8803 | 343.8822 | 1161.1206 | 17416.8097
2020-03-10 06:00 | 5.103 | 5.3714 | 345.685 | 871.4501 | 13071.7517
2020-03-10 07:00 | 4.8702 | 5.1263 | 349.3086 | 748.4026 | 11226.0391
2020-03-10 08:00 | 4.53 | 4.7683 | 353.018 | 587.213 | 8808.1946
2020-03-10 09:00 | 4.1502 | 4.3685 | 354.5212 | 427.716 | 6415.74
2020-03-10 10:00 | 4.0902 | 4.3054 | 353.577 | 405.4916 | 6082.3745
2020-03-10 11:00 | 4.1608 | 4.3796 | 348.335 | 431.6239 | 6474.3584
2020-03-10 12:00 | 4.3516 | 4.5805 | 346.8091 | 507.9802 | 7619.7031
2020-03-10 13:00 | 4.4678 | 4.7027 | 347.6492 | 559.5589 | 8393.3837
2020-03-10 14:00 | 4.0029 | 4.2134 | 355.8271 | 373.1299 | 5596.9479
2020-03-10 15:00 | 3.8402 | 4.0422 | 357.8919 | 312.8621 | 4692.9316
2020-03-10 16:00 | 4.3874 | 4.6182 | 355.0219 | 523.8809 | 7858.2139
2020-03-10 17:00 | 4.415 | 4.6472 | 359.4859 | 536.1288 | 8041.9317
2020-03-10 18:00 | 4.2253 | 4.4475 | 1.6713 | 455.5272 | 6832.9084
2020-03-10 19:00 | 4.2576 | 4.4815 | 359.2291 | 467.4928 | 7012.3914
2020-03-10 20:00 | 4.3416 | 4.5699 | 352.0624 | 503.4963 | 7552.4439
2020-03-10 21:00 | 4.083 | 4.2977 | 344.7757 | 402.8074 | 6042.1115
2020-03-10 22:00 | 4.274 | 4.4988 | 341.3718 | 473.5817 | 7103.725
2020-03-10 23:00 | 3.5764 | 3.7645 | 344.0238 | 230.646 | 3459.6895
2020-03-11 00:00 | 2.7565 | 2.9015 | 336.3327 | 0 | 0
2020-03-11 01:00 | 1.8737 | 1.9723 | 317.5304 | 0 | 0
2020-03-11 02:00 | 1.8894 | 1.9888 | 282.5847 | 0 | 0
2020-03-11 03:00 | 3.1903 | 3.3581 | 251.9109 | 124.6292 | 1869.4382
2020-03-11 04:00 | 5.0761 | 5.3431 | 233.5279 | 857.2233 | 12858.3495
2020-03-11 05:00 | 6.4533 | 6.7927 | 228.5115 | 1819.6594 | 27294.8915
2020-03-11 06:00 | 6.6454 | 6.995 | 223.0884 | 1983.9007 | 29758.5111
2020-03-11 07:00 | 6.5827 | 6.929 | 221.0447 | 1930.3158 | 28954.7366
2020-03-11 08:00 | 7.3296 | 7.7151 | 225.9399 | 2681.5629 | 40223.4434
2020-03-11 09:00 | 8.8182 | 9.282 | 238.7183 | 4411.7146 | 66175.7183
2020-03-11 10:00 | 8.828 | 9.2923 | 240.6657 | 4422.756 | 66341.3397
2020-03-11 11:00 | 8.4409 | 8.8848 | 229.7521 | 3980.1011 | 59701.5162
2020-03-11 12:00 | 10.0827 | 10.613 | 235.9653 | 5391.1705 | 80867.5574
2020-03-11 13:00 | 10.0198 | 10.5468 | 245.4581 | 5365.8735 | 80488.1031
2020-03-11 14:00 | 9.4944 | 9.9938 | 255.833 | 5050.8798 | 75763.1971
2020-03-11 15:00 | 9.2779 | 9.7659 | 263.7077 | 4863.5496 | 72953.2442
2020-03-11 16:00 | 8.8205 | 9.2844 | 266.7142 | 4414.3196 | 66214.7942
2020-03-11 17:00 | 8.7539 | 9.2143 | 264.7807 | 4339.2595 | 65088.8926
2020-03-11 18:00 | 9.3388 | 9.83 | 269.0108 | 4916.2573 | 73743.8591
2020-03-11 19:00 | 9.767 | 10.2807 | 273.9057 | 5219.9474 | 78299.2114
2020-03-11 20:00 | 10.4071 | 10.9544 | 282.7054 | 5521.5891 | 82823.8367
2020-03-11 21:00 | 10.0534 | 10.5821 | 289.2295 | 5379.3776 | 80690.6647
2020-03-11 22:00 | 10.5889 | 11.1458 | 292.0082 | 5571.9443 | 83579.1639
2020-03-11 23:00 | 9.3689 | 9.8616 | 287.5752 | 4942.2722 | 74134.0833
2020-03-12 00:00 | 8.9847 | 9.4572 | 282.1927 | 4599.2507 | 68988.76
2020-03-12 01:00 | 8.6603 | 9.1158 | 276.844 | 4233.8703 | 63508.0542
2020-03-12 02:00 | 8.7492 | 9.2094 | 274.9593 | 4334.0687 | 65011.0298
2020-03-12 03:00 | 8.805 | 9.2681 | 274.977 | 4396.8313 | 65952.4691
2020-03-12 04:00 | 8.4544 | 8.8991 | 272.6944 | 3996.1523 | 59942.2843
2020-03-12 05:00 | 8.2918 | 8.7279 | 266.4051 | 3803.0187 | 57045.2803
2020-03-12 06:00 | 7.6464 | 8.0485 | 258.981 | 3037.6265 | 45564.3972
2020-03-12 07:00 | 6.4266 | 6.7646 | 247.8477 | 1796.8225 | 26952.3382
2020-03-12 08:00 | 6.8293 | 7.1885 | 243.4295 | 2163.6822 | 32455.2327
2020-03-12 09:00 | 7.4346 | 7.8256 | 238.1903 | 2798.4681 | 41977.0212
2020-03-12 10:00 | 7.9556 | 8.374 | 233.6051 | 3404.1106 | 51061.6595
2020-03-12 11:00 | 8.7875 | 9.2496 | 229.1482 | 4377.1084 | 65656.6265
2020-03-12 12:00 | 9.4945 | 9.9938 | 222.1415 | 5050.9211 | 75763.8167
2020-03-12 13:00 | 10.1561 | 10.6902 | 220.2057 | 5420.6593 | 81309.889
2020-03-12 14:00 | 10.5046 | 11.0571 | 224.9699 | 5551.9112 | 83278.6678
2020-03-12 15:00 | 10.258 | 10.7975 | 222.6382 | 5461.6323 | 81924.485
2020-03-12 16:00 | 10.491 | 11.0428 | 219.6378 | 5548.6694 | 83230.0417
2020-03-12 17:00 | 11.1484 | 11.7347 | 225.7752 | 5674.0615 | 85110.9227
2020-03-12 18:00 | 11.8027 | 12.4234 | 239.0439 | 5699.8469 | 85497.7034
2020-03-12 19:00 | 11.9235 | 12.5506 | 240.0716 | 5700 | 85500
2020-03-12 20:00 | 12.0507 | 12.6846 | 237.525 | 5700 | 85500
2020-03-12 21:00 | 11.9472 | 12.5755 | 238.2095 | 5700 | 85500
2020-03-12 22:00 | 12.9044 | 13.5831 | 244.0689 | 5700 | 85500
2020-03-12 23:00 | 12.2236 | 12.8665 | 250.582 | 5700 | 85500
2020-03-13 00:00 | 10.9174 | 11.4916 | 273.762 | 5650.1007 | 84751.51
2020-03-13 01:00 | 9.502 | 10.0018 | 289.4757 | 5057.0381 | 75855.5708
2020-03-13 02:00 | 8.8586 | 9.3246 | 290.84 | 4457.2746 | 66859.1189
2020-03-13 03:00 | 8.9777 | 9.4499 | 290.0009 | 4591.4087 | 68871.1311
2020-03-13 04:00 | 8.0891 | 8.5145 | 288.0072 | 3562.3596 | 53435.3935
2020-03-13 05:00 | 7.473 | 7.8661 | 285.4089 | 2841.3204 | 42619.8065
2020-03-13 06:00 | 6.9052 | 7.2683 | 282.8425 | 2238.098 | 33571.4699
2020-03-13 07:00 | 7.5022 | 7.8968 | 283.8147 | 2873.7919 | 43106.8783
2020-03-13 08:00 | 6.7846 | 7.1414 | 284.9347 | 2119.7725 | 31796.5881
2020-03-13 09:00 | 6.069 | 6.3882 | 279.0844 | 1503.7135 | 22555.703
2020-03-13 10:00 | 5.7392 | 6.041 | 266.9835 | 1260.7126 | 18910.6883
2020-03-13 11:00 | 5.8496 | 6.1572 | 263.4746 | 1342.0594 | 20130.8911
2020-03-13 12:00 | 5.3333 | 5.6138 | 257.5809 | 1003.3948 | 15050.9218
2020-03-13 13:00 | 6.418 | 6.7555 | 258.5169 | 1789.4699 | 26842.0484
2020-03-13 14:00 | 5.8816 | 6.1909 | 257.306 | 1365.6231 | 20484.3466
2020-03-13 15:00 | 5.7024 | 6.0023 | 254.0544 | 1233.6194 | 18504.2914
2020-03-13 16:00 | 6.01 | 6.3261 | 255.1515 | 1460.2573 | 21903.8599
2020-03-13 17:00 | 6.9358 | 7.3006 | 254.4709 | 2268.127 | 34021.9048
2020-03-13 18:00 | 7.5587 | 7.9563 | 261.2378 | 2936.7159 | 44050.7379
2020-03-13 19:00 | 7.709 | 8.1144 | 263.8161 | 3111.8315 | 46677.4722
2020-03-13 20:00 | 7.6635 | 8.0665 | 264.6469 | 3057.914 | 45868.7099
2020-03-13 21:00 | 7.8036 | 8.214 | 263.7676 | 3223.9925 | 48359.8877
2020-03-13 22:00 | 8.1942 | 8.6251 | 264.8391 | 3687.156 | 55307.3406
2020-03-13 23:00 | 8.3634 | 8.8033 | 263.4043 | 3888.1058 | 58321.5863
2020-03-14 00:00 | 8.014 | 8.4355 | 260.68 | 3473.3223 | 52099.8339
2020-03-14 01:00 | 8.4571 | 8.9019 | 256.6552 | 3999.3922 | 59990.8837
2020-03-14 02:00 | 8.7618 | 9.2226 | 253.2754 | 4348.2347 | 65223.5205
2020-03-14 03:00 | 9.5689 | 10.0722 | 254.794 | 5098.141 | 76472.1148
2020-03-14 04:00 | 10.2724 | 10.8127 | 259.7153 | 5467.4393 | 82011.5889
2020-03-14 05:00 | 10.3331 | 10.8765 | 263.866 | 5491.842 | 82377.6306
2020-03-14 06:00 | 9.6821 | 10.1914 | 263.9908 | 5167.7487 | 77516.2305
2020-03-14 07:00 | 12.7721 | 13.4439 | 272.2201 | 5700 | 85500
2020-03-14 08:00 | 13.9829 | 14.7183 | 276.5751 | 5700 | 85500
2020-03-14 09:00 | 13.7988 | 14.5246 | 276.1214 | 5700 | 85500
2020-03-14 10:00 | 14.1257 | 14.8686 | 278.4434 | 5700 | 85500
2020-03-14 11:00 | 14.9502 | 15.7365 | 286.1818 | 5700 | 85500
2020-03-14 12:00 | 14.5598 | 15.3255 | 295.0076 | 5700 | 85500
2020-03-14 13:00 | 14.2468 | 14.9961 | 302.9282 | 5700 | 85500
2020-03-14 14:00 | 12.8931 | 13.5712 | 305.4007 | 5700 | 85500
2020-03-14 15:00 | 11.1379 | 11.7237 | 304.626 | 5673.0292 | 85095.4375
2020-03-14 16:00 | 9.1709 | 9.6533 | 301.5678 | 4771.0045 | 71565.0674
2020-03-14 17:00 | 8.6277 | 9.0815 | 299.5806 | 4197.1971 | 62957.9566
2020-03-14 18:00 | 8.926 | 9.3954 | 304.8426 | 4533.1073 | 67996.6095
2020-03-14 19:00 | 9.0097 | 9.4836 | 314.9844 | 4627.41 | 69411.1504
2020-03-14 20:00 | 8.2643 | 8.6989 | 319.1533 | 3770.3789 | 56555.6833
2020-03-14 21:00 | 7.7554 | 8.1633 | 315.1373 | 3166.8911 | 47503.3668
2020-03-14 22:00 | 9.6392 | 10.1461 | 314.2204 | 5141.3389 | 77120.0831
2020-03-14 23:00 | 10.0522 | 10.5809 | 318.4699 | 5378.9136 | 80683.7034
2020-03-15 00:00 | 9.6562 | 10.1641 | 317.3405 | 5151.8178 | 77277.2673
2020-03-15 01:00 | 9.4111 | 9.9061 | 316.3878 | 4978.7943 | 74681.9142
2020-03-15 02:00 | 10.3122 | 10.8546 | 324.0681 | 5483.4444 | 82251.6664
2020-03-15 03:00 | 9.4341 | 9.9303 | 326.7525 | 4998.6883 | 74980.3247
2020-03-15 04:00 | 8.2939 | 8.7301 | 323.9277 | 3805.5482 | 57083.2226
2020-03-15 05:00 | 7.6388 | 8.0405 | 320.6402 | 3028.6453 | 45429.6799
2020-03-15 06:00 | 8.5054 | 8.9528 | 323.6335 | 4056.7109 | 60850.6634
2020-03-15 07:00 | 8.4958 | 8.9426 | 326.5276 | 4045.2952 | 60679.4282
2020-03-15 08:00 | 8.4765 | 8.9223 | 325.8963 | 4022.3203 | 60334.8049
2020-03-15 09:00 | 8.9292 | 9.3989 | 327.4107 | 4536.7757 | 68051.636
2020-03-15 10:00 | 9.2717 | 9.7594 | 319.3236 | 4858.2044 | 72873.0656
2020-03-15 11:00 | 9.3108 | 9.8005 | 319.8514 | 4892.0278 | 73380.4173
2020-03-15 12:00 | 9.509 | 10.0091 | 318.7369 | 5061.3119 | 75919.6779
2020-03-15 13:00 | 9.5544 | 10.0569 | 321.3204 | 5089.2577 | 76338.865
2020-03-15 14:00 | 9.3488 | 9.8405 | 326.3446 | 4924.8829 | 73873.2442
2020-03-15 15:00 | 7.8475 | 8.2602 | 330.6076 | 3276.0027 | 49140.04
2020-03-15 16:00 | 6.8682 | 7.2294 | 332.7491 | 2201.7944 | 33026.916
2020-03-15 17:00 | 6.2893 | 6.62 | 330.0699 | 1679.4698 | 25192.0474
2020-03-15 18:00 | 6.0188 | 6.3354 | 323.7042 | 1466.7487 | 22001.231
2020-03-15 19:00 | 6.1348 | 6.4574 | 315.7371 | 1552.2133 | 23283.199
2020-03-15 20:00 | 6.2847 | 6.6152 | 310.6304 | 1675.5774 | 25133.6615
2020-03-15 21:00 | 6.2468 | 6.5753 | 308.5489 | 1643.1705 | 24647.5574
2020-03-15 22:00 | 6.133 | 6.4555 | 305.461 | 1550.8649 | 23262.9742
2020-03-15 23:00 | 5.5753 | 5.8685 | 302.2363 | 1154.1712 | 17312.5681
2020-03-16 00:00 | 5.2652 | 5.5421 | 296.133 | 960.9144 | 14413.7162
2020-03-16 01:00 | 5.7751 | 6.0789 | 294.6756 | 1287.2021 | 19308.0316
2020-03-16 02:00 | 5.5043 | 5.7938 | 290.983 | 1109.9306 | 16648.9594
2020-03-16 03:00 | 5.0778 | 5.3449 | 280.6045 | 858.1372 | 12872.058
2020-03-16 04:00 | 4.874 | 5.1304 | 269.3609 | 750.4451 | 11256.6772
2020-03-16 05:00 | 4.6423 | 4.8865 | 256.6832 | 637.0984 | 9556.4758
2020-03-16 06:00 | 3.8152 | 4.0159 | 244.5184 | 303.5907 | 4553.8603
2020-03-16 07:00 | 3.1798 | 3.347 | 240.3541 | 122.2562 | 1833.8432
2020-03-16 08:00 | 3.727 | 3.923 | 235.3878 | 275.9742 | 4139.6134
2020-03-16 09:00 | 3.696 | 3.8904 | 226.6419 | 266.6623 | 3999.9342
2020-03-16 10:00 | 3.5664 | 3.7539 | 219.0052 | 227.6295 | 3414.4427
2020-03-16 11:00 | 3.8106 | 4.011 | 214.3481 | 301.8744 | 4528.1167
2020-03-16 12:00 | 4.2983 | 4.5243 | 210.985 | 484.2732 | 7264.098
2020-03-16 13:00 | 4.7018 | 4.9491 | 207.5245 | 663.5216 | 9952.8245
2020-03-16 14:00 | 5.0796 | 5.3468 | 200.3953 | 859.0949 | 12886.4235
2020-03-16 15:00 | 6.0939 | 6.4144 | 192.7996 | 1522.0749 | 22831.1231
2020-03-16 16:00 | 7.6006 | 8.0004 | 192.7114 | 2983.4203 | 44751.3047
2020-03-16 17:00 | 8.8964 | 9.3643 | 197.642 | 4499.8292 | 67497.4387
2020-03-16 18:00 | 9.2061 | 9.6902 | 204.612 | 4801.382 | 72020.7304
2020-03-16 19:00 | 9.2924 | 9.7812 | 209.9214 | 4876.1309 | 73141.9632
2020-03-16 20:00 | 9.4835 | 9.9823 | 210.6967 | 5041.4272 | 75621.4078
2020-03-16 21:00 | 9.5409 | 10.0427 | 212.4682 | 5080.9392 | 76214.0882
2020-03-16 22:00 | 9.4887 | 9.9877 | 214.4508 | 5045.9098 | 75688.6464
2020-03-16 23:00 | 9.1066 | 9.5855 | 216.7533 | 4715.3143 | 70729.7144
2020-03-17 00:00 | 9.1676 | 9.6497 | 217.3795 | 4768.0859 | 71521.2878
2020-03-17 01:00 | 9.0275 | 9.5023 | 219.3143 | 4646.874 | 69703.1107
2020-03-17 02:00 | 8.6594 | 9.1148 | 224.5447 | 4232.885 | 63493.2743
2020-03-17 03:00 | 8.3179 | 8.7553 | 230.9806 | 3834.0156 | 57510.2343
2020-03-17 04:00 | 7.8483 | 8.2611 | 243.3118 | 3277.0196 | 49155.2937
2020-03-17 05:00 | 7.7667 | 8.1752 | 245.7126 | 3180.2606 | 47703.9094
2020-03-17 06:00 | 7.1558 | 7.5322 | 251.4357 | 2488.076 | 37321.1395
2020-03-17 07:00 | 6.3207 | 6.6531 | 257.9875 | 1706.3113 | 25594.6693
2020-03-17 08:00 | 5.1185 | 5.3877 | 271.559 | 879.6052 | 13194.0786
2020-03-17 09:00 | 4.6399 | 4.8839 | 292.7756 | 636.0139 | 9540.209
2020-03-17 10:00 | 4.3767 | 4.6069 | 307.5868 | 519.1164 | 7786.7454
2020-03-17 11:00 | 5.2709 | 5.5481 | 322.4544 | 964.4583 | 14466.875
2020-03-17 12:00 | 5.3176 | 5.5973 | 333.4277 | 993.6102 | 14904.1533
2020-03-17 13:00 | 5.4485 | 5.7351 | 346.6007 | 1075.1674 | 16127.5109
2020-03-17 14:00 | 5.1342 | 5.4042 | 1.3149 | 887.9134 | 13318.7006
2020-03-17 15:00 | 4.888 | 5.1451 | 11.0273 | 757.8537 | 11367.806
2020-03-17 16:00 | 4.6102 | 4.8527 | 23.2041 | 622.8386 | 9342.5787
2020-03-17 17:00 | 4.6942 | 4.9411 | 29.3226 | 660.1539 | 9902.3084
2020-03-17 18:00 | 4.5295 | 4.7678 | 34.4135 | 587.0004 | 8805.0055
2020-03-17 19:00 | 4.3255 | 4.553 | 39.4447 | 496.3477 | 7445.2155
2020-03-17 20:00 | 4.0321 | 4.2442 | 48.3605 | 383.9543 | 5759.3152
2020-03-17 21:00 | 3.5199 | 3.705 | 61.0439 | 213.6267 | 3204.4007
2020-03-17 22:00 | 2.9634 | 3.1193 | 75.0877 | 73.5229 | 1102.8436
2020-03-17 23:00 | 1.9626 | 2.0658 | 85.4787 | 0 | 0
2020-03-18 00:00 | 0.92265 | 0.97118 | 64.5868 | 0 | 0
2020-03-18 01:00 | 0.77482 | 0.81557 | 20.4482 | 0 | 0
2020-03-18 02:00 | 1.1975 | 1.2605 | 1.4281 | 0 | 0
2020-03-18 03:00 | 1.4216 | 1.4964 | 1.4171 | 0 | 0
2020-03-18 04:00 | 1.1494 | 1.2098 | 18.4629 | 0 | 0
2020-03-18 05:00 | 0.75388 | 0.79353 | 52.5099 | 0 | 0
2020-03-18 06:00 | 0.72267 | 0.76067 | 120.8893 | 0 | 0
2020-03-18 07:00 | 1.0233 | 1.0771 | 163.8118 | 0 | 0
2020-03-18 08:00 | 1.6492 | 1.736 | 180.2073 | 0 | 0
2020-03-18 09:00 | 2.275 | 2.3946 | 207.2123 | 0 | 0
2020-03-18 10:00 | 2.8901 | 3.0421 | 214.4355 | 57.0066 | 855.0987
2020-03-18 11:00 | 3.5621 | 3.7495 | 224.4413 | 226.35 | 3395.2506
2020-03-18 12:00 | 4.1914 | 4.4119 | 232.4639 | 442.984 | 6644.7605
2020-03-18 13:00 | 4.4288 | 4.6617 | 243.5524 | 542.2564 | 8133.8458
2020-03-18 14:00 | 4.4397 | 4.6732 | 252.3098 | 547.0876 | 8206.3142
2020-03-18 15:00 | 4.5442 | 4.7832 | 250.7772 | 593.5005 | 8902.507
2020-03-18 16:00 | 5.1163 | 5.3854 | 247.2736 | 878.4742 | 13177.1125
2020-03-18 17:00 | 5.7341 | 6.0357 | 245.3627 | 1256.9662 | 18854.4927
2020-03-18 18:00 | 6.3951 | 6.7314 | 245.4855 | 1769.9318 | 26548.9764
2020-03-18 19:00 | 6.9477 | 7.3131 | 245.8338 | 2279.7919 | 34196.8779
2020-03-18 20:00 | 7.4266 | 7.8172 | 240.7587 | 2789.5901 | 41843.8511
2020-03-18 21:00 | 7.6178 | 8.0185 | 243.8272 | 3003.8233 | 45057.3493
2020-03-18 22:00 | 7.907 | 8.3229 | 249.9641 | 3346.581 | 50198.7154
2020-03-18 23:00 | 8.0129 | 8.4344 | 251.0169 | 3472.1207 | 52081.8103
2020-03-19 00:00 | 8.0091 | 8.4304 | 248.8885 | 3467.5782 | 52013.6725
2020-03-19 01:00 | 7.9763 | 8.3958 | 250.3242 | 3428.7228 | 51430.8416
2020-03-19 02:00 | 8.1083 | 8.5348 | 252.8561 | 3585.2464 | 53778.6967
2020-03-19 03:00 | 8.1572 | 8.5862 | 253.9972 | 3643.2619 | 54648.9285
2020-03-19 04:00 | 7.9455 | 8.3633 | 257.7139 | 3392.1312 | 50881.9674
2020-03-19 05:00 | 7.7513 | 8.1589 | 260.6954 | 3161.9632 | 47429.4483
2020-03-19 06:00 | 7.247 | 7.6281 | 264.3002 | 2589.5815 | 38843.7219
2020-03-19 07:00 | 5.7472 | 6.0495 | 265.4862 | 1266.616 | 18999.2393
2020-03-19 08:00 | 5.117 | 5.3862 | 269.2118 | 878.86 | 13182.8994
2020-03-19 09:00 | 4.8894 | 5.1466 | 273.4911 | 758.5785 | 11378.6769
2020-03-19 10:00 | 4.5864 | 4.8277 | 274.3314 | 612.2702 | 9184.0537
2020-03-19 11:00 | 5.0182 | 5.2821 | 277.1951 | 826.6375 | 12399.5619
2020-03-19 12:00 | 5.7849 | 6.0891 | 279.808 | 1294.3727 | 19415.5911
2020-03-19 13:00 | 6.4879 | 6.8291 | 286.5282 | 1849.2665 | 27738.9975
2020-03-19 14:00 | 6.7019 | 7.0544 | 295.248 | 2038.7276 | 30580.9144
2020-03-19 15:00 | 6.8608 | 7.2217 | 302.048 | 2194.6107 | 32919.161
2020-03-19 16:00 | 7.1251 | 7.4998 | 303.8596 | 2453.8286 | 36807.4295
2020-03-19 17:00 | 7.7481 | 8.1556 | 307.8009 | 3158.2069 | 47373.104
2020-03-19 18:00 | 8.1855 | 8.616 | 314.6007 | 3676.8595 | 55152.8921
2020-03-19 19:00 | 7.9848 | 8.4048 | 321.0431 | 3438.783 | 51581.745
2020-03-19 20:00 | 7.7027 | 8.1078 | 326.0451 | 3104.4321 | 46566.4811
2020-03-19 21:00 | 7.3042 | 7.6884 | 330.7455 | 2653.3244 | 39799.8663
2020-03-19 22:00 | 6.543 | 6.8871 | 333.7748 | 1896.3606 | 28445.4084
2020-03-19 23:00 | 6.0962 | 6.4168 | 337.1667 | 1523.7893 | 22856.8393
2020-03-20 00:00 | 6.2058 | 6.5322 | 340.9244 | 1608.1463 | 24122.1939
2020-03-20 01:00 | 6.3979 | 6.7344 | 348.0298 | 1772.2954 | 26584.4305
2020-03-20 02:00 | 6.2005 | 6.5266 | 356.2103 | 1603.6043 | 24054.065
2020-03-20 03:00 | 5.9136 | 6.2246 | 2.3927 | 1389.2276 | 20838.4134
2020-03-20 04:00 | 5.6319 | 5.9281 | 7.3221 | 1189.4552 | 17841.8283
2020-03-20 05:00 | 5.1291 | 5.3989 | 11.1817 | 885.2392 | 13278.5882
2020-03-20 06:00 | 3.7976 | 3.9973 | 13.6936 | 297.236 | 4458.5404
2020-03-20 07:00 | 2.8578 | 3.0081 | 16.6483 | 49.7418 | 746.1274
2020-03-20 08:00 | 2.0439 | 2.1514 | 11.1762 | 0 | 0
2020-03-20 09:00 | 2.0165 | 2.1226 | 342.6141 | 0 | 0
2020-03-20 10:00 | 2.5313 | 2.6644 | 318.119 | 0 | 0
2020-03-20 11:00 | 3.0028 | 3.1607 | 317.6409 | 82.3901 | 1235.8508
2020-03-20 12:00 | 2.9949 | 3.1524 | 319.1582 | 80.6234 | 1209.3506
2020-03-20 13:00 | 2.8695 | 3.0204 | 322.041 | 52.3673 | 785.5088
2020-03-20 14:00 | 2.5698 | 2.7049 | 325.5383 | 0 | 0
2020-03-20 15:00 | 1.963 | 2.0663 | 342.5032 | 0 | 0
2020-03-20 16:00 | 2.0228 | 2.1292 | 10.199 | 0 | 0
2020-03-20 17:00 | 2.084 | 2.1936 | 24.0287 | 0 | 0
2020-03-20 18:00 | 1.8446 | 1.9416 | 49.077 | 0 | 0
2020-03-20 19:00 | 1.593 | 1.6768 | 96.3336 | 0 | 0
2020-03-20 20:00 | 1.9581 | 2.0611 | 143.7626 | 0 | 0
2020-03-20 21:00 | 2.4402 | 2.5685 | 176.8882 | 0 | 0
2020-03-20 22:00 | 2.0035 | 2.1089 | 209.2626 | 0 | 0
2020-03-20 23:00 | 1.511 | 1.5905 | 242.1501 | 0 | 0
2020-03-21 00:00 | 1.6189 | 1.704 | 297.5848 | 0 | 0
2020-03-21 01:00 | 3.665 | 3.8577 | 328.6398 | 257.3148 | 3859.7215
2020-03-21 02:00 | 5.2273 | 5.5022 | 344.8416 | 937.32 | 14059.8005
2020-03-21 03:00 | 5.6596 | 5.9572 | 350.6541 | 1206.6804 | 18100.2057
2020-03-21 04:00 | 5.5599 | 5.8524 | 352.3256 | 1144.6035 | 17169.052
2020-03-21 05:00 | 4.9465 | 5.2066 | 352.9497 | 788.7372 | 11831.0577
2020-03-21 06:00 | 4.2861 | 4.5115 | 351.4158 | 478.8629 | 7182.9435
2020-03-21 07:00 | 3.7193 | 3.9149 | 349.9229 | 273.6573 | 4104.8602
2020-03-21 08:00 | 3.8722 | 4.0758 | 352.5349 | 324.6981 | 4870.4714
2020-03-21 09:00 | 4.751 | 5.0009 | 349.7198 | 685.4385 | 10281.5772
2020-03-21 10:00 | 6.1303 | 6.4528 | 348.7983 | 1548.9319 | 23233.9781
2020-03-21 11:00 | 6.5205 | 6.8635 | 350.467 | 1877.1252 | 28156.8778
2020-03-21 12:00 | 6.3766 | 6.7119 | 353.0172 | 1754.0817 | 26311.2254
2020-03-21 13:00 | 6.0234 | 6.3402 | 351.2013 | 1470.1154 | 22051.7305
2020-03-21 14:00 | 5.6842 | 5.9832 | 345.6523 | 1222.0608 | 18330.9123
2020-03-21 15:00 | 5.7255 | 6.0266 | 348.7346 | 1250.6547 | 18759.8202
2020-03-21 16:00 | 5.2408 | 5.5164 | 347.3745 | 945.7311 | 14185.9669
2020-03-21 17:00 | 5.314 | 5.5935 | 348.8904 | 991.3242 | 14869.8632
2020-03-21 18:00 | 5.8978 | 6.208 | 354.1826 | 1377.5765 | 20663.6468
2020-03-21 19:00 | 6.4461 | 6.7851 | 358.7654 | 1813.5186 | 27202.7784
2020-03-21 20:00 | 6.9823 | 7.3495 | 2.9469 | 2313.7499 | 34706.2478
2020-03-21 21:00 | 7.1502 | 7.5262 | 5.8596 | 2481.7655 | 37226.4831
2020-03-21 22:00 | 7.3653 | 7.7527 | 3.6311 | 2721.359 | 40820.3854
2020-03-21 23:00 | 7.4051 | 7.7945 | 3.5217 | 2765.6327 | 41484.4906
2020-03-22 00:00 | 7.1763 | 7.5537 | 359.977 | 2510.818 | 37662.2705
2020-03-22 01:00 | 7.0476 | 7.4183 | 357.5865 | 2377.8117 | 35667.1758
2020-03-22 02:00 | 6.779 | 7.1355 | 355.2901 | 2114.287 | 31714.3055
2020-03-22 03:00 | 6.5974 | 6.9444 | 352.5563 | 1942.8366 | 29142.5491
2020-03-22 04:00 | 6.543 | 6.8871 | 350.8045 | 1896.3152 | 28444.7276
2020-03-22 05:00 | 6.6524 | 7.0022 | 351.1782 | 1990.0771 | 29851.1566
2020-03-22 06:00 | 7.3712 | 7.7588 | 357.9538 | 2727.8506 | 40917.7588
2020-03-22 07:00 | 7.3508 | 7.7374 | 2.9961 | 2705.1736 | 40577.6046
2020-03-22 08:00 | 6.6603 | 7.0106 | 3.6478 | 1997.8443 | 29967.6649
2020-03-22 09:00 | 6.1095 | 6.4309 | 3.9161 | 1533.6088 | 23004.132
2020-03-22 10:00 | 6.4701 | 6.8104 | 349.2965 | 1834.0105 | 27510.1577
2020-03-22 11:00 | 7.1123 | 7.4863 | 358.3586 | 2441.274 | 36619.1093
2020-03-22 12:00 | 8.0624 | 8.4864 | 18.8643 | 3530.677 | 52960.1555
2020-03-22 13:00 | 8.6643 | 9.12 | 34.8705 | 4238.3979 | 63575.9686
2020-03-22 14:00 | 8.501 | 8.9481 | 41.8475 | 4051.4451 | 60771.677
2020-03-22 15:00 | 7.5493 | 7.9463 | 42.6396 | 2926.2077 | 43893.1149
2020-03-22 16:00 | 8.1226 | 8.5498 | 41.792 | 3602.1759 | 54032.6384
2020-03-22 17:00 | 8.1149 | 8.5417 | 45.1159 | 3593.0145 | 53895.2176
2020-03-22 18:00 | 8.1274 | 8.5549 | 46.2287 | 3607.8964 | 54118.4456
2020-03-22 19:00 | 7.9015 | 8.3171 | 44.2574 | 3340.0085 | 50100.1271
2020-03-22 20:00 | 7.5983 | 7.9979 | 40.8574 | 2980.7735 | 44711.6027
2020-03-22 21:00 | 7.3477 | 7.7341 | 37.4379 | 2701.6927 | 40525.3907
2020-03-22 22:00 | 6.54 | 6.8839 | 47.7981 | 1893.746 | 28406.1901
2020-03-22 23:00 | 6.6788 | 7.0301 | 50.5582 | 2016.019 | 30240.2843
2020-03-23 00:00 | 6.7488 | 7.1038 | 50.1298 | 2084.703 | 31270.5452
2020-03-23 01:00 | 7.0015 | 7.3697 | 48.4031 | 2332.5662 | 34988.4924
2020-03-23 02:00 | 7.5277 | 7.9236 | 47.1049 | 2902.1407 | 43532.1101
2020-03-23 03:00 | 7.4386 | 7.8298 | 47.934 | 2802.9378 | 42044.0674
2020-03-23 04:00 | 7.2936 | 7.6772 | 48.1749 | 2641.5041 | 39622.5619
2020-03-23 05:00 | 7.122 | 7.4966 | 45.8862 | 2450.8273 | 36762.4088
2020-03-23 06:00 | 7.0665 | 7.4382 | 48.7518 | 2396.3756 | 35945.6335
2020-03-23 07:00 | 6.8207 | 7.1794 | 51.1583 | 2155.226 | 32328.3896
2020-03-23 08:00 | 7.3324 | 7.718 | 51.6143 | 2684.6845 | 40270.2672
2020-03-23 09:00 | 8.6263 | 9.08 | 54.8899 | 4195.5595 | 62933.3931
2020-03-23 10:00 | 6.4282 | 6.7663 | 47.2529 | 1798.233 | 26973.4944
2020-03-23 11:00 | 7.087 | 7.4597 | 37.5153 | 2416.4736 | 36247.1036
2020-03-23 12:00 | 7.9051 | 8.3208 | 33.4116 | 3344.2399 | 50163.5989
2020-03-23 13:00 | 8.5936 | 9.0456 | 32.617 | 4158.7538 | 62381.3068
2020-03-23 14:00 | 9.0425 | 9.5181 | 35.8267 | 4659.9089 | 69898.6342
2020-03-23 15:00 | 8.5204 | 8.9686 | 43.7092 | 4074.5311 | 61117.9663
2020-03-23 16:00 | 8.0567 | 8.4804 | 51.4224 | 3523.9209 | 52858.813
2020-03-23 17:00 | 7.6661 | 8.0693 | 56.2656 | 3060.99 | 45914.8495
2020-03-23 18:00 | 6.9817 | 7.3489 | 58.9925 | 2313.2005 | 34698.007
2020-03-23 19:00 | 6.1447 | 6.4679 | 59.3764 | 1559.508 | 23392.6207
2020-03-23 20:00 | 5.5531 | 5.8451 | 54.3294 | 1140.3152 | 17104.7279
2020-03-23 21:00 | 5.3744 | 5.6571 | 44.8286 | 1028.9999 | 15434.9981
2020-03-23 22:00 | 4.7824 | 5.0339 | 39.336 | 702.0152 | 10530.2285
2020-03-23 23:00 | 4.9016 | 5.1594 | 30.1079 | 764.9955 | 11474.9321
2020-03-24 00:00 | 5.1129 | 5.3818 | 21.3005 | 876.677 | 13150.155
2020-03-24 01:00 | 5.6473 | 5.9443 | 18.0193 | 1199.0068 | 17985.1022
2020-03-24 02:00 | 6.0038 | 6.3195 | 19.5763 | 1455.6837 | 21835.2562
2020-03-24 03:00 | 6.24 | 6.5682 | 21.0751 | 1637.3384 | 24560.0766
2020-03-24 04:00 | 6.3193 | 6.6517 | 24.4065 | 1705.185 | 25577.7753
2020-03-24 05:00 | 6.4384 | 6.777 | 26.9308 | 1806.9042 | 27103.5633
2020-03-24 06:00 | 5.4722 | 5.76 | 30.7693 | 1089.9274 | 16348.9105
2020-03-24 07:00 | 5.9909 | 6.306 | 38.2357 | 1446.2163 | 21693.2448
2020-03-24 08:00 | 7.4695 | 7.8623 | 48.217 | 2837.3535 | 42560.3024
2020-03-24 09:00 | 6.7451 | 7.0999 | 47.0296 | 2081.1026 | 31216.5392
2020-03-24 10:00 | 4.8575 | 5.113 | 36.9389 | 741.7386 | 11126.079
2020-03-24 11:00 | 5.1879 | 5.4608 | 33.6483 | 916.3032 | 13744.548
2020-03-24 12:00 | 5.7663 | 6.0696 | 30.5411 | 1280.7398 | 19211.0971
2020-03-24 13:00 | 6.2625 | 6.5918 | 29.8292 | 1656.5646 | 24848.4697
2020-03-24 14:00 | 6.539 | 6.883 | 31.1296 | 1892.968 | 28394.5201
2020-03-24 15:00 | 6.7209 | 7.0744 | 33.6514 | 2057.3709 | 30860.5636
2020-03-24 16:00 | 6.4357 | 6.7741 | 39.2296 | 1804.5953 | 27068.9298
2020-03-24 17:00 | 6.6351 | 6.9841 | 44.6662 | 1975.0999 | 29626.4983
2020-03-24 18:00 | 6.391 | 6.7271 | 49.2523 | 1766.4175 | 26496.2626
2020-03-24 19:00 | 6.0681 | 6.3872 | 52.652 | 1503.0593 | 22545.8898
2020-03-24 20:00 | 5.8333 | 6.1401 | 55.0225 | 1330.0472 | 19950.7079
2020-03-24 21:00 | 5.4841 | 5.7726 | 57.2607 | 1097.3553 | 16460.3293
2020-03-24 22:00 | 3.8591 | 4.0621 | 52.5139 | 319.8459 | 4797.6886
2020-03-24 23:00 | 4.1196 | 4.3363 | 42.002 | 416.3634 | 6245.451
2020-03-25 00:00 | 4.6669 | 4.9124 | 29.5302 | 648.0143 | 9720.214
2020-03-25 01:00 | 5.4755 | 5.7635 | 25.871 | 1091.9639 | 16379.4592
2020-03-25 02:00 | 5.6618 | 5.9596 | 28.6979 | 1208.0713 | 18121.0692
2020-03-25 03:00 | 5.6164 | 5.9118 | 32.8064 | 1179.7667 | 17696.4998
2020-03-25 04:00 | 5.6546 | 5.952 | 37.6373 | 1203.5921 | 18053.8818
2020-03-25 05:00 | 5.7886 | 6.093 | 42.2669 | 1297.1012 | 19456.5182
2020-03-25 06:00 | 4.8792 | 5.1358 | 47.3352 | 753.1816 | 11297.7239
2020-03-25 07:00 | 4.977 | 5.2388 | 54.1988 | 804.8614 | 12072.9212
2020-03-25 08:00 | 5.8475 | 6.155 | 66.0127 | 1340.5086 | 20107.6296
2020-03-25 09:00 | 5.8617 | 6.17 | 74.5246 | 1350.9843 | 20264.7652
2020-03-25 10:00 | 4.2751 | 4.5 | 67.8929 | 473.9929 | 7109.894
2020-03-25 11:00 | 4.5627 | 4.8027 | 61.8405 | 601.7203 | 9025.805
2020-03-25 12:00 | 4.9419 | 5.2018 | 58.5604 | 786.3151 | 11794.7269
2020-03-25 13:00 | 5.4433 | 5.7296 | 59.1656 | 1071.896 | 16078.4398
2020-03-25 14:00 | 5.8309 | 6.1376 | 62.3859 | 1328.3164 | 19924.7467
2020-03-25 15:00 | 5.6654 | 5.9634 | 65.0472 | 1210.3156 | 18154.7338
2020-03-25 16:00 | 6.0005 | 6.3161 | 68.8714 | 1453.2524 | 21798.7861
2020-03-25 17:00 | 6.5251 | 6.8683 | 73.1095 | 1881.0508 | 28215.7622
2020-03-25 18:00 | 6.8252 | 7.1842 | 75.0196 | 2159.636 | 32394.5397
2020-03-25 19:00 | 6.6043 | 6.9517 | 77.1268 | 1948.7703 | 29231.5542
2020-03-25 20:00 | 5.9313 | 6.2433 | 81.7295 | 1402.2773 | 21034.1588
2020-03-25 21:00 | 5.4933 | 5.7823 | 87.132 | 1103.1017 | 16546.5254
2020-03-25 22:00 | 4.8773 | 5.1338 | 87.8219 | 752.1872 | 11282.8073
2020-03-25 23:00 | 4.93 | 5.1893 | 88.6395 | 780.0049 | 11700.074
2020-03-26 00:00 | 4.8541 | 5.1094 | 88.4916 | 739.9261 | 11098.8922
2020-03-26 01:00 | 4.8012 | 5.0537 | 87.9749 | 711.9425 | 10679.1375
2020-03-26 02:00 | 4.939 | 5.1988 | 87.9928 | 784.7823 | 11771.7339
2020-03-26 03:00 | 5.293 | 5.5714 | 83.9929 | 978.2754 | 14674.1304
2020-03-26 04:00 | 5.7222 | 6.0231 | 80.8809 | 1248.1942 | 18722.9137
2020-03-26 05:00 | 5.8728 | 6.1817 | 77.8156 | 1359.2006 | 20388.0087
2020-03-26 06:00 | 5.3548 | 5.6364 | 78.7027 | 1016.7745 | 15251.6173
2020-03-26 07:00 | 4.6394 | 4.8834 | 81.3986 | 635.791 | 9536.8643
2020-03-26 08:00 | 5.3539 | 5.6355 | 84.9413 | 1016.2225 | 15243.3369
2020-03-26 09:00 | 5.9083 | 6.219 | 89.0457 | 1385.3241 | 20779.8621
2020-03-26 10:00 | 4.6745 | 4.9204 | 80.49 | 651.3907 | 9770.8598
2020-03-26 11:00 | 4.8599 | 5.1155 | 75.7911 | 742.986 | 11144.7901
2020-03-26 12:00 | 5.3211 | 5.6009 | 72.4145 | 995.7609 | 14936.4128
2020-03-26 13:00 | 5.6067 | 5.9016 | 70.8975 | 1173.7529 | 17606.2937
2020-03-26 14:00 | 5.56 | 5.8524 | 70.2898 | 1144.6427 | 17169.6411
2020-03-26 15:00 | 5.568 | 5.8608 | 65.7162 | 1149.615 | 17244.225
2020-03-26 16:00 | 6.6015 | 6.9487 | 63.7172 | 1946.338 | 29195.0705
2020-03-26 17:00 | 7.3327 | 7.7184 | 66.6487 | 2685.0205 | 40275.3076
2020-03-26 18:00 | 7.2144 | 7.5938 | 69.8774 | 2553.2409 | 38298.614
2020-03-26 19:00 | 6.984 | 7.3513 | 72.7487 | 2315.4194 | 34731.291
2020-03-26 20:00 | 7.0627 | 7.4341 | 75.6017 | 2392.6076 | 35889.114
2020-03-26 21:00 | 7.221 | 7.6008 | 77.6384 | 2560.5967 | 38408.9503
2020-03-26 22:00 | 7.1228 | 7.4974 | 79.3799 | 2451.5674 | 36773.5106
2020-03-26 23:00 | 6.7521 | 7.1072 | 82.8841 | 2087.9434 | 31319.1506
2020-03-27 00:00 | 6.2292 | 6.5568 | 82.3627 | 1628.1201 | 24421.8015
2020-03-27 01:00 | 6.0971 | 6.4178 | 78.5555 | 1524.4439 | 22866.6589
2020-03-27 02:00 | 6.1636 | 6.4878 | 74.7869 | 1573.4613 | 23601.9196
2020-03-27 03:00 | 6.2396 | 6.5678 | 73.5982 | 1637.0637 | 24555.9549
2020-03-27 04:00 | 6.2044 | 6.5307 | 75.185 | 1606.9381 | 24104.0718
2020-03-27 05:00 | 5.8361 | 6.1431 | 75.823 | 1332.1452 | 19982.1775
2020-03-27 06:00 | 4.9884 | 5.2508 | 73.1773 | 810.8985 | 12163.4782
2020-03-27 07:00 | 3.8465 | 4.0488 | 67.5675 | 315.1923 | 4727.8845
2020-03-27 08:00 | 4.102 | 4.3178 | 65.1578 | 409.8546 | 6147.8193
2020-03-27 09:00 | 4.7347 | 4.9837 | 64.9123 | 678.1289 | 10171.9334
2020-03-27 10:00 | 4.4888 | 4.7249 | 66.7073 | 568.8978 | 8533.4677
2020-03-27 11:00 | 5.0981 | 5.3663 | 65.1134 | 868.8628 | 13032.9427
2020-03-27 12:00 | 5.6044 | 5.8991 | 67.503 | 1172.2731 | 17584.0963
2020-03-27 13:00 | 6.1323 | 6.4548 | 67.7817 | 1550.3505 | 23255.2576
2020-03-27 14:00 | 6.2692 | 6.5989 | 68.9723 | 1662.3404 | 24935.1065
2020-03-27 15:00 | 6.0805 | 6.4003 | 69.393 | 1512.201 | 22683.015
2020-03-27 16:00 | 6.1012 | 6.4221 | 66.2163 | 1527.4902 | 22912.3523
2020-03-27 17:00 | 6.6195 | 6.9676 | 64.8382 | 1961.7018 | 29425.5273
2020-03-27 18:00 | 6.8143 | 7.1727 | 68.3206 | 2148.9825 | 32234.7382
2020-03-27 19:00 | 6.7126 | 7.0657 | 72.8489 | 2049.2141 | 30738.2122
2020-03-27 20:00 | 6.3949 | 6.7312 | 74.4157 | 1769.7296 | 26545.9447
2020-03-27 21:00 | 6.1387 | 6.4615 | 75.91 | 1555.0781 | 23326.1719
2020-03-27 22:00 | 5.8057 | 6.111 | 71.3892 | 1309.7298 | 19645.9464
2020-03-27 23:00 | 5.6957 | 5.9953 | 68.0935 | 1229.2075 | 18438.1119
2020-03-28 00:00 | 5.8361 | 6.143 | 66.2265 | 1332.106 | 19981.5899
2020-03-28 01:00 | 5.9455 | 6.2582 | 65.8072 | 1412.7737 | 21191.6062
2020-03-28 02:00 | 6.0114 | 6.3276 | 66.4019 | 1461.3051 | 21919.576
2020-03-28 03:00 | 6.0846 | 6.4047 | 64.1042 | 1515.2602 | 22728.9024
2020-03-28 04:00 | 6.1448 | 6.468 | 63.7672 | 1559.5985 | 23393.9781
2020-03-28 05:00 | 6.1666 | 6.491 | 65.6692 | 1575.6773 | 23635.1588
2020-03-28 06:00 | 5.4154 | 5.7003 | 69.5375 | 1054.554 | 15818.3103
2020-03-28 07:00 | 4.3497 | 4.5785 | 71.1075 | 507.1141 | 7606.7117
2020-03-28 08:00 | 3.965 | 4.1736 | 76.0629 | 359.0943 | 5386.4143
2020-03-28 09:00 | 3.8216 | 4.0226 | 74.8961 | 305.945 | 4589.1748
2020-03-28 10:00 | 3.218 | 3.3872 | 74.6781 | 130.8682 | 1963.023
2020-03-28 11:00 | 3.5271 | 3.7126 | 68.005 | 215.8109 | 3237.163
2020-03-28 12:00 | 3.8864 | 4.0908 | 73.4 | 329.9695 | 4949.5426
2020-03-28 13:00 | 3.8476 | 4.0499 | 77.9129 | 315.5807 | 4733.7103
2020-03-28 14:00 | 3.894 | 4.0988 | 77.8388 | 332.7657 | 4991.4858
2020-03-28 15:00 | 3.9921 | 4.2021 | 69.3151 | 369.1261 | 5536.8912
2020-03-28 16:00 | 4.8667 | 5.1227 | 64.5688 | 746.5767 | 11198.6501
2020-03-28 17:00 | 5.5128 | 5.8027 | 67.7013 | 1115.2012 | 16728.0181
2020-03-28 18:00 | 5.3965 | 5.6803 | 72.6522 | 1042.7364 | 15641.0466
2020-03-28 19:00 | 4.5494 | 4.7887 | 79.003 | 595.8161 | 8937.2408
2020-03-28 20:00 | 3.5896 | 3.7784 | 86.1297 | 234.632 | 3519.4801
2020-03-28 21:00 | 2.6545 | 2.7941 | 94.9329 | 0 | 0
2020-03-28 22:00 | 1.6181 | 1.7032 | 62.5218 | 0 | 0
2020-03-28 23:00 | 1.2702 | 1.337 | 21.3297 | 0 | 0
2020-03-29 00:00 | 1.8124 | 1.9077 | 354.9215 | 0 | 0
2020-03-29 01:00 | 2.8785 | 3.0299 | 341.7247 | 54.3964 | 815.9467
2020-03-29 02:00 | 3.6893 | 3.8834 | 335.0434 | 264.6388 | 3969.5819
2020-03-29 03:00 | 4.1219 | 4.3387 | 331.7794 | 417.2181 | 6258.272
2020-03-29 04:00 | 4.1665 | 4.3856 | 332.5797 | 433.7281 | 6505.9211
2020-03-29 05:00 | 4.1862 | 4.4064 | 332.2936 | 441.0443 | 6615.6645
2020-03-29 06:00 | 3.7516 | 3.9489 | 327.9106 | 283.3914 | 4250.8707
2020-03-29 07:00 | 2.5098 | 2.6418 | 317.2122 | 0 | 0
2020-03-29 08:00 | 2.4955 | 2.6268 | 318.1442 | 0 | 0
2020-03-29 09:00 | 2.4977 | 2.6291 | 317.4654 | 0 | 0
2020-03-29 10:00 | 2.2151 | 2.3316 | 309.9958 | 0 | 0
2020-03-29 11:00 | 2.6178 | 2.7555 | 302.0672 | 0 | 0
2020-03-29 12:00 | 3.4052 | 3.5843 | 300.1792 | 179.103 | 2686.5457
2020-03-29 13:00 | 4.2122 | 4.4338 | 306.9222 | 450.6873 | 6760.3097
2020-03-29 14:00 | 4.4919 | 4.7281 | 316.034 | 570.2743 | 8554.114
2020-03-29 15:00 | 4.6149 | 4.8577 | 315.6821 | 624.9373 | 9374.0595
2020-03-29 16:00 | 5.4099 | 5.6944 | 313.6718 | 1051.0961 | 15766.4416
2020-03-29 17:00 | 6.4429 | 6.7818 | 317.5312 | 1810.7945 | 27161.9168
2020-03-29 18:00 | 7.3211 | 7.7061 | 324.1358 | 2672.1055 | 40081.5827
2020-03-29 19:00 | 7.6823 | 8.0864 | 330.3844 | 3080.2384 | 46203.5764
2020-03-29 20:00 | 7.3709 | 7.7586 | 334.0765 | 2727.5612 | 40913.4186
2020-03-29 21:00 | 6.8794 | 7.2412 | 331.3838 | 2212.7786 | 33191.6791
2020-03-29 22:00 | 6.883 | 7.2451 | 331.2491 | 2216.3935 | 33245.9024
2020-03-29 23:00 | 7.5629 | 7.9607 | 325.7385 | 2941.4358 | 44121.5377
2020-03-30 00:00 | 7.8669 | 8.2807 | 328.7365 | 3299.0209 | 49485.3128
2020-03-30 01:00 | 8.0847 | 8.5099 | 332.2099 | 3557.1398 | 53357.0968
2020-03-30 02:00 | 8.4263 | 8.8695 | 333.0376 | 3962.7614 | 59441.421
2020-03-30 03:00 | 8.7322 | 9.1915 | 331.05 | 4314.8626 | 64722.9392
2020-03-30 04:00 | 8.8983 | 9.3663 | 329.8261 | 4501.9176 | 67528.7647
2020-03-30 05:00 | 9.059 | 9.5355 | 326.1966 | 4674.1553 | 70112.33
2020-03-30 06:00 | 8.619 | 9.0723 | 326.9887 | 4187.3272 | 62809.9073
2020-03-30 07:00 | 7.9107 | 8.3267 | 325.1666 | 3350.8815 | 50263.222
2020-03-30 08:00 | 7.8755 | 8.2897 | 319.0262 | 3309.2268 | 49638.4021
2020-03-30 09:00 | 8.2995 | 8.736 | 316.1083 | 3812.1985 | 57182.9771
2020-03-30 10:00 | 8.3445 | 8.7833 | 316.9872 | 3865.6093 | 57984.1388
2020-03-30 11:00 | 8.6317 | 9.0857 | 314.8189 | 4201.6743 | 63025.114
2020-03-30 12:00 | 9.0368 | 9.5121 | 316.5733 | 4654.9353 | 69824.0292
2020-03-30 13:00 | 9.3341 | 9.825 | 320.5334 | 4912.1608 | 73682.4119
2020-03-30 14:00 | 8.9599 | 9.4311 | 323.6987 | 4571.3037 | 68569.5562
2020-03-30 15:00 | 8.4873 | 8.9336 | 325.2538 | 4035.1462 | 60527.1933
2020-03-30 16:00 | 7.8009 | 8.2112 | 325.8597 | 3220.8432 | 48312.6475
2020-03-30 17:00 | 7.5123 | 7.9074 | 323.5466 | 2884.9939 | 43274.909
2020-03-30 18:00 | 7.686 | 8.0903 | 322.0931 | 3084.6345 | 46269.5179
2020-03-30 19:00 | 7.5844 | 7.9833 | 319.9415 | 2965.3792 | 44480.6881
2020-03-30 20:00 | 7.5544 | 7.9517 | 316.9092 | 2931.9026 | 43978.5397
2020-03-30 21:00 | 7.3727 | 7.7605 | 312.3528 | 2729.5635 | 40943.453
2020-03-30 22:00 | 7.779 | 8.1881 | 308.6105 | 3194.8112 | 47922.1674
2020-03-30 23:00 | 8.1092 | 8.5357 | 310.2992 | 3586.2967 | 53794.4511
2020-03-31 00:00 | 8.2096 | 8.6414 | 312.138 | 3705.5257 | 55582.8848
2020-03-31 01:00 | 7.8514 | 8.2643 | 311.9463 | 3280.5924 | 49208.8867
2020-03-31 02:00 | 7.6566 | 8.0593 | 313.1899 | 3049.7527 | 45746.2905
2020-03-31 03:00 | 7.5479 | 7.9449 | 316.7072 | 2924.7035 | 43870.5531
2020-03-31 04:00 | 7.4781 | 7.8714 | 323.4127 | 2846.9867 | 42704.8007
2020-03-31 05:00 | 7.1923 | 7.5706 | 327.4108 | 2528.6727 | 37930.09
2020-03-31 06:00 | 8.3409 | 8.7796 | 339.0303 | 3861.4127 | 57921.1902
2020-03-31 07:00 | 8.8106 | 9.274 | 345.3225 | 4403.2215 | 66048.3221
2020-03-31 08:00 | 9.1377 | 9.6183 | 349.8395 | 4742.2406 | 71133.6088
2020-03-31 09:00 | 8.787 | 9.2492 | 351.7374 | 4376.6366 | 65649.5496
2020-03-31 10:00 | 7.7676 | 8.1761 | 344.1871 | 3181.3068 | 47719.6021
2020-03-31 11:00 | 7.9355 | 8.3529 | 345.0793 | 3380.3796 | 50705.6942
2020-03-31 12:00 | 8.0014 | 8.4222 | 349.7579 | 3458.4164 | 51876.2458
2020-03-31 13:00 | 7.9452 | 8.363 | 352.1702 | 3391.7823 | 50876.7347
2020-03-31 14:00 | 7.8205 | 8.2318 | 352.8557 | 3244.0055 | 48660.0831
2020-03-31 15:00 | 7.0517 | 7.4226 | 349.8147 | 2381.84 | 35727.6004
2020-03-31 16:00 | 6.1957 | 6.5216 | 349.6501 | 1599.5113 | 23992.6692
2020-03-31 17:00 | 5.996 | 6.3113 | 351.2012 | 1449.9231 | 21748.846
2020-03-31 18:00 | 5.0978 | 5.3659 | 355.7534 | 868.6725 | 13030.0873
2020-03-31 19:00 | 3.5782 | 3.7664 | 356.8094 | 231.2006 | 3468.0091
2020-03-31 20:00 | 2.0089 | 2.1145 | 337.2277 | 0 | 0
2020-03-31 21:00 | 2.2009 | 2.3166 | 296.0422 | 0 | 0
2020-03-31 22:00 | 3.594 | 3.783 | 278.6274 | 235.9302 | 3538.9533
2020-03-31 23:00 | 4.7826 | 5.0341 | 262.7969 | 702.1228 | 10531.8413
2020-04-01 00:00 | 5.8779 | 6.187 | 254.6252 | 1362.9081 | 20443.621
2020-04-01 01:00 | 6.7438 | 7.0985 | 254.1537 | 2079.7888 | 31196.8325
2020-04-01 02:00 | 7.1199 | 7.4943 | 258.3347 | 2448.7028 | 36730.5422
2020-04-01 03:00 | 7.2124 | 7.5917 | 261.3188 | 2551.0079 | 38265.1179
2020-04-01 04:00 | 7.3589 | 7.7459 | 264.0294 | 2714.1903 | 40712.8546
2020-04-01 05:00 | 7.4624 | 7.8549 | 266.2073 | 2829.4348 | 42441.5216
2020-04-01 06:00 | 6.5551 | 6.8998 | 269.8385 | 1906.6584 | 28599.8764
2020-04-01 07:00 | 6.723 | 7.0766 | 273.8559 | 2059.3975 | 30890.9626
2020-04-01 08:00 | 9.0202 | 9.4946 | 280.7884 | 4639.2657 | 69588.9855
2020-04-01 09:00 | 9.7683 | 10.2821 | 282.8506 | 5220.7314 | 78310.9717
2020-04-01 10:00 | 9.0614 | 9.5379 | 280.2316 | 4676.1873 | 70142.8089
2020-04-01 11:00 | 9.8015 | 10.317 | 282.4616 | 5241.124 | 78616.8604
2020-04-01 12:00 | 9.5315 | 10.0328 | 282.1311 | 5075.1366 | 76127.0494
2020-04-01 13:00 | 9.0333 | 9.5084 | 282.0162 | 4651.9364 | 69779.0453
2020-04-01 14:00 | 8.7521 | 9.2124 | 282.442 | 4337.2297 | 65058.4451
2020-04-01 15:00 | 7.333 | 7.7186 | 281.1514 | 2685.3084 | 40279.6262
2020-04-01 16:00 | 6.988 | 7.3556 | 278.6689 | 2319.3755 | 34790.633
2020-04-01 17:00 | 7.4288 | 7.8195 | 281.5832 | 2792.0535 | 41880.8025
2020-04-01 18:00 | 7.2703 | 7.6527 | 284.2648 | 2615.5068 | 39232.6022
2020-04-01 19:00 | 6.8923 | 7.2548 | 277.369 | 2225.515 | 33382.7257
2020-04-01 20:00 | 7.0833 | 7.4558 | 267.7716 | 2412.7997 | 36191.9951
2020-04-01 21:00 | 7.3816 | 7.7698 | 261.8796 | 2739.4646 | 41091.9692
2020-04-01 22:00 | 7.86 | 8.2734 | 262.1113 | 3290.8558 | 49362.8367
2020-04-01 23:00 | 7.7413 | 8.1484 | 261.0611 | 3150.1004 | 47251.506
2020-04-02 00:00 | 7.7419 | 8.1491 | 259.0713 | 3150.915 | 47263.7248
2020-04-02 01:00 | 7.7777 | 8.1868 | 255.4573 | 3193.308 | 47899.6204
2020-04-02 02:00 | 7.7369 | 8.1438 | 253.1277 | 3144.9387 | 47174.081
2020-04-02 03:00 | 7.7906 | 8.2003 | 250.6533 | 3208.592 | 48128.8795
2020-04-02 04:00 | 7.7919 | 8.2017 | 249.7946 | 3210.15 | 48152.2495
2020-04-02 05:00 | 7.3347 | 7.7205 | 248.8492 | 2687.2519 | 40308.7783
2020-04-02 06:00 | 6.1506 | 6.4741 | 249.2507 | 1563.8825 | 23458.2379
2020-04-02 07:00 | 6.367 | 6.7018 | 254.0987 | 1745.8918 | 26188.3777
2020-04-02 08:00 | 6.8189 | 7.1776 | 257.6735 | 2153.4894 | 32302.3407
2020-04-02 09:00 | 7.6215 | 8.0223 | 261.1165 | 3008.1298 | 45121.9472
2020-04-02 10:00 | 7.0736 | 7.4456 | 256.2862 | 2403.2857 | 36049.2852
2020-04-02 11:00 | 7.5529 | 7.9501 | 258.0407 | 2930.2282 | 43953.4234
2020-04-02 12:00 | 7.7848 | 8.1943 | 260.6724 | 3201.7706 | 48026.5586
2020-04-02 13:00 | 7.797 | 8.2071 | 263.0536 | 3216.2011 | 48243.0164
2020-04-02 14:00 | 7.4799 | 7.8733 | 264.708 | 2848.9831 | 42734.7461
2020-04-02 15:00 | 6.5624 | 6.9076 | 264.5949 | 1912.9394 | 28694.0916
2020-04-02 16:00 | 5.7758 | 6.0795 | 259.6593 | 1287.6721 | 19315.0816
2020-04-02 17:00 | 5.7991 | 6.1041 | 255.0246 | 1304.8572 | 19572.8575
2020-04-02 18:00 | 5.9194 | 6.2307 | 250.8989 | 1393.5191 | 20902.7858
2020-04-02 19:00 | 6.2908 | 6.6217 | 243.4729 | 1680.7887 | 25211.8311
2020-04-02 20:00 | 6.8127 | 7.1711 | 237.506 | 2147.431 | 32211.4657
2020-04-02 21:00 | 7.0132 | 7.382 | 232.4306 | 2344.0434 | 35160.6505
2020-04-02 22:00 | 7.2213 | 7.6011 | 227.482 | 2561.0144 | 38415.2156
2020-04-02 23:00 | 7.3752 | 7.7631 | 228.5859 | 2732.3638 | 40985.4567
2020-04-03 00:00 | 7.4814 | 7.8749 | 228.0819 | 2850.6663 | 42759.9945
2020-04-03 01:00 | 7.5607 | 7.9584 | 226.0991 | 2938.9832 | 44084.7479
2020-04-03 02:00 | 7.6397 | 8.0415 | 225.2629 | 3029.7694 | 45446.541
2020-04-03 03:00 | 7.6357 | 8.0373 | 225.725 | 3024.9636 | 45374.4533
2020-04-03 04:00 | 7.6027 | 8.0025 | 223.3662 | 2985.8555 | 44787.832
2020-04-03 05:00 | 7.1276 | 7.5025 | 219.7958 | 2456.6363 | 36849.545
2020-04-03 06:00 | 5.9955 | 6.3108 | 218.5023 | 1449.5748 | 21743.6213
2020-04-03 07:00 | 5.457 | 5.744 | 221.0753 | 1080.4394 | 16206.5916
2020-04-03 08:00 | 5.6638 | 5.9617 | 222.405 | 1209.3417 | 18140.1261
2020-04-03 09:00 | 6.3194 | 6.6518 | 225.1948 | 1705.238 | 25578.5698
2020-04-03 10:00 | 5.8257 | 6.1321 | 218.9071 | 1324.4952 | 19867.4284
2020-04-03 11:00 | 6.6788 | 7.0301 | 224.9813 | 2016.0471 | 30240.7065
2020-04-03 12:00 | 7.1679 | 7.5449 | 233.0997 | 2501.5029 | 37522.5434
2020-04-03 13:00 | 7.3866 | 7.7751 | 242.3504 | 2745.0414 | 41175.6211
2020-04-03 14:00 | 7.5305 | 7.9266 | 250.1725 | 2905.3382 | 43580.0732
2020-04-03 15:00 | 6.8844 | 7.2465 | 253.3893 | 2217.751 | 33266.2649
2020-04-03 16:00 | 6.4986 | 6.8404 | 248.7713 | 1858.3654 | 27875.4813
2020-04-03 17:00 | 6.7572 | 7.1126 | 250.3616 | 2092.985 | 31394.7753
2020-04-03 18:00 | 6.8372 | 7.1968 | 267.7397 | 2171.4455 | 32571.682
2020-04-03 19:00 | 7.0561 | 7.4272 | 292.8694 | 2386.1863 | 35792.794
2020-04-03 20:00 | 6.7472 | 7.1021 | 307.0192 | 2083.1409 | 31247.1133
2020-04-03 21:00 | 6.3364 | 6.6697 | 308.8341 | 1719.7992 | 25796.9884
2020-04-03 22:00 | 6.7439 | 7.0986 | 305.6865 | 2079.8561 | 31197.8409
2020-04-03 23:00 | 6.515 | 6.8577 | 298.5193 | 1872.4267 | 28086.4002
2020-04-04 00:00 | 6.6822 | 7.0337 | 293.5788 | 2019.3963 | 30290.9451
2020-04-04 01:00 | 6.9037 | 7.2668 | 293.2898 | 2236.6952 | 33550.4287
2020-04-04 02:00 | 6.9074 | 7.2707 | 293.7423 | 2240.2542 | 33603.8133
2020-04-04 03:00 | 7.007 | 7.3755 | 296.3546 | 2338.0109 | 35070.1637
2020-04-04 04:00 | 6.99 | 7.3576 | 301.9828 | 2321.3016 | 34819.524
2020-04-04 05:00 | 6.425 | 6.7629 | 307.9757 | 1795.5124 | 26932.6863
2020-04-04 06:00 | 4.751 | 5.0009 | 311.9316 | 685.4606 | 10281.909
2020-04-04 07:00 | 4.2997 | 4.5259 | 317.1012 | 484.9269 | 7273.9028
2020-04-04 08:00 | 5.3611 | 5.6431 | 314.1051 | 1020.7192 | 15310.7876
2020-04-04 09:00 | 5.3956 | 5.6793 | 310.1063 | 1042.169 | 15632.5348
2020-04-04 10:00 | 5.0901 | 5.3578 | 301.9744 | 864.624 | 12969.3603
2020-04-04 11:00 | 5.5684 | 5.8613 | 300.0655 | 1149.8776 | 17248.1647
2020-04-04 12:00 | 6.4595 | 6.7993 | 300.2379 | 1825.0021 | 27375.0322
2020-04-04 13:00 | 6.8967 | 7.2595 | 299.7143 | 2229.8252 | 33447.3786
2020-04-04 14:00 | 7.3137 | 7.6983 | 303.1773 | 2663.843 | 39957.6453
2020-04-04 15:00 | 7.1376 | 7.513 | 314.8878 | 2467.7644 | 37016.4665
2020-04-04 16:00 | 6.7212 | 7.0747 | 325.0038 | 2057.6665 | 30864.9982
2020-04-04 17:00 | 6.5065 | 6.8487 | 332.3413 | 1865.1439 | 27977.1586
2020-04-04 18:00 | 6.4629 | 6.8028 | 338.5638 | 1827.8937 | 27418.4055
2020-04-04 19:00 | 6.1518 | 6.4754 | 346.3693 | 1564.7662 | 23471.4935
2020-04-04 20:00 | 5.7583 | 6.0611 | 354.0675 | 1274.7878 | 19121.8168
2020-04-04 21:00 | 4.971 | 5.2325 | 358.1713 | 801.7087 | 12025.6307
2020-04-04 22:00 | 4.2514 | 4.475 | 355.1932 | 465.1899 | 6977.8483
2020-04-04 23:00 | 3.9907 | 4.2005 | 345.1067 | 368.5927 | 5528.8903
2020-04-05 00:00 | 4.276 | 4.5009 | 334.6631 | 474.3875 | 7115.8126
2020-04-05 01:00 | 4.7706 | 5.0215 | 331.3699 | 695.8121 | 10437.1808
2020-04-05 02:00 | 5.1178 | 5.387 | 331.8518 | 879.2718 | 13189.0776
2020-04-05 03:00 | 5.2931 | 5.5714 | 332.5242 | 978.2936 | 14674.4037
2020-04-05 04:00 | 5.396 | 5.6798 | 335.495 | 1042.422 | 15636.3293
2020-04-05 05:00 | 5.1667 | 5.4384 | 338.3899 | 905.0721 | 13576.0813
2020-04-05 06:00 | 3.7776 | 3.9763 | 336.1172 | 291.2223 | 4368.3348
2020-04-05 07:00 | 3.4677 | 3.65 | 337.3993 | 197.909 | 2968.6346
2020-04-05 08:00 | 4.7234 | 4.9718 | 336.2717 | 673.0927 | 10096.3907
2020-04-05 09:00 | 6.5622 | 6.9073 | 338.3905 | 1912.7189 | 28690.7842
2020-04-05 10:00 | 6.9706 | 7.3372 | 323.2137 | 2302.313 | 34534.6952
2020-04-05 11:00 | 7.528 | 7.924 | 332.292 | 2902.552 | 43538.2793
2020-04-05 12:00 | 7.5864 | 7.9854 | 339.9747 | 2967.5308 | 44512.9618
2020-04-05 13:00 | 7.5034 | 7.898 | 347.3809 | 2875.1188 | 43126.7826
2020-04-05 14:00 | 7.1287 | 7.5036 | 354.481 | 2457.8455 | 36867.6828
2020-04-05 15:00 | 6.5992 | 6.9463 | 0.37519 | 1944.3956 | 29165.9347
2020-04-05 16:00 | 5.8277 | 6.1342 | 3.9322 | 1325.9547 | 19889.3202
2020-04-05 17:00 | 6.2289 | 6.5565 | 5.3598 | 1627.9183 | 24418.7746
2020-04-05 18:00 | 6.4626 | 6.8025 | 10.185 | 1827.6167 | 27414.25
2020-04-05 19:00 | 6.2588 | 6.588 | 15.284 | 1653.4487 | 24801.7308
2020-04-05 20:00 | 6.2137 | 6.5405 | 21.4504 | 1614.896 | 24223.4406
2020-04-05 21:00 | 5.8929 | 6.2029 | 25.3462 | 1374.0116 | 20610.1746
2020-04-05 22:00 | 5.7424 | 6.0445 | 30.5379 | 1263.1236 | 18946.8546
2020-04-05 23:00 | 5.1321 | 5.4021 | 36.6162 | 886.8386 | 13302.579
2020-04-06 00:00 | 4.6342 | 4.878 | 44.5885 | 633.5055 | 9502.5819
2020-04-06 01:00 | 4.186 | 4.4062 | 56.9845 | 440.9802 | 6614.7033
2020-04-06 02:00 | 3.5069 | 3.6913 | 72.2464 | 209.7198 | 3145.7965
2020-04-06 03:00 | 2.7462 | 2.8906 | 91.6761 | 0 | 0
2020-04-06 04:00 | 2.1059 | 2.2167 | 128.8046 | 0 | 0
2020-04-06 05:00 | 2.1587 | 2.2722 | 167.2941 | 0 | 0
2020-04-06 06:00 | 2.3906 | 2.5163 | 194.4829 | 0 | 0
2020-04-06 07:00 | 2.1451 | 2.2579 | 199.4014 | 0 | 0
2020-04-06 08:00 | 2.1137 | 2.2248 | 216.6187 | 0 | 0
2020-04-06 09:00 | 2.0645 | 2.1731 | 239.6022 | 0 | 0
2020-04-06 10:00 | 3.17 | 3.3367 | 261.2842 | 120.0624 | 1800.9354
2020-04-06 11:00 | 3.0672 | 3.2285 | 272.625 | 96.8957 | 1453.4354
2020-04-06 12:00 | 2.9349 | 3.0893 | 280.6456 | 67.1045 | 1006.5681
2020-04-06 13:00 | 2.6779 | 2.8187 | 289.2772 | 0 | 0
2020-04-06 14:00 | 2.2518 | 2.3702 | 296.8833 | 0 | 0
2020-04-06 15:00 | 1.6709 | 1.7588 | 310.3948 | 0 | 0
2020-04-06 16:00 | 0.96428 | 1.015 | 350.9348 | 0 | 0
2020-04-06 17:00 | 0.85714 | 0.90222 | 71.7473 | 0 | 0
2020-04-06 18:00 | 1.5502 | 1.6317 | 116.1181 | 0 | 0
2020-04-06 19:00 | 2.5049 | 2.6367 | 140.252 | 0 | 0
2020-04-06 20:00 | 3.4773 | 3.6602 | 153.2727 | 200.8079 | 3012.1183
2020-04-06 21:00 | 4.3699 | 4.5998 | 161.7147 | 516.1084 | 7741.6256
2020-04-06 22:00 | 4.9752 | 5.2368 | 160.8429 | 803.8861 | 12058.2919
2020-04-06 23:00 | 5.123 | 5.3924 | 171.5484 | 881.9828 | 13229.7413
2020-04-07 00:00 | 4.9488 | 5.209 | 181.0936 | 789.9383 | 11849.074
2020-04-07 01:00 | 4.6718 | 4.9175 | 191.3057 | 650.1841 | 9752.7617
2020-04-07 02:00 | 4.1707 | 4.3901 | 201.4545 | 435.3151 | 6529.7264
2020-04-07 03:00 | 3.5043 | 3.6886 | 210.9594 | 208.9318 | 3133.9763
2020-04-07 04:00 | 2.6822 | 2.8232 | 215.2094 | 0 | 0
2020-04-07 05:00 | 2.2062 | 2.3223 | 202.8403 | 0 | 0
2020-04-07 06:00 | 2.4279 | 2.5556 | 183.1614 | 0 | 0
2020-04-07 07:00 | 2.1259 | 2.2377 | 163.9422 | 0 | 0
2020-04-07 08:00 | 2.7355 | 2.8794 | 165.4536 | 0 | 0
2020-04-07 09:00 | 3.135 | 3.2999 | 177.5483 | 112.1776 | 1682.6645
2020-04-07 10:00 | 3.2684 | 3.4403 | 206.2605 | 142.2209 | 2133.3128
2020-04-07 11:00 | 3.1493 | 3.3149 | 212.1018 | 115.3955 | 1730.9319
2020-04-07 12:00 | 3.0457 | 3.2059 | 219.6844 | 92.064 | 1380.9598
2020-04-07 13:00 | 2.8864 | 3.0382 | 227.1935 | 56.1816 | 842.7234
2020-04-07 14:00 | 2.8156 | 2.9637 | 232.2017 | 0 | 0
2020-04-07 15:00 | 2.8235 | 2.972 | 229.5183 | 0 | 0
2020-04-07 16:00 | 3.1956 | 3.3637 | 214.9668 | 125.8211 | 1887.3168
2020-04-07 17:00 | 4.3353 | 4.5633 | 209.0456 | 500.7202 | 7510.8029
2020-04-07 18:00 | 5.6359 | 5.9323 | 208.8298 | 1191.9096 | 17878.644
2020-04-07 19:00 | 6.6314 | 6.9801 | 212.7409 | 1971.8735 | 29578.1026
2020-04-07 20:00 | 7.4108 | 7.8005 | 219.1223 | 2771.9512 | 41579.2673
2020-04-07 21:00 | 8.0855 | 8.5108 | 222.1656 | 3558.1462 | 53372.1932
2020-04-07 22:00 | 8.4815 | 8.9276 | 225.1405 | 4028.3095 | 60424.6419
2020-04-07 23:00 | 8.7726 | 9.234 | 231.7078 | 4360.3883 | 65405.8243
2020-04-08 00:00 | 9.1725 | 9.6549 | 235.7967 | 4772.3389 | 71585.0841
2020-04-08 01:00 | 9.4425 | 9.9391 | 238.3461 | 5005.9212 | 75088.818
2020-04-08 02:00 | 9.3297 | 9.8204 | 243.9629 | 4908.334 | 73625.0102
2020-04-08 03:00 | 9.3279 | 9.8185 | 248.0498 | 4906.8083 | 73602.1242
2020-04-08 04:00 | 9.2432 | 9.7293 | 252.1836 | 4833.4774 | 72502.1617
2020-04-08 05:00 | 8.5886 | 9.0403 | 257.3366 | 4153.122 | 62296.8306
2020-04-08 06:00 | 7.2437 | 7.6246 | 265.3885 | 2585.8714 | 38788.0705
2020-04-08 07:00 | 6.4452 | 6.7841 | 279.7808 | 1812.715 | 27190.7247
2020-04-08 08:00 | 6.2451 | 6.5735 | 292.1401 | 1641.7038 | 24625.5566
2020-04-08 09:00 | 6.3507 | 6.6847 | 299.4905 | 1731.9957 | 25979.9352
2020-04-08 10:00 | 6.9208 | 7.2848 | 295.1807 | 2253.4481 | 33801.7217
2020-04-08 11:00 | 7.9642 | 8.3831 | 301.5486 | 3414.3781 | 51215.6719
2020-04-08 12:00 | 8.9024 | 9.3706 | 309.2929 | 4506.5054 | 67597.5813
2020-04-08 13:00 | 8.8672 | 9.3335 | 318.8598 | 4466.8695 | 67003.0422
2020-04-08 14:00 | 8.3182 | 8.7557 | 329.5602 | 3834.4356 | 57516.5345
2020-04-08 15:00 | 7.4677 | 7.8604 | 341.156 | 2835.3497 | 42530.245
2020-04-08 16:00 | 6.9215 | 7.2855 | 349.9233 | 2254.0839 | 33811.2587
2020-04-08 17:00 | 6.9936 | 7.3615 | 356.2174 | 2324.8774 | 34873.1604
2020-04-08 18:00 | 6.9736 | 7.3403 | 3.8169 | 2305.1967 | 34577.9498
2020-04-08 19:00 | 6.5992 | 6.9463 | 11.2653 | 1944.4001 | 29166.001
2020-04-08 20:00 | 6.0565 | 6.375 | 19.6821 | 1494.5129 | 22417.6942
2020-04-08 21:00 | 5.3155 | 5.595 | 28.4047 | 992.26 | 14883.8994
2020-04-08 22:00 | 5.0863 | 5.3538 | 37.1035 | 862.6137 | 12939.2052
2020-04-08 23:00 | 4.5833 | 4.8243 | 52.0043 | 610.8748 | 9163.1219
2020-04-09 00:00 | 3.9955 | 4.2056 | 72.117 | 370.3857 | 5555.786
2020-04-09 01:00 | 3.7103 | 3.9055 | 94.5917 | 270.9619 | 4064.428
2020-04-09 02:00 | 3.7253 | 3.9212 | 119.2322 | 275.476 | 4132.1396
2020-04-09 03:00 | 3.6945 | 3.8888 | 138.8516 | 266.21 | 3993.1501
2020-04-09 04:00 | 3.7579 | 3.9555 | 157.9331 | 285.2766 | 4279.1492
2020-04-09 05:00 | 4.0958 | 4.3112 | 176.5046 | 407.5314 | 6112.9717
2020-04-09 06:00 | 3.2503 | 3.4213 | 188.653 | 138.1573 | 2072.3589
2020-04-09 07:00 | 3.2973 | 3.4707 | 201.9825 | 148.7319 | 2230.979
2020-04-09 08:00 | 3.2413 | 3.4117 | 226.9683 | 136.1135 | 2041.7028
2020-04-09 09:00 | 3.4934 | 3.6772 | 245.6357 | 205.6654 | 3084.981
2020-04-09 10:00 | 3.9563 | 4.1644 | 243.2245 | 355.8568 | 5337.852
2020-04-09 11:00 | 4.2488 | 4.4722 | 245.8306 | 464.223 | 6963.3454
2020-04-09 12:00 | 4.5005 | 4.7372 | 252.7393 | 574.0792 | 8611.1879
2020-04-09 13:00 | 4.7553 | 5.0054 | 262.1413 | 687.6926 | 10315.3885
2020-04-09 14:00 | 5.0062 | 5.2695 | 268.339 | 820.2688 | 12304.0321
2020-04-09 15:00 | 4.9577 | 5.2184 | 273.4523 | 794.6351 | 11919.5259
2020-04-09 16:00 | 4.1825 | 4.4025 | 268.101 | 439.6731 | 6595.0965
2020-04-09 17:00 | 4.0353 | 4.2475 | 254.723 | 385.1362 | 5777.0426
2020-04-09 18:00 | 4.6118 | 4.8543 | 243.7391 | 623.5192 | 9352.7878
2020-04-09 19:00 | 5.6551 | 5.9525 | 241.9845 | 1203.8816 | 18058.2235
2020-04-09 20:00 | 6.5472 | 6.8916 | 247.6125 | 1899.9436 | 28499.1539
2020-04-09 21:00 | 7.012 | 7.3808 | 254.4823 | 2342.8952 | 35143.4279
2020-04-09 22:00 | 7.1673 | 7.5443 | 267.7999 | 2500.8637 | 37512.9552
2020-04-09 23:00 | 7.5287 | 7.9247 | 273.7158 | 2903.3228 | 43549.8413
2020-04-10 00:00 | 7.8916 | 8.3067 | 290.0955 | 3328.304 | 49924.5607
2020-04-10 01:00 | 7.8536 | 8.2667 | 312.5255 | 3283.2832 | 49249.2477
2020-04-10 02:00 | 7.9569 | 8.3754 | 329.2919 | 3405.6529 | 51084.7934
2020-04-10 03:00 | 8.0154 | 8.4369 | 330.9943 | 3475.0014 | 52125.0206
2020-04-10 04:00 | 8.1562 | 8.5852 | 325.4483 | 3642.1276 | 54631.9137
2020-04-10 05:00 | 8.1581 | 8.5872 | 321.8646 | 3644.3442 | 54665.1625
2020-04-10 06:00 | 8.3008 | 8.7373 | 327.1328 | 3813.716 | 57205.7396
2020-04-10 07:00 | 8.7154 | 9.1738 | 334.4601 | 4295.9941 | 64439.9112
2020-04-10 08:00 | 9.5168 | 10.0173 | 336.3026 | 5066.1032 | 75991.5476
2020-04-10 09:00 | 10.0051 | 10.5314 | 337.7972 | 5359.977 | 80399.6554
2020-04-10 10:00 | 9.4973 | 9.9968 | 329.3031 | 5053.3871 | 75800.807
2020-04-10 11:00 | 9.7943 | 10.3094 | 329.4527 | 5236.7008 | 78550.5119
2020-04-10 12:00 | 10.0686 | 10.5982 | 332.4033 | 5385.508 | 80782.6205
2020-04-10 13:00 | 10.1645 | 10.6991 | 335.8907 | 5424.0422 | 81360.633
2020-04-10 14:00 | 9.6282 | 10.1346 | 339.5205 | 5134.5985 | 77018.9777
2020-04-10 15:00 | 9.409 | 9.9039 | 341.8146 | 4976.9786 | 74654.6788
2020-04-10 16:00 | 8.5941 | 9.0461 | 345.488 | 4159.2864 | 62389.2957
2020-04-10 17:00 | 8.206 | 8.6376 | 349.9812 | 3701.2303 | 55518.4544
2020-04-10 18:00 | 7.8957 | 8.3109 | 355.5971 | 3333.1071 | 49996.6066
2020-04-10 19:00 | 7.1443 | 7.52 | 359.3927 | 2475.1884 | 37127.8261
2020-04-10 20:00 | 5.979 | 6.2934 | 358.0951 | 1437.3883 | 21560.8239
2020-04-10 21:00 | 5.081 | 5.3483 | 349.1435 | 859.8332 | 12897.4979
2020-04-10 22:00 | 5.0681 | 5.3346 | 331.7973 | 852.9752 | 12794.6278
2020-04-10 23:00 | 5.2855 | 5.5635 | 319.2826 | 973.5758 | 14603.6367
2020-04-11 00:00 | 5.4517 | 5.7384 | 311.6812 | 1077.127 | 16156.9055
2020-04-11 01:00 | 5.5593 | 5.8517 | 308.2259 | 1144.2034 | 17163.051
2020-04-11 02:00 | 5.5332 | 5.8243 | 305.9284 | 1127.9624 | 16919.4354
2020-04-11 03:00 | 5.7491 | 6.0515 | 306.7688 | 1268.0344 | 19020.5155
2020-04-11 04:00 | 5.9592 | 6.2726 | 308.1762 | 1422.8306 | 21342.4589
2020-04-11 05:00 | 5.271 | 5.5482 | 305.5368 | 964.535 | 14468.0256
2020-04-11 06:00 | 4.0625 | 4.2762 | 300.9814 | 395.2049 | 5928.0739
2020-04-11 07:00 | 4.8692 | 5.1253 | 305.054 | 747.8843 | 11218.2643
2020-04-11 08:00 | 6.2233 | 6.5506 | 314.4447 | 1623.0585 | 24345.8774
2020-04-11 09:00 | 8.2684 | 8.7033 | 319.9381 | 3775.2969 | 56629.4532
2020-04-11 10:00 | 8.3014 | 8.738 | 314.0338 | 3814.4726 | 57217.0885
2020-04-11 11:00 | 9.0882 | 9.5662 | 314.2229 | 4699.4443 | 70491.6638
2020-04-11 12:00 | 9.6285 | 10.1349 | 317.7945 | 5134.7759 | 77021.639
2020-04-11 13:00 | 10.0097 | 10.5362 | 324.2906 | 5361.8145 | 80427.2181
2020-04-11 14:00 | 9.8577 | 10.3762 | 332.0645 | 5275.6858 | 79135.2872
2020-04-11 15:00 | 9.3746 | 9.8677 | 339.5637 | 4947.2308 | 74208.4621
2020-04-11 16:00 | 8.3522 | 8.7915 | 347.0195 | 3874.7981 | 58121.9719
2020-04-11 17:00 | 7.9813 | 8.4011 | 355.5017 | 3434.6586 | 51519.8789
2020-04-11 18:00 | 7.7892 | 8.1989 | 4.6361 | 3206.9849 | 48104.7739
2020-04-11 19:00 | 7.496 | 7.8902 | 10.9122 | 2866.8803 | 43003.2044
2020-04-11 20:00 | 6.9235 | 7.2876 | 13.3145 | 2256.0746 | 33841.1186
2020-04-11 21:00 | 6.2929 | 6.6239 | 17.414 | 1682.5903 | 25238.8541
2020-04-11 22:00 | 6.2626 | 6.592 | 29.5222 | 1656.7174 | 24850.7612
2020-04-11 23:00 | 5.5717 | 5.8648 | 46.0173 | 1151.9514 | 17279.2713
2020-04-12 00:00 | 4.8812 | 5.1379 | 58.8934 | 754.2291 | 11313.4367
2020-04-12 01:00 | 4.3499 | 4.5787 | 73.0775 | 507.2028 | 7608.0416
2020-04-12 02:00 | 3.818 | 4.0188 | 87.7093 | 304.6226 | 4569.3394
2020-04-12 03:00 | 3.087 | 3.2494 | 109.1577 | 101.3648 | 1520.4713
2020-04-12 04:00 | 2.586 | 2.722 | 142.3288 | 0 | 0
2020-04-12 05:00 | 2.8409 | 2.9904 | 174.0673 | 0 | 0
2020-04-12 06:00 | 2.4964 | 2.6277 | 179.8911 | 0 | 0
2020-04-12 07:00 | 2.0957 | 2.2059 | 178.4191 | 0 | 0
2020-04-12 08:00 | 1.8438 | 1.9408 | 183.3248 | 0 | 0
2020-04-12 09:00 | 2.3205 | 2.4425 | 193.8199 | 0 | 0
2020-04-12 10:00 | 2.9128 | 3.066 | 229.8518 | 62.1198 | 931.7971
2020-04-12 11:00 | 3.0314 | 3.1909 | 228.6798 | 88.842 | 1332.63
2020-04-12 12:00 | 3.0992 | 3.2622 | 224.7662 | 104.1029 | 1561.5439
2020-04-12 13:00 | 2.9816 | 3.1384 | 221.4699 | 77.6234 | 1164.3513
2020-04-12 14:00 | 3.0918 | 3.2544 | 216.5579 | 102.4442 | 1536.6626
2020-04-12 15:00 | 3.325 | 3.4998 | 212.032 | 154.9645 | 2324.4676
2020-04-12 16:00 | 3.4616 | 3.6437 | 201.7288 | 196.0954 | 2941.431
2020-04-12 17:00 | 4.5042 | 4.7411 | 183.0068 | 575.7641 | 8636.4609
2020-04-12 18:00 | 6.2315 | 6.5592 | 176.7411 | 1630.0645 | 24450.9669
2020-04-12 19:00 | 7.5545 | 7.9518 | 174.9446 | 2931.9846 | 43979.7696
2020-04-12 20:00 | 8.2797 | 8.7151 | 176.4105 | 3788.6746 | 56830.1195
2020-04-12 21:00 | 8.6922 | 9.1493 | 179.6485 | 4269.7965 | 64046.9471
2020-04-12 22:00 | 8.5604 | 9.0106 | 181.8904 | 4121.3742 | 61820.6123
2020-04-12 23:00 | 8.7788 | 9.2405 | 185.2982 | 4367.3808 | 65510.7126
2020-04-13 00:00 | 8.7119 | 9.1701 | 188.4056 | 4292.005 | 64380.0747
2020-04-13 01:00 | 8.7585 | 9.2192 | 193.1635 | 4344.5451 | 65168.1771
2020-04-13 02:00 | 8.9218 | 9.391 | 199.5755 | 4528.3924 | 67925.8865
2020-04-13 03:00 | 8.9371 | 9.4072 | 204.5011 | 4545.6942 | 68185.4127
2020-04-13 04:00 | 8.8024 | 9.2653 | 206.6962 | 4393.878 | 65908.1694
2020-04-13 05:00 | 8.6766 | 9.133 | 206.9503 | 4252.2572 | 63783.8579
2020-04-13 06:00 | 7.2238 | 7.6037 | 207.6046 | 2563.7286 | 38455.9292
2020-04-13 07:00 | 7.1622 | 7.5388 | 209.8833 | 2495.0939 | 37426.4079
2020-04-13 08:00 | 7.4482 | 7.84 | 211.4178 | 2813.6999 | 42205.4987
2020-04-13 09:00 | 7.9049 | 8.3207 | 213.2936 | 3344.0676 | 50161.0143
2020-04-13 10:00 | 8.15 | 8.5787 | 216.4419 | 3634.7255 | 54520.8825
2020-04-13 11:00 | 8.9044 | 9.3727 | 225.9793 | 4508.8244 | 67632.3653
2020-04-13 12:00 | 9.9103 | 10.4315 | 236.7975 | 5308.0182 | 79620.2735
2020-04-13 13:00 | 10.2947 | 10.8361 | 236.0619 | 5476.4078 | 82146.1175
2020-04-13 14:00 | 10.1815 | 10.717 | 232.4861 | 5430.8882 | 81463.3231
2020-04-13 15:00 | 8.9052 | 9.3735 | 230.6647 | 4509.6743 | 67645.114
2020-04-13 16:00 | 7.7029 | 8.1081 | 236.5655 | 3104.6812 | 46570.2181
2020-04-13 17:00 | 7.4414 | 7.8328 | 240.5955 | 2806.087 | 42091.3043
2020-04-13 18:00 | 7.0257 | 7.3952 | 223.7014 | 2356.329 | 35344.9349
2020-04-13 19:00 | 7.4283 | 7.819 | 201.3924 | 2791.5219 | 41872.8283
2020-04-13 20:00 | 8.0553 | 8.479 | 207.7319 | 3522.3258 | 52834.8877
2020-04-13 21:00 | 7.927 | 8.3439 | 234.8293 | 3370.2036 | 50553.0533
2020-04-13 22:00 | 6.387 | 6.7229 | 269.636 | 1763.0257 | 26445.386
2020-04-13 23:00 | 5.8615 | 6.1697 | 301.079 | 1350.8174 | 20262.2616
2020-04-14 00:00 | 7.3614 | 7.7486 | 330.2435 | 2717.0081 | 40755.1208
2020-04-14 01:00 | 7.6934 | 8.098 | 340.3891 | 3093.4023 | 46401.0348
2020-04-14 02:00 | 7.2134 | 7.5928 | 337.1809 | 2552.1637 | 38282.455
2020-04-14 03:00 | 8.2094 | 8.6412 | 335.7328 | 3705.2454 | 55578.6804
2020-04-14 04:00 | 8.4029 | 8.8448 | 340.1543 | 3934.9669 | 59024.5038
2020-04-14 05:00 | 8.1006 | 8.5267 | 342.9509 | 3576.0829 | 53641.2436
2020-04-14 06:00 | 6.8887 | 7.251 | 344.482 | 2221.9621 | 33329.4308
2020-04-14 07:00 | 6.811 | 7.1692 | 338.7892 | 2145.6672 | 32185.0085
2020-04-14 08:00 | 6.0928 | 6.4132 | 335.37 | 1521.2502 | 22818.7536
2020-04-14 09:00 | 5.3303 | 5.6107 | 338.5468 | 1001.5226 | 15022.8388
2020-04-14 10:00 | 5.9726 | 6.2867 | 347.7745 | 1432.702 | 21490.5307
2020-04-14 11:00 | 6.006 | 6.3219 | 348.4902 | 1457.3186 | 21859.7789
2020-04-14 12:00 | 5.7305 | 6.0319 | 348.2113 | 1254.3396 | 18815.0944
2020-04-14 13:00 | 5.1686 | 5.4405 | 348.4343 | 906.1209 | 13591.8133
2020-04-14 14:00 | 5.1038 | 5.3722 | 340.4479 | 871.8558 | 13077.8364
2020-04-14 15:00 | 5.6623 | 5.9601 | 334.9279 | 1208.4023 | 18126.034
2020-04-14 16:00 | 5.4554 | 5.7424 | 330.3697 | 1079.4789 | 16192.1828
2020-04-14 17:00 | 5.2076 | 5.4815 | 318.9297 | 926.7173 | 13900.7594
2020-04-14 18:00 | 5.352 | 5.6335 | 308.8679 | 1015.0083 | 15225.1245
2020-04-14 19:00 | 6.2287 | 6.5563 | 305.9188 | 1627.7329 | 24415.9933
2020-04-14 20:00 | 6.9044 | 7.2675 | 302.8306 | 2237.3185 | 33559.777
2020-04-14 21:00 | 7.3197 | 7.7047 | 302.923 | 2670.5393 | 40058.0897
2020-04-14 22:00 | 8.2807 | 8.7162 | 299.104 | 3789.88 | 56848.2002
2020-04-14 23:00 | 8.3304 | 8.7685 | 299.2914 | 3848.8531 | 57732.796
2020-04-15 00:00 | 8.1887 | 8.6194 | 298.4268 | 3680.6394 | 55209.5912
2020-04-15 01:00 | 7.911 | 8.3271 | 294.5386 | 3351.3418 | 50270.127
2020-04-15 02:00 | 8.1226 | 8.5498 | 291.8843 | 3602.1243 | 54031.8645
2020-04-15 03:00 | 8.3501 | 8.7892 | 290.5424 | 3872.2535 | 58083.8028
2020-04-15 04:00 | 7.869 | 8.2828 | 284.1726 | 3301.4864 | 49522.2963
2020-04-15 05:00 | 7.4289 | 7.8196 | 280.4045 | 2792.1226 | 41881.8393
2020-04-15 06:00 | 9.4478 | 9.9447 | 289.7866 | 5010.5421 | 75158.1316
2020-04-15 07:00 | 10.151 | 10.6849 | 291.6321 | 5418.6394 | 81279.5914
2020-04-15 08:00 | 9.3637 | 9.8562 | 288.2773 | 4937.7921 | 74066.8814
2020-04-15 09:00 | 9.2671 | 9.7545 | 285.695 | 4854.1894 | 72812.8406
2020-04-15 10:00 | 10.2271 | 10.765 | 284.7963 | 5449.2135 | 81738.2028
2020-04-15 11:00 | 10.1172 | 10.6493 | 283.5695 | 5405.0253 | 81075.3802
2020-04-15 12:00 | 10.6536 | 11.2139 | 282.6092 | 5587.3384 | 83810.0765
2020-04-15 13:00 | 11.6015 | 12.2116 | 282.9141 | 5699.4233 | 85491.3494
2020-04-15 14:00 | 11.4282 | 12.0292 | 286.4567 | 5699.0585 | 85485.8769
2020-04-15 15:00 | 11.9121 | 12.5386 | 285.3467 | 5700 | 85500
2020-04-15 16:00 | 11.8723 | 12.4967 | 286.0989 | 5699.9934 | 85499.9006
2020-04-15 17:00 | 10.2549 | 10.7943 | 286.6001 | 5460.4241 | 81906.3622
2020-04-15 18:00 | 9.135 | 9.6154 | 285.4232 | 4739.8882 | 71098.3232
2020-04-15 19:00 | 9.0806 | 9.5582 | 287.5152 | 4692.8676 | 70393.0138
2020-04-15 20:00 | 9.1272 | 9.6073 | 287.1537 | 4733.179 | 70997.6856
2020-04-15 21:00 | 8.9709 | 9.4427 | 285.7019 | 4583.6688 | 68755.0326
2020-04-15 22:00 | 9.2498 | 9.7363 | 286.9829 | 4839.2049 | 72588.0739
2020-04-15 23:00 | 8.767 | 9.2281 | 283.4818 | 4354.0703 | 65311.055
2020-04-16 00:00 | 8.5403 | 8.9895 | 282.1902 | 4098.1061 | 61471.5913
2020-04-16 01:00 | 8.2831 | 8.7188 | 278.7508 | 3792.7799 | 56891.6992
2020-04-16 02:00 | 8.3343 | 8.7726 | 271.9003 | 3853.5317 | 57802.9762
2020-04-16 03:00 | 8.4472 | 8.8914 | 267.7022 | 3987.5398 | 59813.0966
2020-04-16 04:00 | 8.5163 | 8.9642 | 262.7499 | 4069.6339 | 61044.5079
2020-04-16 05:00 | 8.0699 | 8.4943 | 250.9332 | 3539.5917 | 53093.8748
2020-04-16 06:00 | 9.9855 | 10.5107 | 251.5182 | 5352.0936 | 80281.4036
2020-04-16 07:00 | 11.5831 | 12.1923 | 258.7376 | 5699.3846 | 85490.7693
2020-04-16 08:00 | 12.1608 | 12.8004 | 259.3957 | 5700 | 85500
2020-04-16 09:00 | 13.2215 | 13.9169 | 256.9338 | 5700 | 85500
2020-04-16 10:00 | 14.3512 | 15.106 | 252.8432 | 5700 | 85500
2020-04-16 11:00 | 15.4361 | 16.248 | 258.6609 | 5700 | 85500
2020-04-16 12:00 | 15.8506 | 16.6842 | 265.7985 | 5700 | 85500
2020-04-16 13:00 | 15.6767 | 16.5012 | 272.3847 | 5700 | 85500
2020-04-16 14:00 | 15.3418 | 16.1487 | 278.7385 | 5700 | 85500
2020-04-16 15:00 | 14.0672 | 14.8071 | 282.4163 | 5700 | 85500
2020-04-16 16:00 | 12.9695 | 13.6516 | 285.4577 | 5700 | 85500
2020-04-16 17:00 | 12.1698 | 12.8099 | 291.3068 | 5700 | 85500
2020-04-16 18:00 | 11.2371 | 11.8281 | 304.4775 | 5682.8442 | 85242.6625
2020-04-16 19:00 | 10.5877 | 11.1445 | 319.5589 | 5571.6581 | 83574.8721
2020-04-16 20:00 | 10.0423 | 10.5704 | 326.2083 | 5374.9052 | 80623.5781
2020-04-16 21:00 | 9.1677 | 9.6498 | 323.6307 | 4768.1647 | 71522.4701
2020-04-16 22:00 | 8.1047 | 8.5309 | 315.9093 | 3580.8835 | 53713.2518
2020-04-16 23:00 | 7.9657 | 8.3846 | 306.4616 | 3416.1109 | 51241.6629
2020-04-17 00:00 | 7.9843 | 8.4042 | 302.3562 | 3438.138 | 51572.0701
2020-04-17 01:00 | 7.796 | 8.206 | 301.3699 | 3214.9708 | 48224.5625
2020-04-17 02:00 | 7.7737 | 8.1826 | 301.4849 | 3188.5581 | 47828.3709
2020-04-17 03:00 | 7.6242 | 8.0252 | 302.535 | 3011.3303 | 45169.9546
2020-04-17 04:00 | 7.1428 | 7.5185 | 305.2105 | 2473.5333 | 37102.9989
2020-04-17 05:00 | 6.3832 | 6.7189 | 308.3145 | 1759.7616 | 26396.4238
2020-04-17 06:00 | 6.7202 | 7.0736 | 314.9074 | 2056.6269 | 30849.4035
2020-04-17 07:00 | 6.3074 | 6.6391 | 310.8328 | 1694.9382 | 25424.0737
2020-04-17 08:00 | 6.4535 | 6.7929 | 306.3324 | 1819.8718 | 27298.0767
2020-04-17 09:00 | 6.7276 | 7.0815 | 303.9929 | 2063.9297 | 30958.9457
2020-04-17 10:00 | 7.0418 | 7.4121 | 302.3133 | 2372.0984 | 35581.4755
2020-04-17 11:00 | 7.3415 | 7.7277 | 302.6026 | 2694.8747 | 40423.12
2020-04-17 12:00 | 8.6654 | 9.1211 | 299.3611 | 4239.5991 | 63593.9864
2020-04-17 13:00 | 9.4325 | 9.9286 | 297.0076 | 4997.2953 | 74959.4301
2020-04-17 14:00 | 9.1368 | 9.6174 | 296.6544 | 4741.4825 | 71122.2381
2020-04-17 15:00 | 9.6631 | 10.1714 | 304.4575 | 5156.073 | 77341.0949
2020-04-17 16:00 | 9.2724 | 9.7601 | 336.9961 | 4858.8074 | 72882.1107
2020-04-17 17:00 | 8.8385 | 9.3034 | 351.0745 | 4434.6485 | 66519.7273
2020-04-17 18:00 | 5.9142 | 6.2252 | 342.2458 | 1389.6743 | 20845.1145
2020-04-17 19:00 | 4.9269 | 5.186 | 318.75 | 778.3875 | 11675.8132
2020-04-17 20:00 | 4.8327 | 5.0869 | 306.4942 | 728.6267 | 10929.4012
2020-04-17 21:00 | 5.0467 | 5.3122 | 309.791 | 841.7002 | 12625.5029
2020-04-17 22:00 | 5.5019 | 5.7913 | 332.2227 | 1108.4312 | 16626.4683
2020-04-17 23:00 | 5.5648 | 5.8575 | 334.6138 | 1147.6545 | 17214.8173
2020-04-18 00:00 | 5.2278 | 5.5028 | 326.9308 | 937.659 | 14064.8852
2020-04-18 01:00 | 5.0205 | 5.2845 | 315.2011 | 827.8242 | 12417.3624
2020-04-18 02:00 | 5.4628 | 5.7501 | 307.5937 | 1084.0836 | 16261.2547
2020-04-18 03:00 | 5.8497 | 6.1574 | 311.174 | 1342.1542 | 20132.3133
2020-04-18 04:00 | 5.7707 | 6.0742 | 319.7893 | 1283.913 | 19258.6947
2020-04-18 05:00 | 4.298 | 4.5241 | 324.3415 | 484.154 | 7262.3107
2020-04-18 06:00 | 3.7282 | 3.9243 | 330.0876 | 276.3526 | 4145.2893
2020-04-18 07:00 | 4.0851 | 4.2999 | 310.5097 | 403.5811 | 6053.7164
2020-04-18 08:00 | 4.9458 | 5.2059 | 301.9879 | 788.3613 | 11825.4194
2020-04-18 09:00 | 5.4704 | 5.7582 | 301.735 | 1088.8322 | 16332.4829
2020-04-18 10:00 | 5.7499 | 6.0523 | 294.3822 | 1268.595 | 19028.9243
2020-04-18 11:00 | 6.653 | 7.003 | 300.135 | 1990.7516 | 29861.2747
2020-04-18 12:00 | 7.2286 | 7.6088 | 300.5838 | 2569.1045 | 38536.5668
2020-04-18 13:00 | 7.571 | 7.9692 | 302.8439 | 2950.4432 | 44256.6487
2020-04-18 14:00 | 7.6918 | 8.0964 | 307.8498 | 3091.5431 | 46373.1468
2020-04-18 15:00 | 7.6542 | 8.0567 | 315.9589 | 3046.8658 | 45702.9864
2020-04-18 16:00 | 6.9523 | 7.3179 | 329.981 | 2284.3128 | 34264.6924
2020-04-18 17:00 | 6.5258 | 6.869 | 342.8009 | 1881.6541 | 28224.8114
2020-04-18 18:00 | 6.2963 | 6.6274 | 351.6173 | 1685.452 | 25281.7806
2020-04-18 19:00 | 5.692 | 5.9914 | 358.1447 | 1226.8867 | 18403.3009
2020-04-18 20:00 | 4.6149 | 4.8576 | 356.6977 | 624.9228 | 9373.8413
2020-04-18 21:00 | 3.3495 | 3.5256 | 348.9978 | 162.3349 | 2435.0233
2020-04-18 22:00 | 3.0579 | 3.2187 | 350.3318 | 94.8074 | 1422.1104
2020-04-18 23:00 | 2.8296 | 2.9785 | 335.7629 | 0 | 0
2020-04-19 00:00 | 2.9525 | 3.1078 | 325.0655 | 71.0721 | 1066.0815
2020-04-19 01:00 | 3.242 | 3.4125 | 313.2716 | 136.2848 | 2044.2718
2020-04-19 02:00 | 3.8961 | 4.1011 | 301.3473 | 333.5737 | 5003.6054
2020-04-19 03:00 | 4.9336 | 5.1931 | 296.1282 | 781.9112 | 11728.6674
2020-04-19 04:00 | 5.3696 | 5.652 | 293.1761 | 1025.9657 | 15389.4851
2020-04-19 05:00 | 4.5711 | 4.8115 | 288.8851 | 605.4415 | 9081.6228
2020-04-19 06:00 | 3.5565 | 3.7436 | 286.5314 | 224.6647 | 3369.97
2020-04-19 07:00 | 3.8092 | 4.0096 | 287.7872 | 301.3634 | 4520.4509
2020-04-19 08:00 | 4.6665 | 4.9119 | 303.1599 | 647.8394 | 9717.5915
2020-04-19 09:00 | 5.1173 | 5.3864 | 300.5041 | 878.9844 | 13184.7655
2020-04-19 10:00 | 5.2495 | 5.5256 | 295.4505 | 951.1283 | 14266.9248
2020-04-19 11:00 | 5.5808 | 5.8743 | 295.532 | 1157.6019 | 17364.028
2020-04-19 12:00 | 5.9672 | 6.281 | 296.6978 | 1428.7009 | 21430.5141
2020-04-19 13:00 | 6.4505 | 6.7898 | 296.7077 | 1817.3133 | 27259.6992
2020-04-19 14:00 | 6.7476 | 7.1024 | 297.4368 | 2083.4729 | 31252.0942
2020-04-19 15:00 | 7.3362 | 7.722 | 309.1452 | 2688.873 | 40333.0956
2020-04-19 16:00 | 7.4205 | 7.8108 | 332.9257 | 2782.811 | 41742.1657
2020-04-19 17:00 | 8.3 | 8.7365 | 352.8874 | 3812.7931 | 57191.8969
2020-04-19 18:00 | 8.1887 | 8.6194 | 1.207 | 3680.6882 | 55210.3237
2020-04-19 19:00 | 7.4492 | 7.8409 | 2.6709 | 2814.7236 | 42220.8541
2020-04-19 20:00 | 7.1227 | 7.4973 | 0.51099 | 2451.5027 | 36772.5402
2020-04-19 21:00 | 7.0852 | 7.4578 | 357.7956 | 2414.6643 | 36219.964
2020-04-19 22:00 | 7.4461 | 7.8377 | 349.7033 | 2811.282 | 42169.2295
2020-04-19 23:00 | 7.0981 | 7.4714 | 350.5996 | 2427.3322 | 36409.9829
2020-04-20 00:00 | 6.9589 | 7.3249 | 351.0124 | 2290.8366 | 34362.5491
2020-04-20 01:00 | 7.0114 | 7.3801 | 350.0658 | 2342.271 | 35134.0654
2020-04-20 02:00 | 7.0113 | 7.3801 | 348.6822 | 2342.2111 | 35133.1669
2020-04-20 03:00 | 7.0155 | 7.3845 | 346.5441 | 2346.3803 | 35195.7045
2020-04-20 04:00 | 6.9383 | 7.3032 | 344.503 | 2270.6253 | 34059.3799
2020-04-20 05:00 | 6.1177 | 6.4394 | 344.1815 | 1539.5924 | 23093.8858
2020-04-20 06:00 | 6.0839 | 6.4039 | 346.9113 | 1514.738 | 22721.0703
2020-04-20 07:00 | 7.3161 | 7.7009 | 353.9148 | 2666.5 | 39997.4993
2020-04-20 08:00 | 8.2487 | 8.6825 | 357.6232 | 3751.9073 | 56278.6096
2020-04-20 09:00 | 8.1054 | 8.5317 | 355.3482 | 3581.7634 | 53726.4504
2020-04-20 10:00 | 8.4147 | 8.8572 | 349.5004 | 3948.9395 | 59234.0932
2020-04-20 11:00 | 8.4762 | 8.922 | 348.1086 | 4021.9789 | 60329.6839
2020-04-20 12:00 | 8.3564 | 8.7959 | 347.2897 | 3879.7215 | 58195.8229
2020-04-20 13:00 | 8.2296 | 8.6624 | 346.2956 | 3729.2279 | 55938.4183
2020-04-20 14:00 | 8.0407 | 8.4636 | 346.5093 | 3505.0376 | 52575.564
2020-04-20 15:00 | 7.9171 | 8.3335 | 348.132 | 3358.5366 | 50378.0485
2020-04-20 16:00 | 7.6184 | 8.0191 | 350.1356 | 3004.5076 | 45067.6142
2020-04-20 17:00 | 6.775 | 7.1313 | 351.4919 | 2110.3664 | 31655.4961
2020-04-20 18:00 | 6.4789 | 6.8197 | 353.0044 | 1841.5966 | 27623.9488
2020-04-20 19:00 | 6.2985 | 6.6298 | 355.153 | 1687.3926 | 25310.8889
2020-04-20 20:00 | 6.0719 | 6.3912 | 354.3019 | 1505.8653 | 22587.9798
2020-04-20 21:00 | 5.8723 | 6.1812 | 351.2392 | 1358.8286 | 20382.4285
2020-04-20 22:00 | 6.2406 | 6.5688 | 348.0214 | 1637.878 | 24568.1699
2020-04-20 23:00 | 6.2021 | 6.5283 | 346.4066 | 1604.962 | 24074.4302
2020-04-21 00:00 | 6.2866 | 6.6172 | 345.4472 | 1677.169 | 25157.5349
2020-04-21 01:00 | 6.2175 | 6.5445 | 342.7695 | 1618.1363 | 24272.0452
2020-04-21 02:00 | 6.2831 | 6.6135 | 341.9378 | 1674.1874 | 25112.8108
2020-04-21 03:00 | 6.3953 | 6.7317 | 341.6697 | 1770.1103 | 26551.655
2020-04-21 04:00 | 6.2356 | 6.5635 | 342.7348 | 1633.6003 | 24504.0048
2020-04-21 05:00 | 5.0182 | 5.2822 | 346.5197 | 826.6426 | 12399.639
2020-04-21 06:00 | 4.938 | 5.1978 | 354.2562 | 784.2759 | 11764.139
2020-04-21 07:00 | 5.337 | 5.6177 | 0.82892 | 1005.6576 | 15084.8639
2020-04-21 08:00 | 6.6894 | 7.0412 | 11.757 | 2026.419 | 30396.2853
2020-04-21 09:00 | 6.371 | 6.7061 | 13.6259 | 1749.3734 | 26240.6016
2020-04-21 10:00 | 5.5237 | 5.8142 | 3.2947 | 1122.0177 | 16830.2653
2020-04-21 11:00 | 5.6952 | 5.9948 | 358.2537 | 1228.91 | 18433.6502
2020-04-21 12:00 | 6.1835 | 6.5087 | 354.9211 | 1589.0567 | 23835.8503
2020-04-21 13:00 | 7.1145 | 7.4887 | 354.0426 | 2443.4418 | 36651.6269
2020-04-21 14:00 | 7.5828 | 7.9816 | 357.1194 | 2963.5405 | 44453.1071
2020-04-21 15:00 | 7.415 | 7.805 | 1.7413 | 2776.6776 | 41650.1638
2020-04-21 16:00 | 7.0112 | 7.38 | 0.40663 | 2342.1231 | 35131.8463
2020-04-21 17:00 | 6.5729 | 6.9186 | 0.93298 | 1921.8832 | 28828.2478
2020-04-21 18:00 | 5.8291 | 6.1357 | 0.93669 | 1326.9659 | 19904.488
2020-04-21 19:00 | 5.4721 | 5.7599 | 359.6333 | 1089.8416 | 16347.6241
2020-04-21 20:00 | 5.0951 | 5.3631 | 356.9913 | 867.2538 | 13008.807
2020-04-21 21:00 | 4.725 | 4.9735 | 352.8639 | 673.8283 | 10107.4246
2020-04-21 22:00 | 5.1901 | 5.4631 | 343.6563 | 917.4551 | 13761.8267
2020-04-21 23:00 | 5.1064 | 5.375 | 336.5569 | 873.2405 | 13098.6076
2020-04-22 00:00 | 5.0621 | 5.3283 | 328.4959 | 849.8096 | 12747.1436
2020-04-22 01:00 | 5.2906 | 5.5688 | 318.6357 | 976.75 | 14651.2502
2020-04-22 02:00 | 5.7169 | 6.0176 | 311.6165 | 1244.3403 | 18665.1049
2020-04-22 03:00 | 6.0861 | 6.4062 | 310.9288 | 1516.3458 | 22745.1873
2020-04-22 04:00 | 6.311 | 6.6429 | 314.2293 | 1698.0314 | 25470.4712
2020-04-22 05:00 | 6.3323 | 6.6654 | 317.4055 | 1716.3023 | 25744.5344
2020-04-22 06:00 | 6.3876 | 6.7235 | 324.0247 | 1763.4949 | 26452.4238
2020-04-22 07:00 | 7.7243 | 8.1305 | 335.2659 | 3129.9681 | 46949.5221
2020-04-22 08:00 | 7.4897 | 7.8836 | 338.9589 | 2859.8697 | 42898.0455
2020-04-22 09:00 | 7.6158 | 8.0164 | 343.8974 | 3001.4221 | 45021.3318
2020-04-22 10:00 | 7.7245 | 8.1307 | 337.3027 | 3130.1965 | 46952.9476
2020-04-22 11:00 | 8.3164 | 8.7538 | 339.61 | 3832.3262 | 57484.8925
2020-04-22 12:00 | 8.2439 | 8.6775 | 341.9155 | 3746.2493 | 56193.739
2020-04-22 13:00 | 8.3846 | 8.8256 | 346.1245 | 3913.2319 | 58698.4789
2020-04-22 14:00 | 8.5143 | 8.9621 | 351.3635 | 4067.2911 | 61009.3671
2020-04-22 15:00 | 8.2359 | 8.6691 | 354.0265 | 3736.7375 | 56051.063
2020-04-22 16:00 | 7.2841 | 7.6672 | 356.9086 | 2630.9005 | 39463.508
2020-04-22 17:00 | 6.7934 | 7.1507 | 0.3938 | 2128.4376 | 31926.564
2020-04-22 18:00 | 6.5488 | 6.8933 | 2.9491 | 1901.3463 | 28520.1947
2020-04-22 19:00 | 6.2239 | 6.5512 | 2.4875 | 1623.5816 | 24353.7247
2020-04-22 20:00 | 5.8651 | 6.1736 | 359.0807 | 1353.5266 | 20302.8992
2020-04-22 21:00 | 5.412 | 5.6967 | 356.2415 | 1052.4219 | 15786.3283
2020-04-22 22:00 | 5.9551 | 6.2684 | 2.8994 | 1419.8498 | 21297.7471
2020-04-22 23:00 | 5.5665 | 5.8592 | 10.4026 | 1148.6579 | 17229.8683
2020-04-23 00:00 | 4.707 | 4.9546 | 14.3051 | 665.8384 | 9987.5764
2020-04-23 01:00 | 3.777 | 3.9757 | 14.6489 | 291.0394 | 4365.5908
2020-04-23 02:00 | 2.92 | 3.0735 | 4.8121 | 63.7364 | 956.0457
2020-04-23 03:00 | 2.3515 | 2.4752 | 350.227 | 0 | 0
2020-04-23 04:00 | 2.3688 | 2.4934 | 337.0251 | 0 | 0
2020-04-23 05:00 | 2.5278 | 2.6607 | 330.528 | 0 | 0
2020-04-23 06:00 | 1.4839 | 1.562 | 313.0658 | 0 | 0
2020-04-23 07:00 | 2.0311 | 2.1379 | 299.1718 | 0 | 0
2020-04-23 08:00 | 3.9912 | 4.2011 | 321.5634 | 368.7944 | 5531.9158
2020-04-23 09:00 | 4.3028 | 4.5291 | 326.6642 | 486.2653 | 7293.9799
2020-04-23 10:00 | 4.761 | 5.0114 | 308.6795 | 690.722 | 10360.8293
2020-04-23 11:00 | 5.0732 | 5.34 | 310.5809 | 855.6745 | 12835.1174
2020-04-23 12:00 | 5.4038 | 5.688 | 312.3023 | 1047.2927 | 15709.3912
2020-04-23 13:00 | 5.8198 | 6.1258 | 312.111 | 1320.0867 | 19801.3005
2020-04-23 14:00 | 6.3354 | 6.6686 | 305.3681 | 1718.876 | 25783.1402
2020-04-23 15:00 | 7.017 | 7.3861 | 302.4663 | 2347.8477 | 35217.7161
2020-04-23 16:00 | 6.4073 | 6.7443 | 302.0901 | 1780.3831 | 26705.7459
2020-04-23 17:00 | 5.4506 | 5.7372 | 298.8464 | 1076.4483 | 16146.7243
2020-04-23 18:00 | 4.9959 | 5.2587 | 290.1489 | 814.8557 | 12222.8354
2020-04-23 19:00 | 5.2439 | 5.5197 | 281.9442 | 947.6457 | 14214.6856
2020-04-23 20:00 | 5.8456 | 6.153 | 281.4321 | 1339.1134 | 20086.7011
2020-04-23 21:00 | 6.3411 | 6.6746 | 287.9461 | 1723.7611 | 25856.417
2020-04-23 22:00 | 5.8751 | 6.1841 | 295.1175 | 1360.8955 | 20413.4332
2020-04-23 23:00 | 5.7812 | 6.0853 | 295.1671 | 1291.6772 | 19375.1579
2020-04-24 00:00 | 5.8922 | 6.2021 | 290.7739 | 1373.4507 | 20601.7605
2020-04-24 01:00 | 6.2583 | 6.5874 | 286.2313 | 1652.996 | 24794.94
2020-04-24 02:00 | 6.7002 | 7.0526 | 284.6944 | 2036.9962 | 30554.9428
2020-04-24 03:00 | 6.9061 | 7.2694 | 285.957 | 2239.044 | 33585.6599
2020-04-24 04:00 | 6.8274 | 7.1865 | 284.2476 | 2161.8223 | 32427.3345
2020-04-24 05:00 | 5.9275 | 6.2393 | 281.6804 | 1399.5082 | 20992.6235
2020-04-24 06:00 | 5.177 | 5.4493 | 282.2439 | 910.5273 | 13657.9101
2020-04-24 07:00 | 5.6927 | 5.9921 | 285.2629 | 1227.3207 | 18409.8107
2020-04-24 08:00 | 6.1375 | 6.4603 | 287.2995 | 1554.1873 | 23312.81
2020-04-24 09:00 | 6.6537 | 7.0036 | 293.6192 | 1991.3716 | 29870.5741
2020-04-24 10:00 | 6.2004 | 6.5265 | 283.3995 | 1603.5269 | 24052.904
2020-04-24 11:00 | 6.6087 | 6.9563 | 278.8848 | 1952.5164 | 29287.746
2020-04-24 12:00 | 6.7096 | 7.0624 | 276.7758 | 2046.1931 | 30692.8968
2020-04-24 13:00 | 6.8533 | 7.2137 | 277.6648 | 2187.1977 | 32807.9652
2020-04-24 14:00 | 7.1619 | 7.5385 | 279.5107 | 2494.7836 | 37421.7546
2020-04-24 15:00 | 6.715 | 7.0682 | 283.5247 | 2051.5726 | 30773.5895
2020-04-24 16:00 | 5.2558 | 5.5322 | 288.7052 | 955.0578 | 14325.8676
2020-04-24 17:00 | 4.1593 | 4.3781 | 288.3934 | 431.0747 | 6466.1212
2020-04-24 18:00 | 3.9973 | 4.2075 | 278.9965 | 371.0568 | 5565.8524
2020-04-24 19:00 | 4.4388 | 4.6722 | 272.3386 | 546.6861 | 8200.2922
2020-04-24 20:00 | 4.7122 | 4.9601 | 266.361 | 668.1417 | 10022.1249
2020-04-24 21:00 | 4.7637 | 5.0143 | 257.5068 | 692.1619 | 10382.4292
2020-04-24 22:00 | 6.0159 | 6.3323 | 258.5299 | 1464.6225 | 21969.3382
2020-04-24 23:00 | 5.6673 | 5.9654 | 253.7917 | 1211.5209 | 18172.8141
2020-04-25 00:00 | 5.8597 | 6.1679 | 244.251 | 1349.5189 | 20242.7829
2020-04-25 01:00 | 6.2571 | 6.5861 | 238.0347 | 1651.9441 | 24779.1614
2020-04-25 02:00 | 5.7987 | 6.1037 | 232.055 | 1304.5728 | 19568.5922
2020-04-25 03:00 | 6.2307 | 6.5584 | 221.5861 | 1629.3907 | 24440.8605
2020-04-25 04:00 | 6.8906 | 7.2531 | 221.4867 | 2223.8501 | 33357.7511
2020-04-25 05:00 | 6.7505 | 7.1055 | 224.4544 | 2086.3336 | 31295.0046
2020-04-25 06:00 | 6.2616 | 6.5909 | 230.5884 | 1655.8074 | 24837.1113
2020-04-25 07:00 | 6.6932 | 7.0453 | 236.9702 | 2030.1882 | 30452.8226
2020-04-25 08:00 | 6.541 | 6.885 | 243.9275 | 1894.5964 | 28418.9458
2020-04-25 09:00 | 5.7936 | 6.0983 | 243.1859 | 1300.8275 | 19512.4118
2020-04-25 10:00 | 7.5923 | 7.9916 | 247.1755 | 2974.0904 | 44611.3555
2020-04-25 11:00 | 7.4217 | 7.8121 | 251.7698 | 2784.168 | 41762.5199
2020-04-25 12:00 | 7.4074 | 7.797 | 258.8563 | 2768.2426 | 41523.6383
2020-04-25 13:00 | 6.6661 | 7.0167 | 252.5955 | 2003.5777 | 30053.6661
2020-04-25 14:00 | 6.7414 | 7.0959 | 257.3004 | 2077.3871 | 31160.8062
2020-04-25 15:00 | 6.2724 | 6.6023 | 280.2692 | 1665.035 | 24975.5248
2020-04-25 16:00 | 5.2738 | 5.5511 | 291.8984 | 966.2767 | 14494.1499
2020-04-25 17:00 | 4.1179 | 4.3345 | 313.8097 | 415.7429 | 6236.144
2020-04-25 18:00 | 3.7508 | 3.948 | 342.4483 | 283.1402 | 4247.1023
2020-04-25 19:00 | 4.2577 | 4.4817 | 355.8994 | 467.5496 | 7013.2444
2020-04-25 20:00 | 5.3673 | 5.6496 | 348.9697 | 1024.5659 | 15368.488
2020-04-25 21:00 | 6.417 | 6.7545 | 340.2874 | 1788.6376 | 26829.5634
2020-04-25 22:00 | 6.8601 | 7.2209 | 346.8402 | 2193.9139 | 32908.7086
2020-04-25 23:00 | 7.5386 | 7.9351 | 348.2135 | 2914.3255 | 43714.8819
2020-04-26 00:00 | 9.5924 | 10.0969 | 352.4863 | 5112.5788 | 76688.6813
2020-04-26 01:00 | 11.4235 | 12.0243 | 350.6799 | 5699.0485 | 85485.7282
2020-04-26 02:00 | 12.0309 | 12.6637 | 346.0811 | 5700 | 85500
2020-04-26 03:00 | 11.4275 | 12.0285 | 342.881 | 5699.057 | 85485.8556
2020-04-26 04:00 | 10.5594 | 11.1148 | 339.283 | 5564.9483 | 83474.2252
2020-04-26 05:00 | 9.5829 | 10.0869 | 330.4328 | 5106.7412 | 76601.1187
2020-04-26 06:00 | 9.9826 | 10.5077 | 329.4279 | 5350.9273 | 80263.9089
2020-04-26 07:00 | 10.2133 | 10.7505 | 332.922 | 5443.6771 | 81655.157
2020-04-26 08:00 | 10.6763 | 11.2378 | 337.9906 | 5592.7355 | 83891.0325
2020-04-26 09:00 | 10.4243 | 10.9726 | 336.114 | 5528.5157 | 82927.7352
2020-04-26 10:00 | 10.6519 | 11.2122 | 335.2389 | 5586.948 | 83804.2193
2020-04-26 11:00 | 10.1544 | 10.6884 | 331.206 | 5419.9781 | 81299.6709
2020-04-26 12:00 | 9.6887 | 10.1983 | 330.3087 | 5171.7847 | 77576.771
2020-04-26 13:00 | 9.202 | 9.686 | 329.0415 | 4797.856 | 71967.8403
2020-04-26 14:00 | 9.7794 | 10.2938 | 323.6678 | 5227.5694 | 78413.5412
2020-04-26 15:00 | 10.4207 | 10.9688 | 319.5723 | 5527.0813 | 82906.2198
2020-04-26 16:00 | 10.0809 | 10.6111 | 319.9269 | 5390.4329 | 80856.4933
2020-04-26 17:00 | 8.5859 | 9.0375 | 322.7319 | 4150.0718 | 62251.0773
2020-04-26 18:00 | 7.1342 | 7.5094 | 325.26 | 2463.9885 | 36959.8268
2020-04-26 19:00 | 6.4321 | 6.7704 | 323.0756 | 1801.5531 | 27023.2962
2020-04-26 20:00 | 6.2518 | 6.5806 | 319.018 | 1647.4607 | 24711.9104
2020-04-26 21:00 | 6.4825 | 6.8235 | 315.5051 | 1844.6456 | 27669.6835
2020-04-26 22:00 | 7.0318 | 7.4016 | 312.795 | 2362.3128 | 35434.692
2020-04-26 23:00 | 6.7989 | 7.1565 | 313.6323 | 2133.8504 | 32007.7566
2020-04-27 00:00 | 6.7321 | 7.0862 | 311.3889 | 2068.3015 | 31024.5232
2020-04-27 01:00 | 6.5739 | 6.9196 | 305.1339 | 1922.7496 | 28841.2446
2020-04-27 02:00 | 6.5149 | 6.8576 | 297.6364 | 1872.3715 | 28085.5724
2020-04-27 03:00 | 6.7348 | 7.089 | 289.3963 | 2070.9713 | 31064.5695
2020-04-27 04:00 | 6.7383 | 7.0927 | 282.2792 | 2074.4151 | 31116.2266
2020-04-27 05:00 | 5.9641 | 6.2777 | 278.8727 | 1426.4225 | 21396.3374
2020-04-27 06:00 | 6.1272 | 6.4494 | 284.8837 | 1546.5987 | 23198.9798
2020-04-27 07:00 | 7.82 | 8.2313 | 307.6303 | 3243.4291 | 48651.4366
2020-04-27 08:00 | 8.8104 | 9.2738 | 317.6189 | 4402.9836 | 66044.7536
2020-04-27 09:00 | 8.3765 | 8.817 | 318.4253 | 3903.6032 | 58554.0479
2020-04-27 10:00 | 8.5828 | 9.0342 | 312.5208 | 4146.6327 | 62199.4902
2020-04-27 11:00 | 8.8118 | 9.2752 | 311.6509 | 4404.49 | 66067.3507
2020-04-27 12:00 | 8.9705 | 9.4423 | 313.2558 | 4583.2396 | 68748.5937
2020-04-27 13:00 | 8.5523 | 9.0021 | 314.1278 | 4112.2819 | 61684.228
2020-04-27 14:00 | 8.0679 | 8.4922 | 315.7981 | 3537.252 | 53058.7807
2020-04-27 15:00 | 7.2988 | 7.6827 | 317.3889 | 2647.2761 | 39709.1416
2020-04-27 16:00 | 5.802 | 6.1072 | 319.3839 | 1307.0391 | 19605.587
2020-04-27 17:00 | 4.9736 | 5.2352 | 327.1785 | 803.0517 | 12045.775
2020-04-27 18:00 | 4.7572 | 5.0074 | 340.9626 | 688.7086 | 10330.6294
2020-04-27 19:00 | 4.6859 | 4.9323 | 355.086 | 656.4505 | 9846.7578
2020-04-27 20:00 | 4.0205 | 4.2319 | 5.2766 | 379.6322 | 5694.4823
2020-04-27 21:00 | 2.5192 | 2.6517 | 14.602 | 0 | 0
2020-04-27 22:00 | 0.22935 | 0.24141 | 57.2139 | 0 | 0
2020-04-27 23:00 | 1.5233 | 1.6034 | 179.8238 | 0 | 0
2020-04-28 00:00 | 3.3581 | 3.5347 | 191.2366 | 164.9211 | 2473.8166
2020-04-28 01:00 | 5.2966 | 5.5752 | 197.6722 | 980.5016 | 14707.5245
2020-04-28 02:00 | 6.7066 | 7.0594 | 207.4848 | 2043.3278 | 30649.917
2020-04-28 03:00 | 6.9875 | 7.3551 | 215.0683 | 2318.9121 | 34783.6814
2020-04-28 04:00 | 6.6528 | 7.0027 | 221.4234 | 1990.4945 | 29857.4182
2020-04-28 05:00 | 5.675 | 5.9735 | 224.7835 | 1216.29 | 18244.3493
2020-04-28 06:00 | 4.3579 | 4.5871 | 223.0847 | 510.7675 | 7661.5132
2020-04-28 07:00 | 4.3242 | 4.5516 | 221.0702 | 495.7794 | 7436.6906
2020-04-28 08:00 | 4.6496 | 4.8941 | 217.2897 | 640.3301 | 9604.9509
2020-04-28 09:00 | 5.1885 | 5.4614 | 216.7865 | 916.6198 | 13749.297
2020-04-28 10:00 | 6.0294 | 6.3466 | 228.5089 | 1474.5865 | 22118.7979
2020-04-28 11:00 | 6.3898 | 6.7258 | 240.1561 | 1765.3805 | 26480.7077
2020-04-28 12:00 | 6.2641 | 6.5936 | 238.9701 | 1657.9636 | 24869.4536
2020-04-28 13:00 | 6.4132 | 6.7505 | 236.2406 | 1785.4103 | 26781.1538
2020-04-28 14:00 | 6.1492 | 6.4726 | 233.6812 | 1562.8198 | 23442.2972
2020-04-28 15:00 | 4.9129 | 5.1713 | 226.6384 | 770.9787 | 11564.68
2020-04-28 16:00 | 4.8431 | 5.0978 | 204.0877 | 734.114 | 11011.7096
2020-04-28 17:00 | 6.5329 | 6.8765 | 188.2396 | 1887.6934 | 28315.4004
2020-04-28 18:00 | 8.024 | 8.4461 | 183.6831 | 3485.2584 | 52278.8758
2020-04-28 19:00 | 8.6583 | 9.1137 | 184.8374 | 4231.6343 | 63474.5143
2020-04-28 20:00 | 8.5882 | 9.0399 | 189.0887 | 4152.7404 | 62291.1058
2020-04-28 21:00 | 8.3976 | 8.8392 | 192.5296 | 3928.6573 | 58929.8602
2020-04-28 22:00 | 7.4823 | 7.8759 | 198.2459 | 2851.6534 | 42774.8012
2020-04-28 23:00 | 7.6597 | 8.0626 | 203.5155 | 3053.4374 | 45801.5614
2020-04-29 00:00 | 8.0519 | 8.4754 | 207.9182 | 3518.3002 | 52774.5026
2020-04-29 01:00 | 8.0529 | 8.4764 | 211.794 | 3519.4484 | 52791.7266
2020-04-29 02:00 | 7.8012 | 8.2115 | 215.2998 | 3221.1016 | 48316.5245
2020-04-29 03:00 | 7.6502 | 8.0526 | 216.0719 | 3042.2166 | 45633.2487
2020-04-29 04:00 | 7.8183 | 8.2295 | 216.1984 | 3241.3791 | 48620.6859
2020-04-29 05:00 | 7.4354 | 7.8265 | 213.9122 | 2799.426 | 41991.3899
2020-04-29 06:00 | 5.9131 | 6.2241 | 209.9442 | 1388.8755 | 20833.1329
2020-04-29 07:00 | 5.5529 | 5.8449 | 210.1502 | 1140.1955 | 17102.9324
2020-04-29 08:00 | 5.7901 | 6.0947 | 210.2728 | 1298.2684 | 19474.0262
2020-04-29 09:00 | 6.5653 | 6.9106 | 210.1038 | 1915.3951 | 28730.9262
2020-04-29 10:00 | 6.4032 | 6.74 | 194.8343 | 1776.863 | 26652.9456
2020-04-29 11:00 | 7.3008 | 7.6847 | 194.974 | 2649.4654 | 39741.9804
2020-04-29 12:00 | 7.7782 | 8.1873 | 199.8527 | 3193.8545 | 47907.8174
2020-04-29 13:00 | 7.7229 | 8.1291 | 208.046 | 3128.3351 | 46925.026
2020-04-29 14:00 | 7.1782 | 7.5557 | 210.462 | 2512.9483 | 37694.224
2020-04-29 15:00 | 6.4526 | 6.792 | 205.1825 | 1819.0942 | 27286.4123
2020-04-29 16:00 | 6.2343 | 6.5622 | 198.4584 | 1632.4901 | 24487.3521
2020-04-29 17:00 | 7.0297 | 7.3994 | 197.8796 | 2360.2261 | 35403.3918
2020-04-29 18:00 | 7.2247 | 7.6047 | 211.8477 | 2564.7212 | 38470.8174
2020-04-29 19:00 | 6.7024 | 7.0549 | 223.5852 | 2039.1786 | 30587.6796
2020-04-29 20:00 | 6.2491 | 6.5778 | 227.0731 | 1645.1728 | 24677.5917
2020-04-29 21:00 | 5.8654 | 6.1739 | 224.0121 | 1353.7171 | 20305.7565
2020-04-29 22:00 | 4.7919 | 5.0439 | 217.4802 | 707.0475 | 10605.7127
2020-04-29 23:00 | 5.2359 | 5.5112 | 206.141 | 942.6556 | 14139.8336
2020-04-30 00:00 | 5.5999 | 5.8945 | 203.1594 | 1169.5264 | 17542.8958
2020-04-30 01:00 | 6.1105 | 6.4319 | 205.5332 | 1534.3232 | 23014.8486
2020-04-30 02:00 | 6.4732 | 6.8136 | 210.6523 | 1836.6695 | 27550.0422
2020-04-30 03:00 | 6.1205 | 6.4424 | 214.0433 | 1541.7077 | 23125.615
2020-04-30 04:00 | 5.4515 | 5.7382 | 213.7551 | 1077.0136 | 16155.2044
2020-04-30 05:00 | 3.8343 | 4.036 | 214.8338 | 310.6555 | 4659.8332
2020-04-30 06:00 | 3.1351 | 3.3 | 220.0705 | 112.1921 | 1682.8821
2020-04-30 07:00 | 2.9094 | 3.0624 | 220.4504 | 61.3477 | 920.2161
2020-04-30 08:00 | 3.256 | 3.4273 | 209.9767 | 139.4338 | 2091.5077
2020-04-30 09:00 | 4.3197 | 4.5469 | 209.2301 | 493.8042 | 7407.0634
2020-04-30 10:00 | 4.3825 | 4.613 | 227.5094 | 521.6799 | 7825.1988
2020-04-30 11:00 | 4.6207 | 4.8637 | 240.8469 | 627.4752 | 9412.128
2020-04-30 12:00 | 4.2996 | 4.5257 | 250.0946 | 484.8461 | 7272.6921
2020-04-30 13:00 | 3.4381 | 3.6189 | 254.3676 | 189.0039 | 2835.0585
2020-04-30 14:00 | 2.6286 | 2.7668 | 263.8093 | 0 | 0
2020-04-30 15:00 | 3.8634 | 4.0666 | 323.5823 | 321.4259 | 4821.3879
2020-04-30 16:00 | 5.5229 | 5.8133 | 337.663 | 1121.4991 | 16822.4865
2020-04-30 17:00 | 4.1065 | 4.3225 | 2.2865 | 411.5054 | 6172.5815
2020-04-30 18:00 | 2.9233 | 3.0771 | 32.0111 | 64.4944 | 967.4163
2020-04-30 19:00 | 2.6352 | 2.7738 | 30.7245 | 0 | 0
2020-04-30 20:00 | 3.8847 | 4.089 | 9.7045 | 329.3296 | 4939.9444
2020-04-30 21:00 | 5.6876 | 5.9867 | 9.6964 | 1224.1523 | 18362.2843
2020-04-30 22:00 | 6.0346 | 6.3519 | 21.8225 | 1478.3642 | 22175.463
2020-04-30 23:00 | 5.7119 | 6.0123 | 26.8547 | 1240.6207 | 18609.3104
2020-05-01 00:00 | 5.2107 | 5.4847 | 25.7447 | 928.3393 | 13925.0897
2020-05-01 01:00 | 4.7928 | 5.0449 | 23.2883 | 707.5428 | 10613.1419
2020-05-01 02:00 | 4.2063 | 4.4275 | 22.0979 | 448.4748 | 6727.1214
2020-05-01 03:00 | 3.6153 | 3.8055 | 21.9888 | 242.3662 | 3635.4926
2020-05-01 04:00 | 3.3662 | 3.5432 | 25.1129 | 167.3628 | 2510.4415
2020-05-01 05:00 | 3.2835 | 3.4562 | 29.9173 | 145.6218 | 2184.3274
2020-05-01 06:00 | 3.1371 | 3.3021 | 36.0745 | 112.6442 | 1689.663
2020-05-01 07:00 | 2.8014 | 2.9487 | 42.0697 | 0 | 0
2020-05-01 08:00 | 2.5926 | 2.729 | 51.3868 | 0 | 0
2020-05-01 09:00 | 2.4202 | 2.5475 | 62.3124 | 0 | 0
2020-05-01 10:00 | 2.3235 | 2.4457 | 91.5109 | 0 | 0
2020-05-01 11:00 | 2.2064 | 2.3224 | 110.3767 | 0 | 0
2020-05-01 12:00 | 2.0491 | 2.1568 | 117.9396 | 0 | 0
2020-05-01 13:00 | 2.0555 | 2.1636 | 104.5436 | 0 | 0
2020-05-01 14:00 | 2.8709 | 3.0219 | 87.0612 | 52.6823 | 790.2344
2020-05-01 15:00 | 3.5724 | 3.7603 | 78.2878 | 229.4506 | 3441.7597
2020-05-01 16:00 | 4.6042 | 4.8463 | 74.4282 | 620.1597 | 9302.3949
2020-05-01 17:00 | 6.1994 | 6.5255 | 84.6089 | 1602.6864 | 24040.2955
2020-05-01 18:00 | 7.2992 | 7.6831 | 98.9038 | 2647.6839 | 39715.2581
2020-05-01 19:00 | 6.88 | 7.2418 | 104.5099 | 2213.3688 | 33200.532
2020-05-01 20:00 | 6.7715 | 7.1276 | 109.3002 | 2106.9213 | 31603.8198
2020-05-01 21:00 | 7.0944 | 7.4675 | 108.8257 | 2423.694 | 36355.4096
2020-05-01 22:00 | 7.1501 | 7.5262 | 118.5247 | 2481.7197 | 37225.7949
2020-05-01 23:00 | 7.1929 | 7.5712 | 122.6067 | 2529.3519 | 37940.2782
2020-05-02 00:00 | 7.0682 | 7.44 | 127.2191 | 2398.0454 | 35970.6808
2020-05-02 01:00 | 6.4153 | 6.7527 | 130.4 | 1787.2195 | 26808.2924
2020-05-02 02:00 | 6.0335 | 6.3508 | 129.8086 | 1477.5618 | 22163.4267
2020-05-02 03:00 | 5.8338 | 6.1406 | 132.9353 | 1330.4176 | 19956.2647
2020-05-02 04:00 | 5.6317 | 5.9279 | 134.937 | 1189.3128 | 17839.6918
2020-05-02 05:00 | 5.1423 | 5.4128 | 139.3458 | 892.2222 | 13383.333
2020-05-02 06:00 | 4.5346 | 4.7731 | 142.3689 | 589.2306 | 8838.4588
2020-05-02 07:00 | 4.0881 | 4.3031 | 148.2419 | 404.6924 | 6070.3854
2020-05-02 08:00 | 3.8203 | 4.0212 | 153.6808 | 305.4622 | 4581.9326
2020-05-02 09:00 | 4.3119 | 4.5386 | 150.838 | 490.3101 | 7354.652
2020-05-02 10:00 | 4.0677 | 4.2817 | 147.9744 | 397.143 | 5957.1449
2020-05-02 11:00 | 4.3959 | 4.6271 | 153.4323 | 527.6572 | 7914.8583
2020-05-02 12:00 | 3.6635 | 3.8562 | 164.7374 | 256.8772 | 3853.1581
2020-05-02 13:00 | 4.1559 | 4.3745 | 204.7504 | 429.8227 | 6447.3411
2020-05-02 14:00 | 3.6679 | 3.8608 | 217.3826 | 258.179 | 3872.685
2020-05-02 15:00 | 2.4764 | 2.6066 | 192.8582 | 0 | 0
2020-05-02 16:00 | 1.8362 | 1.9327 | 157.7232 | 0 | 0
2020-05-02 17:00 | 3.1441 | 3.3095 | 160.198 | 114.2225 | 1713.3371
2020-05-02 18:00 | 3.443 | 3.6241 | 166.0954 | 190.4946 | 2857.4185
2020-05-02 19:00 | 3.7659 | 3.964 | 162.4098 | 287.7078 | 4315.6172
2020-05-02 20:00 | 3.4233 | 3.6034 | 193.9643 | 184.5668 | 2768.5013
2020-05-02 21:00 | 3.5065 | 3.6909 | 225.7888 | 209.5965 | 3143.9482
2020-05-02 22:00 | 3.8965 | 4.1014 | 240.3087 | 333.7055 | 5005.5818
2020-05-02 23:00 | 2.503 | 2.6347 | 239.6933 | 0 | 0
2020-05-03 00:00 | 1.2323 | 1.2971 | 263.2952 | 0 | 0
2020-05-03 01:00 | 1.5618 | 1.6439 | 298.204 | 0 | 0
2020-05-03 02:00 | 1.7406 | 1.8322 | 310.9418 | 0 | 0
2020-05-03 03:00 | 1.8978 | 1.9976 | 333.123 | 0 | 0
2020-05-03 04:00 | 2.0862 | 2.196 | 347.3847 | 0 | 0
2020-05-03 05:00 | 2.0546 | 2.1627 | 1.2073 | 0 | 0
2020-05-03 06:00 | 1.9839 | 2.0883 | 15.5883 | 0 | 0
2020-05-03 07:00 | 2.0058 | 2.1113 | 25.7448 | 0 | 0
2020-05-03 08:00 | 2.1213 | 2.2328 | 31.8328 | 0 | 0
2020-05-03 09:00 | 2.0873 | 2.1971 | 27.103 | 0 | 0
2020-05-03 10:00 | 2.1393 | 2.2519 | 33.8036 | 0 | 0
2020-05-03 11:00 | 1.9832 | 2.0875 | 35.3104 | 0 | 0
2020-05-03 12:00 | 1.774 | 1.8673 | 35.9661 | 0 | 0
2020-05-03 13:00 | 1.5399 | 1.6209 | 4.2996 | 0 | 0
2020-05-03 14:00 | 2.2101 | 2.3263 | 350.1178 | 0 | 0
2020-05-03 15:00 | 3.2101 | 3.3789 | 350.8922 | 129.0927 | 1936.3907
2020-05-03 16:00 | 3.3002 | 3.4738 | 28.4698 | 149.3969 | 2240.9531
2020-05-03 17:00 | 4.0569 | 4.2703 | 48.0201 | 393.1315 | 5896.9721
2020-05-03 18:00 | 4.0041 | 4.2147 | 44.627 | 373.5734 | 5603.6013
2020-05-03 19:00 | 4.7655 | 5.0161 | 29.4318 | 693.0824 | 10396.2355
2020-05-03 20:00 | 5.2316 | 5.5067 | 24.1831 | 939.9742 | 14099.6132
2020-05-03 21:00 | 5.1177 | 5.3869 | 30.3709 | 879.2094 | 13188.1406
2020-05-03 22:00 | 4.8126 | 5.0658 | 56.3536 | 718.0115 | 10770.1723
2020-05-03 23:00 | 4.2737 | 4.4985 | 51.0683 | 473.4622 | 7101.9332
2020-05-04 00:00 | 3.9473 | 4.1549 | 40.8846 | 352.5314 | 5287.9707
2020-05-04 01:00 | 4.046 | 4.2588 | 29.1996 | 389.1118 | 5836.6776
2020-05-04 02:00 | 4.5161 | 4.7537 | 18.5399 | 581.0423 | 8715.6339
2020-05-04 03:00 | 4.7968 | 5.0491 | 15.3889 | 709.6568 | 10644.8513
2020-05-04 04:00 | 4.3243 | 4.5518 | 16.4343 | 495.8456 | 7437.6835
2020-05-04 05:00 | 3.075 | 3.2367 | 18.2902 | 98.6596 | 1479.8937
2020-05-04 06:00 | 2.6435 | 2.7826 | 19.3763 | 0 | 0
2020-05-04 07:00 | 2.7316 | 2.8753 | 11.8615 | 0 | 0
2020-05-04 08:00 | 2.6635 | 2.8036 | 13.1592 | 0 | 0
2020-05-04 09:00 | 2.3611 | 2.4852 | 12.223 | 0 | 0
2020-05-04 10:00 | 1.8038 | 1.8987 | 356.9426 | 0 | 0
2020-05-04 11:00 | 1.2414 | 1.3067 | 336.782 | 0 | 0
2020-05-04 12:00 | 1.8763 | 1.975 | 311.1004 | 0 | 0
2020-05-04 13:00 | 1.3138 | 1.3829 | 324.9208 | 0 | 0
2020-05-04 14:00 | 5.1651 | 5.4368 | 291.9704 | 904.2752 | 13564.1275
2020-05-04 15:00 | 4.7747 | 5.0258 | 315.4455 | 697.9754 | 10469.6312
2020-05-04 16:00 | 4.3081 | 4.5347 | 321.744 | 488.6306 | 7329.4586
2020-05-04 17:00 | 5.3105 | 5.5898 | 318.966 | 989.1868 | 14837.8015
2020-05-04 18:00 | 6.1211 | 6.443 | 322.9198 | 1542.0932 | 23131.3973
2020-05-04 19:00 | 5.7173 | 6.018 | 325.9061 | 1244.6346 | 18669.5183
2020-05-04 20:00 | 5.2242 | 5.499 | 323.5285 | 935.4764 | 14032.1465
2020-05-04 21:00 | 5.1997 | 5.4731 | 316.1301 | 922.5155 | 13837.7321
2020-05-04 22:00 | 5.3439 | 5.625 | 314.9395 | 1009.9797 | 15149.6954
2020-05-04 23:00 | 5.5608 | 5.8533 | 313.1055 | 1145.1361 | 17177.0408
2020-05-05 00:00 | 5.7061 | 6.0062 | 310.7901 | 1236.3609 | 18545.4129
2020-05-05 01:00 | 5.4947 | 5.7837 | 310.5809 | 1103.9302 | 16558.9528
2020-05-05 02:00 | 5.6718 | 5.9701 | 305.1389 | 1214.3041 | 18214.562
2020-05-05 03:00 | 5.7356 | 6.0373 | 304.1932 | 1258.0949 | 18871.4242
2020-05-05 04:00 | 5.4679 | 5.7555 | 301.1736 | 1087.2302 | 16308.4532
2020-05-05 05:00 | 5.3279 | 5.6081 | 298.6876 | 999.9873 | 14999.809
2020-05-05 06:00 | 5.7228 | 6.0238 | 306.015 | 1248.6556 | 18729.8344
2020-05-05 07:00 | 4.8012 | 5.0537 | 307.427 | 711.9712 | 10679.5676
2020-05-05 08:00 | 4.4896 | 4.7257 | 305.3931 | 569.2664 | 8538.9962
2020-05-05 09:00 | 4.4001 | 4.6315 | 306.8168 | 529.4911 | 7942.3658
2020-05-05 10:00 | 4.6071 | 4.8494 | 303.3933 | 621.4527 | 9321.791
2020-05-05 11:00 | 4.2539 | 4.4776 | 303.5064 | 466.1291 | 6991.9367
2020-05-05 12:00 | 4.0479 | 4.2608 | 294.9435 | 389.7966 | 5846.9492
2020-05-05 13:00 | 4.139 | 4.3567 | 281.9213 | 423.571 | 6353.5643
2020-05-05 14:00 | 4.4569 | 4.6913 | 280.5118 | 554.7366 | 8321.0485
2020-05-05 15:00 | 4.7166 | 4.9646 | 279.6424 | 670.0822 | 10051.2328
2020-05-05 16:00 | 4.4767 | 4.7122 | 285.6113 | 563.5286 | 8452.9283
2020-05-05 17:00 | 4.3274 | 4.555 | 292.4588 | 497.227 | 7458.4046
2020-05-05 18:00 | 4.02 | 4.2314 | 300.7661 | 379.4512 | 5691.7683
2020-05-05 19:00 | 3.3867 | 3.5648 | 318.5045 | 173.5397 | 2603.0962
2020-05-05 20:00 | 2.6492 | 2.7886 | 351.8854 | 0 | 0
2020-05-05 21:00 | 1.7852 | 1.8791 | 6.7318 | 0 | 0
2020-05-05 22:00 | 0.66049 | 0.69522 | 291.2481 | 0 | 0
2020-05-05 23:00 | 1.5517 | 1.6333 | 222.9876 | 0 | 0
2020-05-06 00:00 | 2.7334 | 2.8772 | 208.4256 | 0 | 0
2020-05-06 01:00 | 4.7579 | 5.0082 | 227.4294 | 689.104 | 10336.5604
2020-05-06 02:00 | 6.2361 | 6.5641 | 251.6621 | 1634.011 | 24510.1655
2020-05-06 03:00 | 6.9551 | 7.321 | 267.0315 | 2287.1272 | 34306.9087
2020-05-06 04:00 | 6.6503 | 7.0001 | 277.3279 | 1988.1052 | 29821.5776
2020-05-06 05:00 | 6.7861 | 7.1431 | 285.1637 | 2121.3287 | 31819.9302
2020-05-06 06:00 | 6.9935 | 7.3613 | 280.0667 | 2324.7033 | 34870.5502
2020-05-06 07:00 | 5.8513 | 6.1591 | 273.7687 | 1343.3602 | 20150.4026
2020-05-06 08:00 | 4.8411 | 5.0957 | 278.0154 | 733.0422 | 10995.6332
2020-05-06 09:00 | 4.6474 | 4.8918 | 274.79 | 639.3565 | 9590.3479
2020-05-06 10:00 | 4.6753 | 4.9212 | 253.8676 | 651.7444 | 9776.1665
2020-05-06 11:00 | 3.8862 | 4.0906 | 249.083 | 329.8901 | 4948.352
2020-05-06 12:00 | 3.6837 | 3.8775 | 250.2529 | 262.9531 | 3944.2959
2020-05-06 13:00 | 4.0571 | 4.2704 | 244.2658 | 393.1971 | 5897.957
2020-05-06 14:00 | 3.9559 | 4.1639 | 238.7057 | 355.6994 | 5335.4908
2020-05-06 15:00 | 3.2681 | 3.44 | 242.3923 | 142.1679 | 2132.5181
2020-05-06 16:00 | 2.7783 | 2.9244 | 260.8831 | 0 | 0
2020-05-06 17:00 | 2.6587 | 2.7985 | 290.5515 | 0 | 0
2020-05-06 18:00 | 2.9483 | 3.1033 | 323.2278 | 70.1142 | 1051.7128
2020-05-06 19:00 | 3.2942 | 3.4675 | 345.5997 | 148.0434 | 2220.6514
2020-05-06 20:00 | 3.2957 | 3.4691 | 2.4011 | 148.3828 | 2225.7422
2020-05-06 21:00 | 2.8854 | 3.0371 | 29.3441 | 55.9442 | 839.1631
2020-05-06 22:00 | 1.984 | 2.0884 | 86.7136 | 0 | 0
2020-05-06 23:00 | 0.84518 | 0.88964 | 103.3644 | 0 | 0
2020-05-07 00:00 | 0.52221 | 0.54967 | 256.1404 | 0 | 0
2020-05-07 01:00 | 1.9079 | 2.0082 | 273.1212 | 0 | 0
2020-05-07 02:00 | 3.5856 | 3.7742 | 265.2122 | 233.4074 | 3501.1115
2020-05-07 03:00 | 4.5917 | 4.8332 | 258.3181 | 614.6058 | 9219.0871
2020-05-07 04:00 | 5.0213 | 5.2854 | 252.3479 | 828.2718 | 12424.0774
2020-05-07 05:00 | 5.8377 | 6.1447 | 245.3639 | 1333.3169 | 19999.7528
2020-05-07 06:00 | 6.188 | 6.5135 | 238.4015 | 1592.9677 | 23894.5153
2020-05-07 07:00 | 6.1906 | 6.5162 | 229.8162 | 1595.1694 | 23927.5414
2020-05-07 08:00 | 5.7013 | 6.0012 | 232.0255 | 1232.8108 | 18492.1626
2020-05-07 09:00 | 5.0299 | 5.2944 | 244.9528 | 832.7945 | 12491.9174
2020-05-07 10:00 | 5.2848 | 5.5627 | 290.9978 | 973.1446 | 14597.1688
2020-05-07 11:00 | 7.1594 | 7.536 | 314.1665 | 2492.0719 | 37381.0782
2020-05-07 12:00 | 6.9369 | 7.3017 | 324.0036 | 2269.2213 | 34038.3202
2020-05-07 13:00 | 6.0675 | 6.3866 | 333.8316 | 1502.6172 | 22539.258
2020-05-07 14:00 | 6.8314 | 7.1907 | 341.2754 | 2165.6997 | 32485.4949
2020-05-07 15:00 | 6.7243 | 7.078 | 342.4549 | 2060.7067 | 30910.6008
2020-05-07 16:00 | 7.1045 | 7.4781 | 342.3954 | 2433.6319 | 36504.4782
2020-05-07 17:00 | 7.0798 | 7.4521 | 339.3454 | 2409.3687 | 36140.5298
2020-05-07 18:00 | 7.1132 | 7.4873 | 338.0139 | 2442.19 | 36632.8501
2020-05-07 19:00 | 7.2167 | 7.5963 | 343.9236 | 2555.8973 | 38338.46
2020-05-07 20:00 | 6.8545 | 7.215 | 347.0034 | 2188.4029 | 32826.0429
2020-05-07 21:00 | 6.7529 | 7.1081 | 340.778 | 2088.7585 | 31331.3774
2020-05-07 22:00 | 7.431 | 7.8218 | 331.7312 | 2794.4721 | 41917.0818
2020-05-07 23:00 | 8.4165 | 8.8592 | 327.0984 | 3951.1546 | 59267.3193
2020-05-08 00:00 | 8.838 | 9.3028 | 330.7158 | 4433.9879 | 66509.8178
2020-05-08 01:00 | 8.7102 | 9.1683 | 332.5342 | 4290.0707 | 64351.06
2020-05-08 02:00 | 8.4937 | 8.9404 | 330.4039 | 4042.8168 | 60642.2522
2020-05-08 03:00 | 8.3862 | 8.8273 | 327.441 | 3915.1612 | 58727.4185
2020-05-08 04:00 | 7.9963 | 8.4168 | 325.2443 | 3452.3508 | 51785.2622
2020-05-08 05:00 | 6.9559 | 7.3217 | 322.312 | 2287.8286 | 34317.4285
2020-05-08 06:00 | 6.6507 | 7.0005 | 326.2953 | 1988.497 | 29827.455
2020-05-08 07:00 | 6.6837 | 7.0352 | 328.9726 | 2020.8511 | 30312.7666
2020-05-08 08:00 | 9.2266 | 9.7119 | 338.1691 | 4819.1909 | 72287.863
2020-05-08 09:00 | 9.1525 | 9.6339 | 337.1985 | 4755.0799 | 71326.1981
2020-05-08 10:00 | 7.5024 | 7.897 | 332.7828 | 2874.0593 | 43110.8891
2020-05-08 11:00 | 7.4426 | 7.834 | 328.8785 | 2807.3801 | 42110.7011
2020-05-08 12:00 | 7.398 | 7.7871 | 326.5733 | 2757.7788 | 41366.6818
2020-05-08 13:00 | 6.9445 | 7.3097 | 325.3757 | 2276.6499 | 34149.748
2020-05-08 14:00 | 6.7821 | 7.1388 | 327.1747 | 2117.3343 | 31760.0138
2020-05-08 15:00 | 5.9711 | 6.2851 | 330.0949 | 1431.5971 | 21473.9563
2020-05-08 16:00 | 4.799 | 5.0514 | 330.1354 | 710.7824 | 10661.7363
2020-05-08 17:00 | 4.513 | 4.7504 | 324.8741 | 579.6492 | 8694.7384
2020-05-08 18:00 | 4.2486 | 4.4721 | 325.9953 | 464.1675 | 6962.5121
2020-05-08 19:00 | 3.7685 | 3.9667 | 337.282 | 288.4796 | 4327.194
2020-05-08 20:00 | 3.3482 | 3.5243 | 356.0989 | 161.9619 | 2429.4284
2020-05-08 21:00 | 2.8905 | 3.0425 | 18.8708 | 57.0898 | 856.3474
2020-05-08 22:00 | 1.2304 | 1.2951 | 87.5044 | 0 | 0
2020-05-08 23:00 | 1.2859 | 1.3535 | 138.8118 | 0 | 0
2020-05-09 00:00 | 1.288 | 1.3557 | 201.1941 | 0 | 0
2020-05-09 01:00 | 2.2722 | 2.3917 | 257.3038 | 0 | 0
2020-05-09 02:00 | 3.8027 | 4.0027 | 282.0816 | 298.9637 | 4484.4554
2020-05-09 03:00 | 5.0235 | 5.2877 | 295.7097 | 829.4354 | 12441.5307
2020-05-09 04:00 | 5.1441 | 5.4147 | 303.8455 | 893.1699 | 13397.5481
2020-05-09 05:00 | 4.1728 | 4.3923 | 312.3708 | 436.0903 | 6541.3542
2020-05-09 06:00 | 3.2059 | 3.3745 | 323.0069 | 128.1452 | 1922.1778
2020-05-09 07:00 | 3.113 | 3.2767 | 338.664 | 107.2155 | 1608.2322
2020-05-09 08:00 | 3.2658 | 3.4376 | 351.7126 | 141.6439 | 2124.6588
2020-05-09 09:00 | 3.8577 | 4.0606 | 347.6195 | 319.3291 | 4789.9363
2020-05-09 10:00 | 3.0208 | 3.1796 | 327.7937 | 86.4417 | 1296.6258
2020-05-09 11:00 | 4.3073 | 4.5339 | 328.3688 | 488.2911 | 7324.3664
2020-05-09 12:00 | 4.506 | 4.743 | 326.6919 | 576.5303 | 8647.9538
2020-05-09 13:00 | 4.929 | 5.1883 | 326.551 | 779.5141 | 11692.7113
2020-05-09 14:00 | 4.4477 | 4.6817 | 326.8908 | 550.6661 | 8259.9921
2020-05-09 15:00 | 3.6782 | 3.8717 | 327.7335 | 261.3016 | 3919.5241
2020-05-09 16:00 | 2.3685 | 2.4931 | 312.0775 | 0 | 0
2020-05-09 17:00 | 1.9902 | 2.0949 | 273.2423 | 0 | 0
2020-05-09 18:00 | 2.8685 | 3.0194 | 245.0617 | 52.1477 | 782.2153
2020-05-09 19:00 | 3.9963 | 4.2065 | 234.4449 | 370.6712 | 5560.0678
2020-05-09 20:00 | 5.3544 | 5.636 | 234.8341 | 1016.5254 | 15247.8804
2020-05-09 21:00 | 6.2645 | 6.594 | 237.5227 | 1658.3093 | 24874.6394
2020-05-09 22:00 | 6.741 | 7.0955 | 248.4451 | 2077.0319 | 31155.4783
2020-05-09 23:00 | 6.9621 | 7.3283 | 254.6033 | 2293.9771 | 34409.6561
2020-05-10 00:00 | 7.2127 | 7.5921 | 260.4373 | 2551.4029 | 38271.0429
2020-05-10 01:00 | 7.1569 | 7.5333 | 267.7836 | 2489.2514 | 37338.7706
2020-05-10 02:00 | 6.9445 | 7.3097 | 274.9832 | 2276.6581 | 34149.8721
2020-05-10 03:00 | 6.791 | 7.1482 | 282.9291 | 2126.083 | 31891.2445
2020-05-10 04:00 | 6.0581 | 6.3767 | 290.8347 | 1495.6783 | 22435.175
2020-05-10 05:00 | 4.7298 | 4.9786 | 297.3671 | 675.9685 | 10139.5277
2020-05-10 06:00 | 3.7187 | 3.9143 | 304.1269 | 273.4892 | 4102.3385
2020-05-10 07:00 | 3.5611 | 3.7484 | 308.7978 | 226.0549 | 3390.8239
2020-05-10 08:00 | 3.6845 | 3.8783 | 313.3849 | 263.2032 | 3948.0473
2020-05-10 09:00 | 4.5854 | 4.8266 | 312.4882 | 611.8198 | 9177.2964
2020-05-10 10:00 | 4.6623 | 4.9076 | 299.0909 | 645.9899 | 9689.8487
2020-05-10 11:00 | 4.812 | 5.0651 | 295.046 | 717.677 | 10765.1551
2020-05-10 12:00 | 5.0215 | 5.2856 | 295.8811 | 828.3732 | 12425.5987
2020-05-10 13:00 | 5.0816 | 5.3489 | 300.9128 | 860.1565 | 12902.3469
2020-05-10 14:00 | 4.8407 | 5.0953 | 306.5314 | 732.8462 | 10992.6928
2020-05-10 15:00 | 4.1595 | 4.3783 | 312.3591 | 431.1504 | 6467.2563
2020-05-10 16:00 | 2.5157 | 2.648 | 319.8564 | 0 | 0
2020-05-10 17:00 | 1.2361 | 1.3012 | 304.9754 | 0 | 0
2020-05-10 18:00 | 0.96283 | 1.0135 | 235.7423 | 0 | 0
2020-05-10 19:00 | 1.9739 | 2.0777 | 209.1413 | 0 | 0
2020-05-10 20:00 | 3.1632 | 3.3296 | 217.8733 | 118.5312 | 1777.9685
2020-05-10 21:00 | 3.9157 | 4.1217 | 227.3535 | 340.8214 | 5112.3208
2020-05-10 22:00 | 4.065 | 4.2788 | 255.1862 | 396.142 | 5942.1304
2020-05-10 23:00 | 4.2461 | 4.4695 | 246.0531 | 463.253 | 6948.7957
2020-05-11 00:00 | 4.7291 | 4.9778 | 232.4952 | 675.6323 | 10134.4848
2020-05-11 01:00 | 5.1253 | 5.3949 | 218.079 | 883.2433 | 13248.6499
2020-05-11 02:00 | 5.9254 | 6.237 | 209.3177 | 1397.9122 | 20968.6834
2020-05-11 03:00 | 6.6281 | 6.9767 | 202.8805 | 1969.1197 | 29536.7961
2020-05-11 04:00 | 6.971 | 7.3377 | 196.3441 | 2302.7 | 34540.5001
2020-05-11 05:00 | 7.0875 | 7.4603 | 191.2615 | 2417.0093 | 36255.1393
2020-05-11 06:00 | 6.0104 | 6.3265 | 186.9855 | 1460.5641 | 21908.4617
2020-05-11 07:00 | 6.1057 | 6.4268 | 187.0397 | 1530.7598 | 22961.3968
2020-05-11 08:00 | 6.64 | 6.9892 | 192.0556 | 1979.2573 | 29688.8598
2020-05-11 09:00 | 6.9409 | 7.3059 | 197.9907 | 2273.1306 | 34096.9588
2020-05-11 10:00 | 5.5811 | 5.8746 | 192.7586 | 1157.7651 | 17366.4763
2020-05-11 11:00 | 4.8647 | 5.1206 | 198.1893 | 745.5454 | 11183.1807
2020-05-11 12:00 | 5.2764 | 5.554 | 193.0093 | 967.9453 | 14519.1798
2020-05-11 13:00 | 6.4727 | 6.8132 | 194.6376 | 1836.3025 | 27544.5375
2020-05-11 14:00 | 7.4009 | 7.7901 | 202.6723 | 2760.9414 | 41414.1206
2020-05-11 15:00 | 7.2708 | 7.6533 | 202.3714 | 2616.1462 | 39242.1923
2020-05-11 16:00 | 7.233 | 7.6134 | 194.1643 | 2574.0015 | 38610.0224
2020-05-11 17:00 | 8.2108 | 8.6426 | 184.661 | 3706.8754 | 55603.1316
2020-05-11 18:00 | 9.3946 | 9.8887 | 179.4118 | 4964.5019 | 74467.5292
2020-05-11 19:00 | 10.1351 | 10.6682 | 178.1326 | 5412.2451 | 81183.6771
2020-05-11 20:00 | 10.8662 | 11.4377 | 179.9461 | 5637.9103 | 84568.654
2020-05-11 21:00 | 11.173 | 11.7606 | 181.8838 | 5676.4971 | 85147.4563
2020-05-11 22:00 | 11.0407 | 11.6214 | 185.8249 | 5663.4123 | 84951.1843
2020-05-11 23:00 | 10.7272 | 11.2914 | 187.1581 | 5604.864 | 84072.96
2020-05-12 00:00 | 10.4361 | 10.9849 | 189.7 | 5533.2488 | 82998.7324
2020-05-12 01:00 | 9.4457 | 9.9425 | 198.0689 | 5008.7684 | 75131.5258
2020-05-12 02:00 | 8.8567 | 9.3225 | 194.4367 | 4455.1124 | 66826.6855
2020-05-12 03:00 | 9.67 | 10.1786 | 190.8573 | 5160.3263 | 77404.8949
2020-05-12 04:00 | 9.6098 | 10.1152 | 201.0145 | 5123.3057 | 76849.5851
2020-05-12 05:00 | 9.4537 | 9.9509 | 209.3527 | 5015.6352 | 75234.5276
2020-05-12 06:00 | 8.8491 | 9.3145 | 210.7099 | 4446.4968 | 66697.4513
2020-05-12 07:00 | 7.8473 | 8.26 | 217.4067 | 3275.7371 | 49136.0563
2020-05-12 08:00 | 9.9819 | 10.5069 | 249.4862 | 5350.6516 | 80259.7743
2020-05-12 09:00 | 10.8627 | 11.434 | 273.5121 | 5637.0925 | 84556.3869
2020-05-12 10:00 | 12.2466 | 12.8907 | 282.3818 | 5700 | 85500
2020-05-12 11:00 | 12.872 | 13.549 | 291.7727 | 5700 | 85500
2020-05-12 12:00 | 12.7837 | 13.4561 | 301.275 | 5700 | 85500
2020-05-12 13:00 | 13.004 | 13.688 | 307.2233 | 5700 | 85500
2020-05-12 14:00 | 13.0072 | 13.6913 | 310.3692 | 5700 | 85500
2020-05-12 15:00 | 12.8104 | 13.4842 | 314.3095 | 5700 | 85500
2020-05-12 16:00 | 12.3287 | 12.9771 | 318.2098 | 5700 | 85500
2020-05-12 17:00 | 11.5209 | 12.1268 | 321.4607 | 5699.2537 | 85488.8052
2020-05-12 18:00 | 9.8823 | 10.4021 | 322.7751 | 5290.8063 | 79362.0942
2020-05-12 19:00 | 8.7372 | 9.1967 | 323.6441 | 4320.4649 | 64806.974
2020-05-12 20:00 | 8.1761 | 8.6061 | 323.7195 | 3665.6705 | 54985.0582
2020-05-12 21:00 | 7.6587 | 8.0615 | 321.8586 | 3052.2529 | 45783.794
2020-05-12 22:00 | 6.4039 | 6.7407 | 313.8554 | 1777.4461 | 26661.691
2020-05-12 23:00 | 5.9088 | 6.2196 | 308.9903 | 1385.7227 | 20785.8408
2020-05-13 00:00 | 5.5714 | 5.8644 | 301.113 | 1151.7199 | 17275.7981
2020-05-13 01:00 | 5.324 | 5.6041 | 292.8104 | 997.6057 | 14964.085
2020-05-13 02:00 | 5.1061 | 5.3746 | 286.853 | 873.0548 | 13095.8225
2020-05-13 03:00 | 5.021 | 5.2851 | 277.6613 | 828.1339 | 12422.0083
2020-05-13 04:00 | 4.5169 | 4.7545 | 265.5193 | 581.392 | 8720.8803
2020-05-13 05:00 | 4.0225 | 4.2341 | 262.8866 | 380.3984 | 5705.9762
2020-05-13 06:00 | 3.4605 | 3.6425 | 257.7996 | 195.7503 | 2936.2547
2020-05-13 07:00 | 3.126 | 3.2904 | 241.8496 | 110.1542 | 1652.3126
2020-05-13 08:00 | 3.4614 | 3.6434 | 234.63 | 196.0188 | 2940.2817
2020-05-13 09:00 | 4.108 | 4.3241 | 224.4811 | 412.0781 | 6181.1722
2020-05-13 10:00 | 4.0959 | 4.3113 | 213.3951 | 407.5865 | 6113.7968
2020-05-13 11:00 | 4.8312 | 5.0853 | 208.7139 | 727.8273 | 10917.41
2020-05-13 12:00 | 5.6648 | 5.9627 | 203.4174 | 1209.919 | 18148.7851
2020-05-13 13:00 | 6.2529 | 6.5818 | 202.8671 | 1648.4104 | 24726.1554
2020-05-13 14:00 | 6.7108 | 7.0637 | 209.8092 | 2047.3935 | 30710.9026
2020-05-13 15:00 | 7.3338 | 7.7196 | 218.6394 | 2686.2926 | 40294.3894
2020-05-13 16:00 | 6.1603 | 6.4843 | 215.8735 | 1571.0138 | 23565.2072
2020-05-13 17:00 | 5.6586 | 5.9562 | 206.799 | 1206.0647 | 18090.9703
2020-05-13 18:00 | 6.2141 | 6.5409 | 197.5899 | 1615.2056 | 24228.0839
2020-05-13 19:00 | 6.9154 | 7.2791 | 182.6579 | 2248.1314 | 33721.9707
2020-05-13 20:00 | 7.378 | 7.766 | 180.9999 | 2735.44 | 41031.5997
2020-05-13 21:00 | 7.378 | 7.7661 | 183.1718 | 2735.5266 | 41032.899
2020-05-13 22:00 | 6.0128 | 6.329 | 184.6035 | 1462.3218 | 21934.8272
2020-05-13 23:00 | 5.3529 | 5.6344 | 185.5465 | 1015.5925 | 15233.8869
2020-05-14 00:00 | 4.6201 | 4.8631 | 191.3351 | 627.2255 | 9408.382
2020-05-14 01:00 | 4.068 | 4.282 | 182.3142 | 397.2537 | 5958.805
2020-05-14 02:00 | 3.7161 | 3.9115 | 167.4138 | 272.6983 | 4090.4739
2020-05-14 03:00 | 4.1889 | 4.4092 | 152.1847 | 442.0416 | 6630.6239
2020-05-14 04:00 | 4.5397 | 4.7784 | 148.609 | 591.4916 | 8872.3741
2020-05-14 05:00 | 3.982 | 4.1914 | 151.4895 | 365.3772 | 5480.6583
2020-05-14 06:00 | 3.3393 | 3.515 | 145.6371 | 159.2785 | 2389.1768
2020-05-14 07:00 | 1.5456 | 1.6269 | 110.4943 | 0 | 0
2020-05-14 08:00 | 1.4124 | 1.4867 | 53.0792 | 0 | 0
2020-05-14 09:00 | 1.6099 | 1.6946 | 43.8422 | 0 | 0
2020-05-14 10:00 | 0.80567 | 0.84805 | 25.1935 | 0 | 0
2020-05-14 11:00 | 2.2821 | 2.4022 | 3.5301 | 0 | 0
2020-05-14 12:00 | 4.3961 | 4.6274 | 355.5175 | 527.7419 | 7916.1289
2020-05-14 13:00 | 6.297 | 6.6281 | 354.4172 | 1686.0536 | 25290.8043
2020-05-14 14:00 | 7.5909 | 7.9902 | 346.893 | 2972.6206 | 44589.3089
2020-05-14 15:00 | 8.0426 | 8.4656 | 342.9123 | 3507.2343 | 52608.5147
2020-05-14 16:00 | 6.8769 | 7.2385 | 347.8316 | 2210.3221 | 33154.8313
2020-05-14 17:00 | 6.3175 | 6.6498 | 342.9594 | 1703.626 | 25554.3906
2020-05-14 18:00 | 6.4539 | 6.7933 | 337.3729 | 1820.1833 | 27302.7495
2020-05-14 19:00 | 6.6413 | 6.9906 | 333.7137 | 1980.3984 | 29705.9754
2020-05-14 20:00 | 6.6528 | 7.0027 | 332.9562 | 1990.525 | 29857.8754
2020-05-14 21:00 | 6.2538 | 6.5827 | 331.3626 | 1649.131 | 24736.9655
2020-05-14 22:00 | 5.7117 | 6.0121 | 322.2168 | 1240.4775 | 18607.1622
2020-05-14 23:00 | 5.338 | 5.6188 | 321.8101 | 1006.3178 | 15094.7668
2020-05-15 00:00 | 5.2696 | 5.5468 | 318.5141 | 963.7029 | 14455.5432
2020-05-15 01:00 | 5.0694 | 5.336 | 310.7196 | 853.6661 | 12804.9908
2020-05-15 02:00 | 4.7484 | 4.9982 | 308.8063 | 684.2257 | 10263.386
2020-05-15 03:00 | 4.1953 | 4.4159 | 306.8981 | 444.4125 | 6666.1873
2020-05-15 04:00 | 3.5542 | 3.7412 | 296.8932 | 223.9731 | 3359.5968
2020-05-15 05:00 | 2.1161 | 2.2274 | 295.9729 | 0 | 0
2020-05-15 06:00 | 1.3795 | 1.4521 | 266.9236 | 0 | 0
2020-05-15 07:00 | 1.0426 | 1.0975 | 271.7763 | 0 | 0
2020-05-15 08:00 | 0.71184 | 0.74927 | 237.32 | 0 | 0
2020-05-15 09:00 | 0.47653 | 0.5016 | 120 | 0 | 0
2020-05-15 10:00 | 0.46437 | 0.48879 | 205.7239 | 0 | 0
2020-05-15 11:00 | 0.83536 | 0.87929 | 186.17 | 0 | 0
2020-05-15 12:00 | 1.0341 | 1.0885 | 190.9972 | 0 | 0
2020-05-15 13:00 | 0.78201 | 0.82313 | 131.0093 | 0 | 0
2020-05-15 14:00 | 1.4357 | 1.5112 | 127.9947 | 0 | 0
2020-05-15 15:00 | 1.9125 | 2.0131 | 107.8239 | 0 | 0
2020-05-15 16:00 | 1.6602 | 1.7475 | 84.2303 | 0 | 0
2020-05-15 17:00 | 2.2261 | 2.3432 | 43.7902 | 0 | 0
2020-05-15 18:00 | 3.029 | 3.1883 | 22.3824 | 88.3037 | 1324.5558
2020-05-15 19:00 | 3.9028 | 4.1081 | 21.6811 | 336.0387 | 5040.5809
2020-05-15 20:00 | 4.2574 | 4.4813 | 31.1488 | 467.4246 | 7011.3692
2020-05-15 21:00 | 4.3951 | 4.6263 | 32.6739 | 527.2795 | 7909.1928
2020-05-15 22:00 | 3.3959 | 3.5745 | 28.5075 | 176.298 | 2644.4694
2020-05-15 23:00 | 3.218 | 3.3872 | 17.5747 | 130.8671 | 1963.0072
2020-05-16 00:00 | 3.1983 | 3.3665 | 2.2664 | 126.4242 | 1896.3623
2020-05-16 01:00 | 3.9032 | 4.1085 | 344.9846 | 336.1754 | 5042.6307
2020-05-16 02:00 | 4.6003 | 4.8423 | 333.3132 | 618.4481 | 9276.7209
2020-05-16 03:00 | 4.9997 | 5.2626 | 319.4849 | 816.8438 | 12252.6564
2020-05-16 04:00 | 4.4983 | 4.7349 | 297.8561 | 573.1347 | 8597.0205
2020-05-16 05:00 | 4.0124 | 4.2234 | 280.5775 | 376.6514 | 5649.7714
2020-05-16 06:00 | 4.762 | 5.0125 | 280.9993 | 691.2748 | 10369.1215
2020-05-16 07:00 | 5.0267 | 5.2911 | 281.3326 | 831.1383 | 12467.0741
2020-05-16 08:00 | 5.2545 | 5.5308 | 286.9529 | 954.2615 | 14313.9225
2020-05-16 09:00 | 5.3965 | 5.6804 | 283.414 | 1042.776 | 15641.6394
2020-05-16 10:00 | 6.2782 | 6.6083 | 279.6243 | 1669.9794 | 25049.6916
2020-05-16 11:00 | 7.1204 | 7.4949 | 277.0636 | 2449.2749 | 36739.123
2020-05-16 12:00 | 7.5939 | 7.9933 | 273.5328 | 2975.9592 | 44639.3876
2020-05-16 13:00 | 7.7806 | 8.1898 | 271.7319 | 3196.7263 | 47950.8948
2020-05-16 14:00 | 8.1691 | 8.5988 | 274.251 | 3657.4403 | 54861.6041
2020-05-16 15:00 | 7.5251 | 7.9209 | 276.1798 | 2899.2887 | 43489.3302
2020-05-16 16:00 | 6.3887 | 6.7247 | 275.2838 | 1764.4823 | 26467.2338
2020-05-16 17:00 | 6.1537 | 6.4773 | 272.217 | 1566.1123 | 23491.6846
2020-05-16 18:00 | 5.959 | 6.2724 | 269.2217 | 1422.6657 | 21339.9854
2020-05-16 19:00 | 6.4008 | 6.7375 | 267.5492 | 1774.832 | 26622.4801
2020-05-16 20:00 | 6.4208 | 6.7585 | 263.6477 | 1791.8619 | 26877.9286
2020-05-16 21:00 | 5.9581 | 6.2715 | 258.2371 | 1422.0245 | 21330.367
2020-05-16 22:00 | 5.0913 | 5.3591 | 264.5549 | 865.2813 | 12979.219
2020-05-16 23:00 | 5.3184 | 5.5981 | 260.6044 | 994.0787 | 14911.1799
2020-05-17 00:00 | 5.0253 | 5.2897 | 256.5274 | 830.4047 | 12456.0704
2020-05-17 01:00 | 5.5999 | 5.8944 | 252.9217 | 1169.5086 | 17542.6285
2020-05-17 02:00 | 5.5007 | 5.79 | 257.7521 | 1107.688 | 16615.3199
2020-05-17 03:00 | 4.6567 | 4.9017 | 255.4149 | 643.5042 | 9652.5633
2020-05-17 04:00 | 3.9144 | 4.1203 | 241.6704 | 340.333 | 5104.9944
2020-05-17 05:00 | 3.2992 | 3.4727 | 222.7453 | 149.1684 | 2237.5266
2020-05-17 06:00 | 3.1004 | 3.2635 | 219.9989 | 104.3886 | 1565.8292
2020-05-17 07:00 | 3.5816 | 3.7699 | 219.8595 | 232.2045 | 3483.0674
2020-05-17 08:00 | 4.3147 | 4.5416 | 225.9666 | 491.5693 | 7373.5401
2020-05-17 09:00 | 5.0212 | 5.2853 | 220.7044 | 828.2027 | 12423.0398
2020-05-17 10:00 | 5.4346 | 5.7204 | 222.8695 | 1066.4689 | 15997.0339
2020-05-17 11:00 | 6.681 | 7.0324 | 219.7263 | 2018.197 | 30272.9555
2020-05-17 12:00 | 6.3025 | 6.634 | 211.2174 | 1690.8201 | 25362.3015
2020-05-17 13:00 | 6.2004 | 6.5265 | 211.7822 | 1603.4971 | 24052.4558
2020-05-17 14:00 | 5.6947 | 5.9942 | 204.7476 | 1228.5456 | 18428.1841
2020-05-17 15:00 | 5.5526 | 5.8446 | 216.0017 | 1140.0247 | 17100.3712
2020-05-17 16:00 | 3.9807 | 4.1901 | 211.1966 | 364.8982 | 5473.4732
2020-05-17 17:00 | 4.1777 | 4.3974 | 194.9674 | 437.9003 | 6568.504
2020-05-17 18:00 | 5.1375 | 5.4077 | 210.0384 | 889.6843 | 13345.2647
2020-05-17 19:00 | 6.0913 | 6.4117 | 243.5957 | 1520.1759 | 22802.6387
2020-05-17 20:00 | 7.0249 | 7.3944 | 272.8134 | 2355.6003 | 35334.0039
2020-05-17 21:00 | 7.8904 | 8.3054 | 290.0802 | 3326.8532 | 49902.7982
2020-05-17 22:00 | 8.4363 | 8.88 | 297.0407 | 3974.671 | 59620.0653
2020-05-17 23:00 | 8.648 | 9.1028 | 294.8734 | 4220.0208 | 63300.3117
2020-05-18 00:00 | 8.6247 | 9.0783 | 294.8196 | 4193.8214 | 62907.3203
2020-05-18 01:00 | 8.4262 | 8.8694 | 295.374 | 3962.6735 | 59440.1025
2020-05-18 02:00 | 8.0968 | 8.5226 | 292.9035 | 3571.515 | 53572.7247
2020-05-18 03:00 | 7.6159 | 8.0165 | 290.8292 | 3001.5726 | 45023.5888
2020-05-18 04:00 | 7.0557 | 7.4268 | 282.3593 | 2385.7693 | 35786.5398
2020-05-18 05:00 | 6.3395 | 6.673 | 269.243 | 1722.4373 | 25836.559
2020-05-18 06:00 | 6.4514 | 6.7907 | 265.6106 | 1818.0707 | 27271.0611
2020-05-18 07:00 | 7.2747 | 7.6574 | 264.3971 | 2620.4839 | 39307.2584
2020-05-18 08:00 | 8.7241 | 9.1829 | 264.1233 | 4305.7143 | 64585.7149
2020-05-18 09:00 | 10.8899 | 11.4627 | 267.8348 | 5643.57 | 84653.55
2020-05-18 10:00 | 9.8919 | 10.4122 | 267.3381 | 5296.7106 | 79450.6595
2020-05-18 11:00 | 12.1233 | 12.7609 | 271.1859 | 5700 | 85500
2020-05-18 12:00 | 13.4907 | 14.2002 | 278.5791 | 5700 | 85500
2020-05-18 13:00 | 13.0432 | 13.7292 | 290.6826 | 5700 | 85500
2020-05-18 14:00 | 10.8367 | 11.4067 | 308.0072 | 5630.9061 | 84463.5914
2020-05-18 15:00 | 9.2003 | 9.6842 | 309.9052 | 4796.4354 | 71946.531
2020-05-18 16:00 | 8.4867 | 8.933 | 310.6291 | 4034.4623 | 60516.9339
2020-05-18 17:00 | 7.2786 | 7.6614 | 315.5257 | 2624.7882 | 39371.8226
2020-05-18 18:00 | 5.9902 | 6.3053 | 313.0178 | 1445.709 | 21685.6355
2020-05-18 19:00 | 5.4409 | 5.727 | 305.5674 | 1070.3951 | 16055.9271
2020-05-18 20:00 | 4.9647 | 5.2258 | 294.6343 | 798.3428 | 11975.1417
2020-05-18 21:00 | 5.0555 | 5.3214 | 282.1167 | 846.3458 | 12695.1865
2020-05-18 22:00 | 5.243 | 5.5188 | 295.6135 | 947.1202 | 14206.8034
2020-05-18 23:00 | 4.4502 | 4.6842 | 292.3837 | 551.7422 | 8276.1336
2020-05-19 00:00 | 4.1663 | 4.3854 | 277.9631 | 433.6705 | 6505.0573
2020-05-19 01:00 | 4.5584 | 4.7981 | 258.9194 | 599.7964 | 8996.9467
2020-05-19 02:00 | 4.6468 | 4.8911 | 246.7052 | 639.064 | 9585.9605
2020-05-19 03:00 | 4.3784 | 4.6087 | 239.8767 | 519.8517 | 7797.7757
2020-05-19 04:00 | 4.2428 | 4.466 | 230.3513 | 462.0263 | 6930.3952
2020-05-19 05:00 | 4.8842 | 5.1411 | 222.8418 | 755.8187 | 11337.28
2020-05-19 06:00 | 5.9461 | 6.2588 | 219.8621 | 1413.1545 | 21197.3178
2020-05-19 07:00 | 6.1886 | 6.5141 | 217.6626 | 1593.4351 | 23901.5267
2020-05-19 08:00 | 5.3205 | 5.6003 | 221.1763 | 995.4061 | 14931.0909
2020-05-19 09:00 | 4.6141 | 4.8568 | 231.609 | 624.5564 | 9368.3461
2020-05-19 10:00 | 3.9666 | 4.1753 | 228.8468 | 359.695 | 5395.4253
2020-05-19 11:00 | 5.2208 | 5.4953 | 252.9412 | 933.6651 | 14004.9762
2020-05-19 12:00 | 5.4676 | 5.7552 | 276.256 | 1087.051 | 16305.765
2020-05-19 13:00 | 5.2201 | 5.4946 | 293.4752 | 933.311 | 13999.6645
2020-05-19 14:00 | 3.9797 | 4.189 | 307.3686 | 364.5389 | 5468.0836
2020-05-19 15:00 | 2.5292 | 2.6623 | 301.2966 | 0 | 0
2020-05-19 16:00 | 2.6016 | 2.7384 | 308.5099 | 0 | 0
2020-05-19 17:00 | 3.2645 | 3.4362 | 328.6264 | 141.3463 | 2120.1938
2020-05-19 18:00 | 1.6522 | 1.7391 | 324.8051 | 0 | 0
2020-05-19 19:00 | 1.8175 | 1.9131 | 256.0488 | 0 | 0
2020-05-19 20:00 | 3.3898 | 3.5681 | 258.7163 | 174.4687 | 2617.0298
2020-05-19 21:00 | 4.4311 | 4.6642 | 277.3688 | 543.2841 | 8149.2608
2020-05-19 22:00 | 6.1359 | 6.4587 | 282.7594 | 1553.0604 | 23295.9058
2020-05-19 23:00 | 7.7299 | 8.1365 | 284.6035 | 3136.6476 | 47049.7139
2020-05-20 00:00 | 8.5011 | 8.9482 | 288.8381 | 4051.5943 | 60773.9142
2020-05-20 01:00 | 8.2934 | 8.7296 | 294.115 | 3805.0132 | 57075.1983
2020-05-20 02:00 | 8.5426 | 8.9919 | 297.8954 | 4100.8706 | 61513.059
2020-05-20 03:00 | 8.421 | 8.8639 | 300.3797 | 3956.5258 | 59347.8875
2020-05-20 04:00 | 8.763 | 9.2239 | 304.66 | 4349.5854 | 65243.7808
2020-05-20 05:00 | 9.3405 | 9.8317 | 310.3952 | 4917.679 | 73765.185
2020-05-20 06:00 | 8.5535 | 9.0034 | 318.7689 | 4113.5895 | 61703.8429
2020-05-20 07:00 | 7.4261 | 7.8167 | 321.9052 | 2789.0557 | 41835.8358
2020-05-20 08:00 | 7.0861 | 7.4588 | 321.655 | 2415.5818 | 36233.7265
2020-05-20 09:00 | 6.9625 | 7.3287 | 324.1614 | 2294.3048 | 34414.5719
2020-05-20 10:00 | 7.9546 | 8.3729 | 321.6711 | 3402.9262 | 51043.8925
2020-05-20 11:00 | 8.1163 | 8.5431 | 320.3474 | 3594.67 | 53920.0507
2020-05-20 12:00 | 8.1824 | 8.6128 | 321.9747 | 3673.2414 | 55098.6207
2020-05-20 13:00 | 8.5657 | 9.0162 | 322.1432 | 4127.3609 | 61910.4142
2020-05-20 14:00 | 8.2751 | 8.7104 | 326.0581 | 3783.2843 | 56749.2646
2020-05-20 15:00 | 8.2253 | 8.6579 | 330.2778 | 3724.0758 | 55861.1377
2020-05-20 16:00 | 8.2531 | 8.6872 | 335.8047 | 3757.1564 | 56357.3467
2020-05-20 17:00 | 7.8012 | 8.2115 | 339.917 | 3221.1702 | 48317.5524
2020-05-20 18:00 | 7.2363 | 7.6169 | 341.8378 | 2577.6393 | 38664.5894
2020-05-20 19:00 | 6.9328 | 7.2975 | 344.1222 | 2265.2421 | 33978.6316
2020-05-20 20:00 | 6.8725 | 7.234 | 344.8338 | 2206.0736 | 33091.1035
2020-05-20 21:00 | 6.8342 | 7.1936 | 344.7879 | 2168.4638 | 32526.9567
2020-05-20 22:00 | 6.7819 | 7.1386 | 339.8223 | 2117.1372 | 31757.0576
2020-05-20 23:00 | 6.3345 | 6.6676 | 336.8314 | 1718.1064 | 25771.5957
2020-05-21 00:00 | 6.3041 | 6.6357 | 337.3018 | 1692.1788 | 25382.6818
2020-05-21 01:00 | 6.2307 | 6.5584 | 337.9384 | 1629.4329 | 24441.4929
2020-05-21 02:00 | 5.7169 | 6.0176 | 333.8971 | 1244.3292 | 18664.9383
2020-05-21 03:00 | 5.2777 | 5.5553 | 327.4752 | 968.7228 | 14530.8421
2020-05-21 04:00 | 4.6665 | 4.9119 | 319.9997 | 647.8139 | 9717.2092
2020-05-21 05:00 | 3.5973 | 3.7865 | 317.0908 | 236.943 | 3554.1456
2020-05-21 06:00 | 3.7694 | 3.9677 | 320.4749 | 288.7563 | 4331.3444
2020-05-21 07:00 | 5.5659 | 5.8586 | 328.7071 | 1148.3165 | 17224.7469
2020-05-21 08:00 | 6.4134 | 6.7507 | 326.9159 | 1785.5609 | 26783.4142
2020-05-21 09:00 | 6.4624 | 6.8023 | 320.4522 | 1827.497 | 27412.4557
2020-05-21 10:00 | 6.4071 | 6.7441 | 313.0232 | 1780.2216 | 26703.324
2020-05-21 11:00 | 6.8533 | 7.2138 | 311.3767 | 2187.2308 | 32808.4621
2020-05-21 12:00 | 7.0618 | 7.4332 | 310.3165 | 2391.7267 | 35875.8999
2020-05-21 13:00 | 7.392 | 7.7808 | 310.8709 | 2751.0974 | 41266.4612
2020-05-21 14:00 | 7.2392 | 7.62 | 311.3633 | 2580.9511 | 38714.2665
2020-05-21 15:00 | 7.3029 | 7.687 | 313.7411 | 2651.8839 | 39778.2583
2020-05-21 16:00 | 7.3004 | 7.6844 | 317.3781 | 2649.1005 | 39736.5069
2020-05-21 17:00 | 7.035 | 7.405 | 322.2895 | 2365.4159 | 35481.2386
2020-05-21 18:00 | 7.2488 | 7.6301 | 325.5636 | 2591.636 | 38874.5406
2020-05-21 19:00 | 7.3797 | 7.7679 | 323.8384 | 2737.4031 | 41061.0472
2020-05-21 20:00 | 7.28 | 7.6629 | 320.9145 | 2626.3295 | 39394.9418
2020-05-21 21:00 | 6.9563 | 7.3221 | 316.8301 | 2288.2121 | 34323.1821
2020-05-21 22:00 | 6.6731 | 7.024 | 311.3025 | 2010.399 | 30155.9848
2020-05-21 23:00 | 6.287 | 6.6176 | 299.1562 | 1677.5094 | 25162.6409
2020-05-22 00:00 | 6.675 | 7.0261 | 291.8545 | 2012.3286 | 30184.9287
2020-05-22 01:00 | 7.1893 | 7.5674 | 295.8402 | 2525.3217 | 37879.8259
2020-05-22 02:00 | 7.1586 | 7.5351 | 307.3411 | 2491.1543 | 37367.3146
2020-05-22 03:00 | 6.9083 | 7.2716 | 315.5431 | 2241.1401 | 33617.1019
2020-05-22 04:00 | 7.8716 | 8.2856 | 322.2328 | 3304.5695 | 49568.5424
2020-05-22 05:00 | 8.2619 | 8.6965 | 323.6768 | 3767.6282 | 56514.4236
2020-05-22 06:00 | 8.5152 | 8.9631 | 321.4767 | 4068.3242 | 61024.8634
2020-05-22 07:00 | 8.6633 | 9.1189 | 322.8157 | 4237.2401 | 63558.602
2020-05-22 08:00 | 8.6825 | 9.1392 | 323.9292 | 4258.9041 | 63883.5618
2020-05-22 09:00 | 8.517 | 8.9649 | 326.4486 | 4070.4261 | 61056.3922
2020-05-22 10:00 | 9.0778 | 9.5553 | 330.3931 | 4690.4441 | 70356.6608
2020-05-22 11:00 | 8.6032 | 9.0556 | 329.3078 | 4169.5345 | 62543.0178
2020-05-22 12:00 | 7.8003 | 8.2105 | 329.352 | 3220.0524 | 48300.7867
2020-05-22 13:00 | 7.4441 | 7.8356 | 328.7727 | 2809.0711 | 42136.0669
2020-05-22 14:00 | 7.1944 | 7.5728 | 331.3526 | 2531.0055 | 37965.082
2020-05-22 15:00 | 7.3778 | 7.7659 | 331.9005 | 2735.282 | 41029.2298
2020-05-22 16:00 | 6.8211 | 7.1798 | 332.1442 | 2155.5931 | 32333.8971
2020-05-22 17:00 | 6.0114 | 6.3276 | 333.9211 | 1461.3042 | 21919.5624
2020-05-22 18:00 | 5.7835 | 6.0877 | 337.6796 | 1293.4047 | 19401.0706
2020-05-22 19:00 | 5.6693 | 5.9675 | 341.1474 | 1212.734 | 18191.0101
2020-05-22 20:00 | 5.4094 | 5.6939 | 343.3717 | 1050.7794 | 15761.6907
2020-05-22 21:00 | 5.2871 | 5.5651 | 338.4128 | 974.5652 | 14618.4784
2020-05-22 22:00 | 5.5908 | 5.8848 | 332.1092 | 1163.8074 | 17457.1111
2020-05-22 23:00 | 6.0678 | 6.3869 | 324.6797 | 1502.8479 | 22542.7181
2020-05-23 00:00 | 6.187 | 6.5124 | 322.4293 | 1592.0516 | 23880.7733
2020-05-23 01:00 | 6.4486 | 6.7877 | 321.5807 | 1815.6373 | 27234.5592
2020-05-23 02:00 | 6.2183 | 6.5453 | 318.5987 | 1618.8196 | 24282.2943
2020-05-23 03:00 | 6.0348 | 6.3522 | 314.5184 | 1478.5388 | 22178.0824
2020-05-23 04:00 | 5.587 | 5.8809 | 311.4269 | 1161.473 | 17422.0946
2020-05-23 05:00 | 5.2734 | 5.5508 | 313.0442 | 966.0453 | 14490.68
2020-05-23 06:00 | 5.9546 | 6.2677 | 322.9844 | 1419.4166 | 21291.249
2020-05-23 07:00 | 6.3349 | 6.6681 | 331.616 | 1718.4756 | 25777.1334
2020-05-23 08:00 | 7.3239 | 7.709 | 338.2331 | 2675.1745 | 40127.6173
2020-05-23 09:00 | 6.0366 | 6.3541 | 338.7703 | 1479.8923 | 22198.3844
2020-05-23 10:00 | 4.3352 | 4.5633 | 335.3668 | 500.6954 | 7510.4305
2020-05-23 11:00 | 5.1394 | 5.4097 | 329.6764 | 890.6902 | 13360.3529
2020-05-23 12:00 | 5.7675 | 6.0708 | 332.146 | 1281.5796 | 19223.6935
2020-05-23 13:00 | 6.3048 | 6.6364 | 343.8574 | 1692.7506 | 25391.2595
2020-05-23 14:00 | 6.0959 | 6.4165 | 358.6857 | 1523.5265 | 22852.8973
2020-05-23 15:00 | 5.5552 | 5.8474 | 13.685 | 1141.6529 | 17124.7931
2020-05-23 16:00 | 5.1789 | 5.4513 | 24.5475 | 911.5516 | 13673.2742
2020-05-23 17:00 | 5.124 | 5.3935 | 31.1858 | 882.5542 | 13238.3135
2020-05-23 18:00 | 5.0653 | 5.3317 | 34.8253 | 851.5304 | 12772.9566
2020-05-23 19:00 | 4.6453 | 4.8896 | 41.4247 | 638.4029 | 9576.0432
2020-05-23 20:00 | 3.6715 | 3.8646 | 47.2493 | 259.2811 | 3889.2159
2020-05-23 21:00 | 2.0171 | 2.1232 | 48.3774 | 0 | 0
2020-05-23 22:00 | 0.2893 | 0.30452 | 45.1474 | 0 | 0
2020-05-23 23:00 | 0.97239 | 1.0235 | 229.4943 | 0 | 0
2020-05-24 00:00 | 2.0575 | 2.1657 | 243.7399 | 0 | 0
2020-05-24 01:00 | 3.1467 | 3.3122 | 259.2766 | 114.8076 | 1722.114
2020-05-24 02:00 | 1.971 | 2.0746 | 254.9797 | 0 | 0
2020-05-24 03:00 | 1.3457 | 1.4165 | 255.9806 | 0 | 0
2020-05-24 04:00 | 0.28185 | 0.29667 | 338.1986 | 0 | 0
2020-05-24 05:00 | 1.7897 | 1.8838 | 92.8246 | 0 | 0
2020-05-24 06:00 | 1.6629 | 1.7503 | 146.2364 | 0 | 0
2020-05-24 07:00 | 2.9954 | 3.1529 | 120.638 | 80.7216 | 1210.8245
2020-05-24 08:00 | 3.6451 | 3.8368 | 120.6462 | 251.3362 | 3770.0426
2020-05-24 09:00 | 2.996 | 3.1536 | 141.569 | 80.8648 | 1212.9716
2020-05-24 10:00 | 2.4181 | 2.5452 | 132.353 | 0 | 0
2020-05-24 11:00 | 2.4366 | 2.5648 | 127.9462 | 0 | 0
2020-05-24 12:00 | 2.5804 | 2.7161 | 121.3647 | 0 | 0
2020-05-24 13:00 | 2.1197 | 2.2312 | 126.0571 | 0 | 0
2020-05-24 14:00 | 1.332 | 1.4021 | 132.2194 | 0 | 0
2020-05-24 15:00 | 0.81018 | 0.85279 | 120.777 | 0 | 0
2020-05-24 16:00 | 0.9426 | 0.99218 | 93.2322 | 0 | 0
2020-05-24 17:00 | 1.4839 | 1.5619 | 97.1981 | 0 | 0
2020-05-24 18:00 | 1.9221 | 2.0232 | 105.3586 | 0 | 0
2020-05-24 19:00 | 1.9997 | 2.1048 | 108.5559 | 0 | 0
2020-05-24 20:00 | 1.9813 | 2.0856 | 98.0978 | 0 | 0
2020-05-24 21:00 | 2.2469 | 2.3651 | 92.5973 | 0 | 0
2020-05-24 22:00 | 2.4528 | 2.5818 | 68.3867 | 0 | 0
2020-05-24 23:00 | 3.0752 | 3.2369 | 66.702 | 98.7011 | 1480.5168
2020-05-25 00:00 | 3.1808 | 3.3481 | 64.9565 | 122.4835 | 1837.2522
2020-05-25 01:00 | 3.3679 | 3.5451 | 62.6307 | 167.8911 | 2518.3667
2020-05-25 02:00 | 3.4156 | 3.5952 | 51.5856 | 182.2409 | 2733.6141
2020-05-25 03:00 | 3.8497 | 4.0522 | 32.74 | 316.3593 | 4745.3893
2020-05-25 04:00 | 4.6519 | 4.8966 | 21.0495 | 641.3476 | 9620.2138
2020-05-25 05:00 | 5.4306 | 5.7163 | 20.1601 | 1064.033 | 15960.4943
2020-05-25 06:00 | 5.3557 | 5.6374 | 21.3906 | 1017.3567 | 15260.3499
2020-05-25 07:00 | 4.8909 | 5.1481 | 20.9376 | 759.3431 | 11390.1466
2020-05-25 08:00 | 4.6011 | 4.8431 | 21.9307 | 618.7688 | 9281.5324
2020-05-25 09:00 | 4.6933 | 4.9401 | 25.3351 | 659.7383 | 9896.0749
2020-05-25 10:00 | 5.1606 | 5.4321 | 18.7412 | 901.8966 | 13528.4497
2020-05-25 11:00 | 5.5891 | 5.8831 | 29.4478 | 1162.7664 | 17441.4964
2020-05-25 12:00 | 5.745 | 6.0472 | 35.2726 | 1265.0316 | 18975.4744
2020-05-25 13:00 | 6.078 | 6.3976 | 38.3316 | 1510.3398 | 22655.0966
2020-05-25 14:00 | 6.2341 | 6.5619 | 36.5958 | 1632.303 | 24484.5455
2020-05-25 15:00 | 6.638 | 6.9871 | 34.7413 | 1977.5126 | 29662.6896
2020-05-25 16:00 | 6.3144 | 6.6465 | 36.0047 | 1700.9982 | 25514.9725
2020-05-25 17:00 | 5.6101 | 5.9052 | 26.3183 | 1175.8639 | 17637.9586
2020-05-25 18:00 | 5.577 | 5.8703 | 16.9033 | 1155.2222 | 17328.3334
2020-05-25 19:00 | 5.772 | 6.0756 | 17.8056 | 1284.9225 | 19273.8373
2020-05-25 20:00 | 5.3694 | 5.6518 | 18.0746 | 1025.8824 | 15388.2364
2020-05-25 21:00 | 5.1926 | 5.4657 | 13.5228 | 918.7658 | 13781.4865
2020-05-25 22:00 | 5.2928 | 5.5712 | 19.0759 | 978.1335 | 14672.0027
2020-05-25 23:00 | 5.2024 | 5.476 | 31.1224 | 923.9442 | 13859.1624
2020-05-26 00:00 | 5.1407 | 5.411 | 43.9768 | 891.3367 | 13370.0499
2020-05-26 01:00 | 5.1101 | 5.3789 | 60.7544 | 875.2122 | 13128.1827
2020-05-26 02:00 | 5.3974 | 5.6813 | 75.5866 | 1043.3194 | 15649.7914
2020-05-26 03:00 | 6.4021 | 6.7388 | 85.867 | 1775.9326 | 26638.9895
2020-05-26 04:00 | 6.7538 | 7.109 | 89.4105 | 2089.6065 | 31344.097
2020-05-26 05:00 | 6.5876 | 6.9341 | 87.9805 | 1934.4562 | 29016.843
2020-05-26 06:00 | 5.7794 | 6.0834 | 83.2434 | 1290.3758 | 19355.6365
2020-05-26 07:00 | 4.8599 | 5.1156 | 78.0596 | 743.0066 | 11145.0992
2020-05-26 08:00 | 4.4131 | 4.6453 | 70.527 | 535.2957 | 8029.4353
2020-05-26 09:00 | 4.2798 | 4.5049 | 65.1258 | 476.0672 | 7141.0075
2020-05-26 10:00 | 4.6329 | 4.8766 | 48.214 | 632.9079 | 9493.6191
2020-05-26 11:00 | 5.7457 | 6.0479 | 47.4393 | 1265.5342 | 18983.0137
2020-05-26 12:00 | 5.5141 | 5.8041 | 53.9205 | 1116.0564 | 16740.8464
2020-05-26 13:00 | 3.9739 | 4.1829 | 52.6675 | 362.3725 | 5435.5876
2020-05-26 14:00 | 6.3783 | 6.7137 | 57.4179 | 1755.5568 | 26333.3517
2020-05-26 15:00 | 6.6398 | 6.989 | 50.4743 | 1979.0676 | 29686.0146
2020-05-26 16:00 | 4.6924 | 4.9392 | 38.1124 | 659.3306 | 9889.9597
2020-05-26 17:00 | 5.7281 | 6.0293 | 40.7738 | 1252.5358 | 18788.037
2020-05-26 18:00 | 6.5033 | 6.8453 | 34.7901 | 1862.3978 | 27935.9668
2020-05-26 19:00 | 6.4109 | 6.7481 | 27.164 | 1783.4815 | 26752.2222
2020-05-26 20:00 | 6.3459 | 6.6797 | 21.7056 | 1727.9237 | 25918.8552
2020-05-26 21:00 | 6.3127 | 6.6447 | 18.7282 | 1699.5039 | 25492.559
2020-05-26 22:00 | 6.512 | 6.8545 | 15.6913 | 1869.8652 | 28047.9773
2020-05-26 23:00 | 6.7236 | 7.0772 | 17.579 | 2059.9941 | 30899.9113
2020-05-27 00:00 | 6.4417 | 6.7805 | 21.3931 | 1809.7505 | 27146.2582
2020-05-27 01:00 | 6.1657 | 6.49 | 18.4982 | 1574.9965 | 23624.9472
2020-05-27 02:00 | 6.2686 | 6.5983 | 15.9592 | 1661.8151 | 24927.2267
2020-05-27 03:00 | 5.9437 | 6.2563 | 16.0314 | 1411.4158 | 21171.2376
2020-05-27 04:00 | 5.6881 | 5.9873 | 19.3303 | 1224.4744 | 18367.1166
2020-05-27 05:00 | 5.6279 | 5.9239 | 25.9585 | 1186.9648 | 17804.4727
2020-05-27 06:00 | 4.3296 | 4.5573 | 20.4064 | 498.1814 | 7472.7215
2020-05-27 07:00 | 4.0263 | 4.238 | 16.1685 | 381.7872 | 5726.8083
2020-05-27 08:00 | 4.1386 | 4.3562 | 17.4034 | 423.3992 | 6350.9882
2020-05-27 09:00 | 4.2622 | 4.4864 | 22.9792 | 469.1955 | 7037.932
2020-05-27 10:00 | 3.9414 | 4.1487 | 32.7261 | 350.3427 | 5255.1402
2020-05-27 11:00 | 3.9224 | 4.1287 | 35.5618 | 343.3002 | 5149.5028
2020-05-27 12:00 | 3.8294 | 4.0308 | 40.1139 | 308.8425 | 4632.6368
2020-05-27 13:00 | 3.7425 | 3.9394 | 41.0687 | 280.6602 | 4209.9026
2020-05-27 14:00 | 3.5095 | 3.6941 | 41.8894 | 210.5139 | 3157.7087
2020-05-27 15:00 | 4.9582 | 5.2189 | 39.9335 | 794.9027 | 11923.5402
2020-05-27 16:00 | 2.787 | 2.9336 | 57.4708 | 0 | 0
2020-05-27 17:00 | 2.5784 | 2.7141 | 25.4729 | 0 | 0
2020-05-27 18:00 | 3.5322 | 3.718 | 19.8329 | 217.351 | 3260.2652
2020-05-27 19:00 | 4.5013 | 4.738 | 29.5584 | 574.4522 | 8616.7837
2020-05-27 20:00 | 4.9392 | 5.199 | 40.5895 | 784.8925 | 11773.3869
2020-05-27 21:00 | 4.3844 | 4.6149 | 44.5021 | 522.5082 | 7837.6228
2020-05-27 22:00 | 4.2928 | 4.5186 | 49.4879 | 481.8596 | 7227.8934
2020-05-27 23:00 | 2.9357 | 3.0901 | 56.7342 | 67.2718 | 1009.0765
2020-05-28 00:00 | 3.6014 | 3.7908 | 43.1133 | 238.1642 | 3572.4636
2020-05-28 01:00 | 3.9744 | 4.1834 | 27.3262 | 362.5733 | 5438.6
2020-05-28 02:00 | 5.0617 | 5.3279 | 19.2965 | 849.6087 | 12744.1303
2020-05-28 03:00 | 5.7238 | 6.0249 | 25.5386 | 1249.4091 | 18741.1372
2020-05-28 04:00 | 5.4665 | 5.754 | 27.714 | 1086.3858 | 16295.7875
2020-05-28 05:00 | 5.2917 | 5.57 | 31.5112 | 977.4204 | 14661.3055
2020-05-28 06:00 | 5.8319 | 6.1386 | 34.6151 | 1329.0512 | 19935.7682
2020-05-28 07:00 | 5.5897 | 5.8837 | 32.7493 | 1163.1375 | 17447.0623
2020-05-28 08:00 | 6.0941 | 6.4146 | 29.5315 | 1522.218 | 22833.2694
2020-05-28 09:00 | 6.887 | 7.2493 | 33.0108 | 2220.3165 | 33304.7468
2020-05-28 10:00 | 7.653 | 8.0556 | 36.1531 | 3045.5517 | 45683.2762
2020-05-28 11:00 | 8.0444 | 8.4675 | 42.1187 | 3509.4253 | 52641.3794
2020-05-28 12:00 | 8.6982 | 9.1556 | 45.1238 | 4276.5295 | 64147.9422
2020-05-28 13:00 | 8.889 | 9.3565 | 45.119 | 4491.486 | 67372.2903
2020-05-28 14:00 | 8.6214 | 9.0749 | 46.0688 | 4190.1057 | 62851.5861
2020-05-28 15:00 | 8.7961 | 9.2587 | 46.5604 | 4386.839 | 65802.5854
2020-05-28 16:00 | 8.2989 | 8.7354 | 43.9673 | 3811.4942 | 57172.4132
2020-05-28 17:00 | 7.9692 | 8.3883 | 39.7335 | 3420.2724 | 51304.0862
2020-05-28 18:00 | 8.1593 | 8.5884 | 31.3562 | 3645.7069 | 54685.6042
2020-05-28 19:00 | 8.7403 | 9.1999 | 21.0789 | 4323.9435 | 64859.1532
2020-05-28 20:00 | 9.4067 | 9.9015 | 14.1725 | 4975.0283 | 74625.424
2020-05-28 21:00 | 9.6578 | 10.1658 | 7.2741 | 5152.82 | 77292.3005
2020-05-28 22:00 | 10.2355 | 10.7738 | 4.1308 | 5452.5842 | 81788.7634
2020-05-28 23:00 | 10.6112 | 11.1693 | 4.4405 | 5577.2596 | 83658.8937
2020-05-29 00:00 | 10.8663 | 11.4378 | 4.0268 | 5637.953 | 84569.2943
2020-05-29 01:00 | 10.5368 | 11.091 | 0.25838 | 5559.5587 | 83393.3799
2020-05-29 02:00 | 10.0318 | 10.5594 | 357.6971 | 5370.6849 | 80560.274
2020-05-29 03:00 | 9.702 | 10.2122 | 355.9755 | 5179.9449 | 77699.1739
2020-05-29 04:00 | 9.4085 | 9.9034 | 353.6213 | 4976.566 | 74648.4899
2020-05-29 05:00 | 9.0127 | 9.4868 | 354.0546 | 4630.8386 | 69462.5786
2020-05-29 06:00 | 8.6885 | 9.1454 | 356.2287 | 4265.6244 | 63984.3654
2020-05-29 07:00 | 9.1305 | 9.6107 | 1.5549 | 4735.9802 | 71039.7035
2020-05-29 08:00 | 10.1064 | 10.6379 | 5.0511 | 5400.6942 | 81010.4133
2020-05-29 09:00 | 8.9116 | 9.3803 | 4.8666 | 4516.9381 | 67754.0719
2020-05-29 10:00 | 7.8985 | 8.314 | 356.2907 | 3336.5134 | 50047.7008
2020-05-29 11:00 | 7.8462 | 8.2588 | 355.1715 | 3274.4552 | 49116.8287
2020-05-29 12:00 | 7.2538 | 7.6353 | 358.6496 | 2597.1928 | 38957.8926
2020-05-29 13:00 | 6.8085 | 7.1666 | 359.2313 | 2143.2816 | 32149.2243
2020-05-29 14:00 | 5.371 | 5.6534 | 354.3243 | 1026.8325 | 15402.4876
2020-05-29 15:00 | 4.9655 | 5.2267 | 353.5348 | 798.7786 | 11981.6783
2020-05-29 16:00 | 4.8823 | 5.1391 | 344.5387 | 754.8112 | 11322.1682
2020-05-29 17:00 | 5.0322 | 5.2969 | 334.127 | 834.0247 | 12510.3708
2020-05-29 18:00 | 5.4902 | 5.779 | 328.6033 | 1101.1493 | 16517.2394
2020-05-29 19:00 | 5.3461 | 5.6273 | 330.4753 | 1011.3333 | 15170
2020-05-29 20:00 | 4.6886 | 4.9352 | 331.0233 | 657.638 | 9864.5703
2020-05-29 21:00 | 4.478 | 4.7135 | 325.0525 | 564.1141 | 8461.7119
2020-05-29 22:00 | 4.5584 | 4.7982 | 323.1907 | 599.8349 | 8997.5234
2020-05-29 23:00 | 4.3878 | 4.6186 | 325.2487 | 524.0528 | 7860.7918
2020-05-30 00:00 | 4.3811 | 4.6115 | 332.754 | 521.0503 | 7815.7549
2020-05-30 01:00 | 4.079 | 4.2935 | 340.5088 | 401.3244 | 6019.8655
2020-05-30 02:00 | 3.3634 | 3.5403 | 345.7156 | 166.5393 | 2498.0898
2020-05-30 03:00 | 2.9843 | 3.1413 | 330.5912 | 78.2314 | 1173.4713
2020-05-30 04:00 | 3.6515 | 3.8436 | 311.3485 | 253.2652 | 3798.9777
2020-05-30 05:00 | 4.5964 | 4.8382 | 314.1594 | 616.7108 | 9250.6623
2020-05-30 06:00 | 4.3118 | 4.5386 | 321.8234 | 490.2781 | 7354.1714
2020-05-30 07:00 | 4.6345 | 4.8782 | 312.6497 | 633.6122 | 9504.1826
2020-05-30 08:00 | 4.9616 | 5.2225 | 301.5094 | 796.7076 | 11950.6144
2020-05-30 09:00 | 6.1027 | 6.4237 | 290.4452 | 1528.5626 | 22928.4391
2020-05-30 10:00 | 7.1445 | 7.5202 | 285.2001 | 2475.4073 | 37131.1098
2020-05-30 11:00 | 7.8913 | 8.3064 | 286.3866 | 3327.9738 | 49919.6069
2020-05-30 12:00 | 8.0954 | 8.5211 | 282.755 | 3569.8272 | 53547.4075
2020-05-30 13:00 | 8.7684 | 9.2296 | 275.5075 | 4355.6559 | 65334.8391
2020-05-30 14:00 | 9.8679 | 10.3869 | 268.7675 | 5281.9388 | 79229.0818
2020-05-30 15:00 | 9.9032 | 10.4241 | 261.5374 | 5303.6605 | 79554.9082
2020-05-30 16:00 | 9.2235 | 9.7086 | 251.5855 | 4816.4618 | 72246.9268
2020-05-30 17:00 | 8.3837 | 8.8246 | 239.7955 | 3912.1388 | 58682.0816
2020-05-30 18:00 | 8.178 | 8.6081 | 228.2659 | 3667.9508 | 55019.2617
2020-05-30 19:00 | 8.0491 | 8.4724 | 211.7822 | 3514.9566 | 52724.3489
2020-05-30 20:00 | 8.2934 | 8.7296 | 202.1186 | 3805.0129 | 57075.1938
2020-05-30 21:00 | 8.272 | 8.707 | 197.2413 | 3779.548 | 56693.2195
2020-05-30 22:00 | 7.6747 | 8.0784 | 190.2055 | 3071.2656 | 46068.9844
2020-05-30 23:00 | 7.1958 | 7.5743 | 183.8658 | 2532.6191 | 37989.287
2020-05-31 00:00 | 6.6434 | 6.9928 | 178.2093 | 1982.1822 | 29732.7337
2020-05-31 01:00 | 6.3057 | 6.6374 | 173.515 | 1693.5361 | 25403.0418
2020-05-31 02:00 | 6.1619 | 6.486 | 171.4078 | 1572.1766 | 23582.6497
2020-05-31 03:00 | 6.0361 | 6.3536 | 168.1581 | 1479.4863 | 22192.2939
2020-05-31 04:00 | 6.3487 | 6.6826 | 169.1782 | 1730.3031 | 25954.5462
2020-05-31 05:00 | 6.2458 | 6.5743 | 169.665 | 1642.2927 | 24634.39
2020-05-31 06:00 | 5.6496 | 5.9467 | 161.1887 | 1200.4544 | 18006.8159
2020-05-31 07:00 | 5.2532 | 5.5295 | 150.7489 | 953.4684 | 14302.0258
2020-05-31 08:00 | 5.2584 | 5.535 | 141.4891 | 956.6969 | 14350.4534
2020-05-31 09:00 | 5.2468 | 5.5227 | 139.7481 | 949.4526 | 14241.7888
2020-05-31 10:00 | 5.7442 | 6.0463 | 148.84 | 1264.4372 | 18966.5576
2020-05-31 11:00 | 5.1471 | 5.4178 | 146.1859 | 894.7428 | 13421.1422
2020-05-31 12:00 | 5.046 | 5.3114 | 144.7655 | 841.3227 | 12619.8402
2020-05-31 13:00 | 3.9355 | 4.1425 | 138.9812 | 348.1573 | 5222.3595
2020-05-31 14:00 | 2.7539 | 2.8987 | 123.3996 | 0 | 0
2020-05-31 15:00 | 1.8773 | 1.9761 | 97.3624 | 0 | 0
2020-05-31 16:00 | 2.0099 | 2.1156 | 66.4342 | 0 | 0
2020-05-31 17:00 | 2.8255 | 2.9741 | 46.2395 | 0 | 0
2020-05-31 18:00 | 3.75 | 3.9472 | 42.0468 | 282.9092 | 4243.6373
2020-05-31 19:00 | 4.237 | 4.4598 | 43.2633 | 459.8576 | 6897.8634
2020-05-31 20:00 | 4.3222 | 4.5495 | 38.8751 | 494.88 | 7423.2005
2020-05-31 21:00 | 4.3506 | 4.5795 | 30.2377 | 507.5344 | 7613.0153
2020-05-31 22:00 | 4.9271 | 5.1863 | 24.0175 | 778.5021 | 11677.531
2020-05-31 23:00 | 5.4031 | 5.6872 | 15.4869 | 1046.8484 | 15702.7266
2020-06-01 00:00 | 6.4103 | 6.7474 | 11.8388 | 1782.9233 | 26743.8497
2020-06-01 01:00 | 7.6028 | 8.0026 | 11.7066 | 2985.9816 | 44789.7239
2020-06-01 02:00 | 8.2517 | 8.6857 | 14.9543 | 3755.4249 | 56331.3735
2020-06-01 03:00 | 8.7778 | 9.2395 | 16.1436 | 4366.2801 | 65494.2011
2020-06-01 04:00 | 9.4732 | 9.9714 | 16.1401 | 5032.5187 | 75487.7807
2020-06-01 05:00 | 9.8303 | 10.3473 | 17.3554 | 5258.8517 | 78882.7756
2020-06-01 06:00 | 9.4033 | 9.8978 | 20.1103 | 4972.0124 | 74580.1861
2020-06-01 07:00 | 8.2468 | 8.6805 | 16.4059 | 3749.6392 | 56244.5878
2020-06-01 08:00 | 7.7233 | 8.1295 | 10.1618 | 3128.7793 | 46931.6891
2020-06-01 09:00 | 7.8443 | 8.2569 | 6.5948 | 3272.243 | 49083.6445
2020-06-01 10:00 | 8.0718 | 8.4964 | 357.4543 | 3541.8997 | 53128.4949
2020-06-01 11:00 | 8.8374 | 9.3022 | 359.2891 | 4433.3494 | 66500.2414
2020-06-01 12:00 | 8.7319 | 9.1912 | 358.3331 | 4314.5551 | 64718.3268
2020-06-01 13:00 | 8.5165 | 8.9644 | 355.2261 | 4069.8472 | 61047.7077
2020-06-01 14:00 | 8.9098 | 9.3784 | 355.3621 | 4514.85 | 67722.7494
2020-06-01 15:00 | 8.9806 | 9.4529 | 357.4317 | 4594.6462 | 68919.6933
2020-06-01 16:00 | 7.9486 | 8.3667 | 354.4216 | 3395.8992 | 50938.4875
2020-06-01 17:00 | 6.3406 | 6.674 | 342.5899 | 1723.3171 | 25849.757
2020-06-01 18:00 | 6.6025 | 6.9498 | 329.7747 | 1947.2361 | 29208.542
2020-06-01 19:00 | 7.1353 | 7.5106 | 328.6638 | 2465.1789 | 36977.6839
2020-06-01 20:00 | 6.8154 | 7.1738 | 325.6645 | 2150.011 | 32250.1644
2020-06-01 21:00 | 6.3371 | 6.6704 | 320.7897 | 1720.3867 | 25805.8006
2020-06-01 22:00 | 5.7902 | 6.0948 | 320.8982 | 1298.3394 | 19475.0909
2020-06-01 23:00 | 4.7213 | 4.9696 | 314.4477 | 672.1836 | 10082.7542
2020-06-02 00:00 | 4.3219 | 4.5492 | 288.482 | 494.7482 | 7421.2224
2020-06-02 01:00 | 5.5287 | 5.8195 | 269.2904 | 1125.1596 | 16877.3947
2020-06-02 02:00 | 5.4988 | 5.788 | 268.4069 | 1106.4998 | 16597.4968
2020-06-02 03:00 | 4.9831 | 5.2451 | 263.8011 | 808.0583 | 12120.8738
2020-06-02 04:00 | 4.7382 | 4.9874 | 256.7751 | 679.6952 | 10195.4275
2020-06-02 05:00 | 4.3548 | 4.5839 | 249.7589 | 509.3982 | 7640.9731
2020-06-02 06:00 | 3.8259 | 4.0271 | 245.3209 | 307.5393 | 4613.0896
2020-06-02 07:00 | 3.4284 | 3.6087 | 227.6122 | 186.0977 | 2791.4654
2020-06-02 08:00 | 3.6009 | 3.7903 | 206.5973 | 238.0215 | 3570.3222
2020-06-02 09:00 | 4.3071 | 4.5336 | 193.2564 | 488.1877 | 7322.8154
2020-06-02 10:00 | 5.0272 | 5.2916 | 209.2027 | 831.3877 | 12470.8158
2020-06-02 11:00 | 4.7962 | 5.0484 | 209.5139 | 709.3075 | 10639.6118
2020-06-02 12:00 | 4.3983 | 4.6296 | 206.7476 | 528.6947 | 7930.42
2020-06-02 13:00 | 4.1569 | 4.3755 | 207.2031 | 430.1801 | 6452.7019
2020-06-02 14:00 | 4.4932 | 4.7295 | 200.8459 | 570.8499 | 8562.748
2020-06-02 15:00 | 5.8136 | 6.1193 | 213.3363 | 1315.5419 | 19733.1282
2020-06-02 16:00 | 4.4905 | 4.7266 | 216.4071 | 569.641 | 8544.615
2020-06-02 17:00 | 4.2919 | 4.5176 | 205.2707 | 481.4305 | 7221.457
2020-06-02 18:00 | 4.6763 | 4.9222 | 190.3375 | 652.1861 | 9782.7908
2020-06-02 19:00 | 5.5993 | 5.8937 | 184.1447 | 1169.0968 | 17536.4525
2020-06-02 20:00 | 5.9432 | 6.2558 | 182.2988 | 1411.0675 | 21166.0128
2020-06-02 21:00 | 5.8361 | 6.143 | 179.5313 | 1332.1124 | 19981.6864
2020-06-02 22:00 | 6.7568 | 7.1121 | 170.3392 | 2092.4991 | 31387.4862
2020-06-02 23:00 | 6.8496 | 7.2099 | 172.4925 | 2183.5921 | 32753.8815
2020-06-03 00:00 | 6.9382 | 7.3031 | 173.7008 | 2270.5358 | 34058.0365
2020-06-03 01:00 | 7.2187 | 7.5984 | 168.7521 | 2558.107 | 38371.6052
2020-06-03 02:00 | 7.1819 | 7.5597 | 169.1488 | 2517.1383 | 37757.0749
2020-06-03 03:00 | 6.8706 | 7.232 | 169.3527 | 2204.2237 | 33063.3561
2020-06-03 04:00 | 7.9045 | 8.3202 | 173.4509 | 3343.5481 | 50153.2222
2020-06-03 05:00 | 7.9295 | 8.3466 | 177.1905 | 3373.2311 | 50598.4664
2020-06-03 06:00 | 7.3095 | 7.694 | 172.1029 | 2659.2327 | 39888.49
2020-06-03 07:00 | 7.1813 | 7.559 | 169.4244 | 2516.4156 | 37746.2335
2020-06-03 08:00 | 6.6126 | 6.9604 | 164.1292 | 1955.8089 | 29337.1333
2020-06-03 09:00 | 6.9508 | 7.3164 | 169.7604 | 2282.8847 | 34243.2708
2020-06-03 10:00 | 6.0275 | 6.3446 | 182.6171 | 1473.191 | 22097.8643
2020-06-03 11:00 | 4.9546 | 5.2152 | 176.2284 | 793.0198 | 11895.2965
2020-06-03 12:00 | 5.799 | 6.104 | 192.4701 | 1304.7668 | 19571.5021
2020-06-03 13:00 | 4.3037 | 4.53 | 192.7707 | 486.6602 | 7299.9025
2020-06-03 14:00 | 4.3688 | 4.5986 | 195.3233 | 515.6042 | 7734.0637
2020-06-03 15:00 | 3.6497 | 3.8417 | 192.5188 | 252.7128 | 3790.6924
2020-06-03 16:00 | 3.7582 | 3.9559 | 169.5339 | 285.3826 | 4280.7386
2020-06-03 17:00 | 4.8586 | 5.1141 | 191.2179 | 742.282 | 11134.2298
2020-06-03 18:00 | 4.4848 | 4.7206 | 208.5969 | 567.1113 | 8506.67
2020-06-03 19:00 | 4.539 | 4.7777 | 209.5231 | 591.1941 | 8867.9112
2020-06-03 20:00 | 5.0341 | 5.2989 | 213.0253 | 835.0364 | 12525.5465
2020-06-03 21:00 | 5.3871 | 5.6704 | 219.4372 | 1036.8937 | 15553.406
2020-06-03 22:00 | 4.491 | 4.7272 | 228.2526 | 569.8607 | 8547.9101
2020-06-03 23:00 | 4.5302 | 4.7684 | 224.8678 | 587.2755 | 8809.1319
2020-06-04 00:00 | 5.8687 | 6.1774 | 226.9189 | 1356.1673 | 20342.5097
2020-06-04 01:00 | 5.8186 | 6.1246 | 232.4098 | 1319.2273 | 19788.4094
2020-06-04 02:00 | 5.3877 | 5.6711 | 230.945 | 1037.2854 | 15559.281
2020-06-04 03:00 | 5.2153 | 5.4896 | 220.7527 | 930.7922 | 13961.8836
2020-06-04 04:00 | 5.0531 | 5.3189 | 211.813 | 845.0629 | 12675.9428
2020-06-04 05:00 | 4.2661 | 4.4905 | 212.0472 | 470.6484 | 7059.7267
2020-06-04 06:00 | 4.7302 | 4.9789 | 218.2024 | 676.1108 | 10141.6619
2020-06-04 07:00 | 5.5445 | 5.8361 | 221.9417 | 1134.9579 | 17024.369
2020-06-04 08:00 | 5.6567 | 5.9542 | 224.5106 | 1204.8627 | 18072.9406
2020-06-04 09:00 | 5.6133 | 5.9086 | 227.905 | 1177.8781 | 17668.1719
2020-06-04 10:00 | 5.4738 | 5.7617 | 228.1787 | 1090.9175 | 16363.7624
2020-06-04 11:00 | 5.5933 | 5.8875 | 227.9515 | 1165.4068 | 17481.1023
2020-06-04 12:00 | 5.8327 | 6.1394 | 227.1311 | 1329.6134 | 19944.2013
2020-06-04 13:00 | 5.7403 | 6.0422 | 229.2415 | 1261.564 | 18923.4594
2020-06-04 14:00 | 5.485 | 5.7734 | 229.4979 | 1097.8771 | 16468.1566
2020-06-04 15:00 | 4.6427 | 4.8869 | 228.7721 | 637.273 | 9559.0943
2020-06-04 16:00 | 3.7622 | 3.9601 | 216.8596 | 286.5853 | 4298.78
2020-06-04 17:00 | 3.7963 | 3.9959 | 199.2436 | 296.831 | 4452.4643
2020-06-04 18:00 | 4.8412 | 5.0959 | 192.846 | 733.1191 | 10996.7869
2020-06-04 19:00 | 5.4106 | 5.6952 | 193.4067 | 1051.5489 | 15773.2339
2020-06-04 20:00 | 5.7512 | 6.0536 | 188.8837 | 1269.5534 | 19043.3012
2020-06-04 21:00 | 6.8404 | 7.2001 | 189.0067 | 2174.5262 | 32617.893
2020-06-04 22:00 | 6.6421 | 6.9915 | 194.1109 | 1981.0779 | 29716.1686
2020-06-04 23:00 | 6.9822 | 7.3494 | 206.6467 | 2313.6172 | 34704.2581
2020-06-05 00:00 | 6.864 | 7.225 | 214.9869 | 2197.6817 | 32965.2252
2020-06-05 01:00 | 6.8338 | 7.1932 | 212.8278 | 2168.0776 | 32521.1644
2020-06-05 02:00 | 6.6477 | 6.9974 | 210.1369 | 1985.8628 | 29787.9423
2020-06-05 03:00 | 6.3674 | 6.7023 | 206.0306 | 1746.2661 | 26193.9922
2020-06-05 04:00 | 6.465 | 6.805 | 203.4384 | 1829.6977 | 27445.4656
2020-06-05 05:00 | 5.5628 | 5.8554 | 204.4186 | 1146.4101 | 17196.1515
2020-06-05 06:00 | 5.0639 | 5.3303 | 208.2518 | 850.8015 | 12762.0229
2020-06-05 07:00 | 5.4127 | 5.6973 | 211.1172 | 1052.8271 | 15792.4069
2020-06-05 08:00 | 5.9341 | 6.2462 | 211.9013 | 1404.3274 | 21064.9105
2020-06-05 09:00 | 5.6959 | 5.9955 | 208.2794 | 1229.3315 | 18439.9723
2020-06-05 10:00 | 4.098 | 4.3135 | 198.9399 | 408.3565 | 6125.3475
2020-06-05 11:00 | 3.0465 | 3.2067 | 184.6627 | 92.2413 | 1383.619
2020-06-05 12:00 | 3.1074 | 3.2708 | 173.8814 | 105.9565 | 1589.348
2020-06-05 13:00 | 3.463 | 3.6451 | 170.2579 | 196.4977 | 2947.4649
2020-06-05 14:00 | 4.0569 | 4.2703 | 173.2231 | 393.1332 | 5896.9979
2020-06-05 15:00 | 4.2353 | 4.458 | 178.4454 | 459.2211 | 6888.3162
2020-06-05 16:00 | 3.7825 | 3.9815 | 169.7354 | 292.6986 | 4390.4796
2020-06-05 17:00 | 4.266 | 4.4904 | 158.4209 | 470.6081 | 7059.1209
2020-06-05 18:00 | 5.3078 | 5.587 | 159.6974 | 987.5018 | 14812.5266
2020-06-05 19:00 | 5.8854 | 6.1949 | 170.308 | 1368.4424 | 20526.6358
2020-06-05 20:00 | 5.9221 | 6.2336 | 171.5411 | 1395.4911 | 20932.3665
2020-06-05 21:00 | 6.199 | 6.5251 | 167.8919 | 1602.3692 | 24035.5382
2020-06-05 22:00 | 6.3744 | 6.7097 | 166.8836 | 1752.2704 | 26284.0556
2020-06-05 23:00 | 7.3279 | 7.7133 | 168.3304 | 2679.6324 | 40194.4859
2020-06-06 00:00 | 7.4906 | 7.8846 | 177.7775 | 2860.8921 | 42913.382
2020-06-06 01:00 | 7.4396 | 7.8309 | 181.4719 | 2804.0617 | 42060.9249
2020-06-06 02:00 | 7.4358 | 7.8269 | 184.8596 | 2799.8446 | 41997.6697
2020-06-06 03:00 | 7.3351 | 7.7209 | 191.385 | 2687.7499 | 40316.2481
2020-06-06 04:00 | 6.7232 | 7.0768 | 195.0876 | 2059.5616 | 30893.4246
2020-06-06 05:00 | 5.3626 | 5.6446 | 197.6403 | 1021.6124 | 15324.186
2020-06-06 06:00 | 4.7989 | 5.0513 | 208.1053 | 710.744 | 10661.1606
2020-06-06 07:00 | 4.3052 | 4.5316 | 225.4483 | 487.3293 | 7309.9394
2020-06-06 08:00 | 3.5734 | 3.7614 | 242.5181 | 229.7488 | 3446.2313
2020-06-06 09:00 | 3.0523 | 3.2128 | 250.5639 | 93.5386 | 1403.0792
2020-06-06 10:00 | 1.8652 | 1.9633 | 225.4431 | 0 | 0
2020-06-06 11:00 | 2.4345 | 2.5626 | 195.1933 | 0 | 0
2020-06-06 12:00 | 4.0781 | 4.2926 | 200.2728 | 400.9938 | 6014.9069
2020-06-06 13:00 | 5.3552 | 5.6369 | 215.2979 | 1017.0304 | 15255.4564
2020-06-06 14:00 | 4.0313 | 4.2433 | 220.717 | 383.6539 | 5754.8083
2020-06-06 15:00 | 2.5246 | 2.6574 | 218.8373 | 0 | 0
2020-06-06 16:00 | 1.9029 | 2.0029 | 220.8187 | 0 | 0
2020-06-06 17:00 | 1.1608 | 1.2219 | 208.1645 | 0 | 0
2020-06-06 18:00 | 0.88081 | 0.92713 | 157.9411 | 0 | 0
2020-06-06 19:00 | 1.5507 | 1.6323 | 125.8144 | 0 | 0
2020-06-06 20:00 | 2.1665 | 2.2804 | 120.7387 | 0 | 0
2020-06-06 21:00 | 3.0057 | 3.1638 | 120.359 | 83.0515 | 1245.7719
2020-06-06 22:00 | 4.8491 | 5.1042 | 128.002 | 737.2896 | 11059.3436
2020-06-06 23:00 | 5.9603 | 6.2738 | 128.9655 | 1423.6303 | 21354.4546
2020-06-07 00:00 | 6.1542 | 6.4779 | 135.2757 | 1566.5355 | 23498.0323
2020-06-07 01:00 | 5.8033 | 6.1086 | 146.8906 | 1307.9996 | 19619.9941
2020-06-07 02:00 | 5.3161 | 5.5957 | 158.9427 | 992.6777 | 14890.1651
2020-06-07 03:00 | 5.1775 | 5.4498 | 163.14 | 910.8232 | 13662.3485
2020-06-07 04:00 | 5.2966 | 5.5752 | 160.6541 | 980.5091 | 14707.6367
2020-06-07 05:00 | 4.7226 | 4.971 | 156.1441 | 672.7754 | 10091.6304
2020-06-07 06:00 | 4.2416 | 4.4646 | 153.3967 | 461.5529 | 6923.2941
2020-06-07 07:00 | 3.9963 | 4.2065 | 149.1024 | 370.6822 | 5560.2328
2020-06-07 08:00 | 4.1568 | 4.3755 | 144.8138 | 430.1597 | 6452.3957
2020-06-07 09:00 | 4.7679 | 5.0186 | 142.652 | 694.3589 | 10415.3828
2020-06-07 10:00 | 5.3792 | 5.6621 | 141.8957 | 1031.9729 | 15479.5934
2020-06-07 11:00 | 6.1133 | 6.4348 | 145.3768 | 1536.3602 | 23045.4032
2020-06-07 12:00 | 6.4825 | 6.8235 | 146.85 | 1844.6624 | 27669.9365
2020-06-07 13:00 | 6.5291 | 6.8725 | 147.6326 | 1884.4402 | 28266.6026
2020-06-07 14:00 | 6.0074 | 6.3233 | 147.6117 | 1458.3133 | 21874.6997
2020-06-07 15:00 | 5.4506 | 5.7373 | 139.0253 | 1076.4937 | 16147.4051
2020-06-07 16:00 | 5.9672 | 6.281 | 132.0645 | 1428.7082 | 21430.6234
2020-06-07 17:00 | 6.4028 | 6.7396 | 130.2542 | 1776.5338 | 26648.0077
2020-06-07 18:00 | 6.8985 | 7.2614 | 129.2068 | 2231.5792 | 33473.6886
2020-06-07 19:00 | 7.367 | 7.7545 | 128.2866 | 2723.2247 | 40848.3704
2020-06-07 20:00 | 7.6118 | 8.0122 | 130.1047 | 2996.7112 | 44950.6673
2020-06-07 21:00 | 7.831 | 8.2429 | 133.8472 | 3256.4817 | 48847.2256
2020-06-07 22:00 | 7.8024 | 8.2127 | 138.9266 | 3222.5505 | 48338.258
2020-06-07 23:00 | 7.6594 | 8.0623 | 141.4341 | 3053.1053 | 45796.5793
2020-06-08 00:00 | 7.4341 | 7.825 | 146.0553 | 2797.895 | 41968.4249
2020-06-08 01:00 | 7.3963 | 7.7853 | 148.898 | 2755.866 | 41337.9898
2020-06-08 02:00 | 7.2276 | 7.6078 | 150.6526 | 2568.0328 | 38520.4925
2020-06-08 03:00 | 6.8797 | 7.2416 | 151.2883 | 2213.1308 | 33196.9621
2020-06-08 04:00 | 6.086 | 6.4061 | 148.0453 | 1516.2413 | 22743.619
2020-06-08 05:00 | 4.6212 | 4.8642 | 141.3081 | 627.697 | 9415.455
2020-06-08 06:00 | 3.5996 | 3.7889 | 131.6388 | 237.6184 | 3564.2766
2020-06-08 07:00 | 3.4375 | 3.6182 | 128.1879 | 188.8192 | 2832.2883
2020-06-08 08:00 | 3.6882 | 3.8822 | 123.9729 | 264.3062 | 3964.5931
2020-06-08 09:00 | 4.9026 | 5.1604 | 128.9411 | 765.5341 | 11483.0116
2020-06-08 10:00 | 5.1296 | 5.3994 | 134.3346 | 885.5162 | 13282.7424
2020-06-08 11:00 | 5.5028 | 5.7922 | 124.0112 | 1109.0087 | 16635.131
2020-06-08 12:00 | 5.9371 | 6.2494 | 118.5367 | 1406.5461 | 21098.1919
2020-06-08 13:00 | 5.992 | 6.3071 | 116.3688 | 1446.9967 | 21704.9511
2020-06-08 14:00 | 5.7901 | 6.0946 | 111.8323 | 1298.2535 | 19473.8029
2020-06-08 15:00 | 5.4143 | 5.699 | 105.9224 | 1053.8145 | 15807.2176
2020-06-08 16:00 | 5.8003 | 6.1054 | 101.2402 | 1305.7662 | 19586.4929
2020-06-08 17:00 | 6.2508 | 6.5796 | 99.4736 | 1646.5963 | 24698.9445
2020-06-08 18:00 | 6.8684 | 7.2296 | 100.8407 | 2202.0027 | 33030.041
2020-06-08 19:00 | 7.5283 | 7.9242 | 106.3201 | 2902.8544 | 43542.8162
2020-06-08 20:00 | 7.9309 | 8.3481 | 108.8231 | 3374.9247 | 50623.8706
2020-06-08 21:00 | 8.0451 | 8.4682 | 113.2826 | 3510.2381 | 52653.5718
2020-06-08 22:00 | 7.4934 | 7.8875 | 119.9887 | 2863.9569 | 42959.353
2020-06-08 23:00 | 5.8058 | 6.1112 | 100.8052 | 1309.8428 | 19647.6416
2020-06-09 00:00 | 6.6448 | 6.9943 | 74.3687 | 1983.3432 | 29750.1483
2020-06-09 01:00 | 6.5709 | 6.9165 | 72.9384 | 1920.2137 | 28803.2049
2020-06-09 02:00 | 7.2492 | 7.6305 | 72.0139 | 2592.0734 | 38881.1011
2020-06-09 03:00 | 7.226 | 7.606 | 72.9285 | 2566.1721 | 38492.5822
2020-06-09 04:00 | 6.5043 | 6.8464 | 78.321 | 1863.2989 | 27949.4835
2020-06-09 05:00 | 5.9816 | 6.2962 | 85.3298 | 1439.3102 | 21589.6528
2020-06-09 06:00 | 5.4782 | 5.7663 | 95.1763 | 1093.6717 | 16405.0752
2020-06-09 07:00 | 5.3446 | 5.6257 | 103.0339 | 1010.3959 | 15155.9392
2020-06-09 08:00 | 5.7865 | 6.0909 | 103.6576 | 1295.6207 | 19434.3104
2020-06-09 09:00 | 6.6392 | 6.9884 | 107.2553 | 1978.5765 | 29678.6472
2020-06-09 10:00 | 6.383 | 6.7187 | 111.7586 | 1759.6215 | 26394.322
2020-06-09 11:00 | 6.3567 | 6.691 | 121.7329 | 1737.1146 | 26056.7192
2020-06-09 12:00 | 6.0083 | 6.3243 | 129.7868 | 1459.0355 | 21885.5318
2020-06-09 13:00 | 5.8595 | 6.1677 | 132.4838 | 1349.3909 | 20240.8628
2020-06-09 14:00 | 5.7692 | 6.0727 | 138.0293 | 1282.8699 | 19243.0487
2020-06-09 15:00 | 5.3174 | 5.5971 | 141.6723 | 993.4583 | 14901.8749
2020-06-09 16:00 | 4.544 | 4.783 | 140.6186 | 593.4208 | 8901.3119
2020-06-09 17:00 | 4.0832 | 4.298 | 137.313 | 402.8822 | 6043.2337
2020-06-09 18:00 | 3.637 | 3.8282 | 131.8023 | 248.8763 | 3733.1438
2020-06-09 19:00 | 3.9398 | 4.147 | 126.7796 | 349.7347 | 5246.02
2020-06-09 20:00 | 4.0279 | 4.2398 | 127.8936 | 382.4 | 5736.0007
2020-06-09 21:00 | 4.445 | 4.6787 | 128.4401 | 549.4279 | 8241.4185
2020-06-09 22:00 | 4.2915 | 4.5172 | 160.0327 | 481.2682 | 7219.0232
2020-06-09 23:00 | 4.106 | 4.3219 | 171.9359 | 411.3107 | 6169.6609
2020-06-10 00:00 | 3.6782 | 3.8717 | 179.8695 | 261.3072 | 3919.6083
2020-06-10 01:00 | 3.5054 | 3.6898 | 182.243 | 209.2825 | 3139.2382
2020-06-10 02:00 | 3.3995 | 3.5783 | 173.1449 | 177.3973 | 2660.9598
2020-06-10 03:00 | 4.0072 | 4.218 | 163.7641 | 374.7304 | 5620.9559
2020-06-10 04:00 | 4.4368 | 4.6701 | 160.727 | 545.7944 | 8186.9158
2020-06-10 05:00 | 3.689 | 3.883 | 157.9077 | 264.5347 | 3968.0207
2020-06-10 06:00 | 3.0896 | 3.2521 | 149.3059 | 101.9503 | 1529.2539
2020-06-10 07:00 | 3.4971 | 3.681 | 146.4802 | 206.7792 | 3101.6884
2020-06-10 08:00 | 3.9637 | 4.1721 | 148.8989 | 358.586 | 5378.79
2020-06-10 09:00 | 4.2558 | 4.4797 | 148.5763 | 466.837 | 7002.5546
2020-06-10 10:00 | 4.0484 | 4.2613 | 148.076 | 389.9926 | 5849.8893
2020-06-10 11:00 | 4.2814 | 4.5066 | 143.1767 | 476.7644 | 7151.4653
2020-06-10 12:00 | 4.831 | 5.0851 | 138.5014 | 727.7269 | 10915.9034
2020-06-10 13:00 | 5.4309 | 5.7165 | 135.3231 | 1064.1616 | 15962.4245
2020-06-10 14:00 | 5.7299 | 6.0313 | 135.8636 | 1253.9175 | 18808.7619
2020-06-10 15:00 | 5.3252 | 5.6053 | 132.3563 | 998.3148 | 14974.7214
2020-06-10 16:00 | 5.3214 | 5.6013 | 121.1983 | 995.9801 | 14939.7021
2020-06-10 17:00 | 6.0449 | 6.3628 | 111.885 | 1485.9702 | 22289.5537
2020-06-10 18:00 | 6.855 | 7.2156 | 108.648 | 2188.9263 | 32833.895
2020-06-10 19:00 | 7.2994 | 7.6833 | 112.5902 | 2647.891 | 39718.3652
2020-06-10 20:00 | 7.3517 | 7.7383 | 119.792 | 2706.1729 | 40592.5938
2020-06-10 21:00 | 6.4084 | 6.7454 | 128.812 | 1781.3022 | 26719.5332
2020-06-10 22:00 | 4.7236 | 4.9721 | 131.0652 | 673.2171 | 10098.2567
2020-06-10 23:00 | 5.9837 | 6.2984 | 128.2711 | 1440.8749 | 21613.1232
2020-06-11 00:00 | 5.7203 | 6.0211 | 118.9341 | 1246.7937 | 18701.9059
2020-06-11 01:00 | 7.063 | 7.4345 | 102.5795 | 2392.9734 | 35894.6015
2020-06-11 02:00 | 7.0909 | 7.4638 | 106.3963 | 2420.2616 | 36303.9243
2020-06-11 03:00 | 6.9326 | 7.2972 | 111.601 | 2264.9588 | 33974.382
2020-06-11 04:00 | 6.3209 | 6.6533 | 114.6133 | 1706.5051 | 25597.5759
2020-06-11 05:00 | 5.3809 | 5.6639 | 112.4732 | 1033.0285 | 15495.4268
2020-06-11 06:00 | 4.691 | 4.9377 | 110.0985 | 658.7049 | 9880.5742
2020-06-11 07:00 | 5.1977 | 5.4711 | 112.5856 | 921.5035 | 13822.5527
2020-06-11 08:00 | 6.1425 | 6.4655 | 113.3436 | 1557.885 | 23368.2746
2020-06-11 09:00 | 7.4522 | 7.8441 | 112.3731 | 2818.0695 | 42271.0427
2020-06-11 10:00 | 5.3713 | 5.6538 | 100.3571 | 1027.0419 | 15405.6278
2020-06-11 11:00 | 4.2829 | 4.5081 | 96.7594 | 477.4208 | 7161.3123
2020-06-11 12:00 | 6.0436 | 6.3615 | 93.5013 | 1485.0558 | 22275.8374
2020-06-11 13:00 | 6.1132 | 6.4348 | 92.6016 | 1536.3303 | 23044.954
2020-06-11 14:00 | 6.2017 | 6.5279 | 85.4137 | 1604.6328 | 24069.4916
2020-06-11 15:00 | 6.4736 | 6.8141 | 73.7864 | 1837.0412 | 27555.6178
2020-06-11 16:00 | 7.4151 | 7.8051 | 73.6013 | 2776.8359 | 41652.539
2020-06-11 17:00 | 8.1393 | 8.5674 | 78.8631 | 3622.0435 | 54330.6532
2020-06-11 18:00 | 8.3898 | 8.8311 | 83.1569 | 3919.4893 | 58792.3389
2020-06-11 19:00 | 8.4582 | 8.9031 | 81.6469 | 4000.6993 | 60010.4899
2020-06-11 20:00 | 8.5634 | 9.0138 | 78.3853 | 4124.7837 | 61871.7549
2020-06-11 21:00 | 8.8084 | 9.2717 | 77.1399 | 4400.6683 | 66010.0249
2020-06-11 22:00 | 9.5054 | 10.0053 | 78.737 | 5059.0991 | 75886.4858
2020-06-11 23:00 | 9.3767 | 9.8699 | 80.0692 | 4949.0545 | 74235.8171
2020-06-12 00:00 | 9.1403 | 9.621 | 82.1913 | 4744.4849 | 71167.2733
2020-06-12 01:00 | 8.8442 | 9.3093 | 83.605 | 4440.9616 | 66614.424
2020-06-12 02:00 | 8.4946 | 8.9413 | 84.8982 | 4043.8363 | 60657.5444
2020-06-12 03:00 | 7.9814 | 8.4012 | 84.0274 | 3434.7333 | 51520.9989
2020-06-12 04:00 | 7.2622 | 7.6442 | 79.8733 | 2606.5632 | 39098.4479
2020-06-12 05:00 | 5.9634 | 6.2771 | 71.9737 | 1425.9667 | 21389.5008
2020-06-12 06:00 | 5.7638 | 6.067 | 68.0839 | 1278.8748 | 19183.1213
2020-06-12 07:00 | 5.7441 | 6.0462 | 63.2438 | 1264.3528 | 18965.2915
2020-06-12 08:00 | 5.8479 | 6.1555 | 56.283 | 1340.8587 | 20112.8806
2020-06-12 09:00 | 6.2312 | 6.559 | 49.8282 | 1629.8756 | 24448.1333
2020-06-12 10:00 | 6.8235 | 7.1824 | 45.8334 | 2157.9666 | 32369.4988
2020-06-12 11:00 | 8.336 | 8.7745 | 49.9735 | 3855.6025 | 57834.0375
2020-06-12 12:00 | 9.1276 | 9.6077 | 56.2901 | 4733.4928 | 71002.3927
2020-06-12 13:00 | 8.8562 | 9.322 | 62.8899 | 4454.5507 | 66818.2607
2020-06-12 14:00 | 7.817 | 8.2282 | 65.5144 | 3239.9182 | 48598.7727
2020-06-12 15:00 | 6.1321 | 6.4546 | 74.4637 | 1550.2274 | 23253.4105
2020-06-12 16:00 | 4.6185 | 4.8614 | 68.5925 | 626.5099 | 9397.6484
2020-06-12 17:00 | 6.1665 | 6.4908 | 43.9989 | 1575.5717 | 23633.5757
2020-06-12 18:00 | 7.9749 | 8.3944 | 44.2439 | 3427.0677 | 51406.0155
2020-06-12 19:00 | 8.4656 | 8.9109 | 50.6963 | 4009.4529 | 60141.7939
2020-06-12 20:00 | 8.0198 | 8.4416 | 53.26 | 3480.2313 | 52203.47
2020-06-12 21:00 | 7.4513 | 7.8432 | 55.6973 | 2817.1018 | 42256.5274
2020-06-12 22:00 | 8.2188 | 8.6511 | 55.2525 | 3716.4235 | 55746.352
2020-06-12 23:00 | 7.3654 | 7.7528 | 51.6259 | 2721.4938 | 40822.4066
2020-06-13 00:00 | 7.0673 | 7.439 | 47.2396 | 2397.1767 | 35957.6512
2020-06-13 01:00 | 7.2763 | 7.659 | 38.7324 | 2622.1874 | 39332.8113
2020-06-13 02:00 | 6.7121 | 7.0652 | 36.1355 | 2048.7394 | 30731.0904
2020-06-13 03:00 | 6.5962 | 6.9431 | 38.3355 | 1941.7865 | 29126.7981
2020-06-13 04:00 | 6.4932 | 6.8347 | 37.4756 | 1853.8088 | 27807.132
2020-06-13 05:00 | 5.5522 | 5.8442 | 35.9275 | 1139.7572 | 17096.3574
2020-06-13 06:00 | 5.3367 | 5.6174 | 38.3677 | 1005.514 | 15082.7101
2020-06-13 07:00 | 5.475 | 5.763 | 43.1537 | 1091.6767 | 16375.1498
2020-06-13 08:00 | 5.6657 | 5.9636 | 49.8629 | 1210.4771 | 18157.156
2020-06-13 09:00 | 5.9452 | 6.2579 | 59.6252 | 1412.5557 | 21188.3355
2020-06-13 10:00 | 6.3439 | 6.6776 | 85.8864 | 1726.2041 | 25893.061
2020-06-13 11:00 | 5.7978 | 6.1027 | 86.7772 | 1303.9052 | 19558.5785
2020-06-13 12:00 | 5.6831 | 5.982 | 87.6735 | 1221.3191 | 18319.7864
2020-06-13 13:00 | 5.6503 | 5.9475 | 88.8005 | 1200.9349 | 18014.0229
2020-06-13 14:00 | 5.1647 | 5.4363 | 85.2501 | 904.0297 | 13560.4448
2020-06-13 15:00 | 6.3072 | 6.6389 | 47.6983 | 1694.8051 | 25422.0772
2020-06-13 16:00 | 7.8052 | 8.2157 | 32.4152 | 3225.8822 | 48388.2328
2020-06-13 17:00 | 6.8751 | 7.2367 | 34.3864 | 2208.5988 | 33128.982
2020-06-13 18:00 | 8.4348 | 8.8784 | 34.4396 | 3972.8227 | 59592.3398
2020-06-13 19:00 | 7.4064 | 7.7959 | 46.6194 | 2767.1004 | 41506.5058
2020-06-13 20:00 | 7.2794 | 7.6622 | 51.8475 | 2625.6167 | 39384.251
2020-06-13 21:00 | 7.9005 | 8.3161 | 41.7758 | 3338.8769 | 50083.1542
2020-06-13 22:00 | 6.013 | 6.3292 | 19.9929 | 1462.4594 | 21936.8909
2020-06-13 23:00 | 7.2604 | 7.6423 | 21.9 | 2604.5113 | 39067.669
2020-06-14 00:00 | 7.5796 | 7.9783 | 30.7996 | 2960.0319 | 44400.4783
2020-06-14 01:00 | 6.9892 | 7.3568 | 29.8812 | 2320.5192 | 34807.7878
2020-06-14 02:00 | 7.3191 | 7.7041 | 34.2362 | 2669.9057 | 40048.5856
2020-06-14 03:00 | 7.5797 | 7.9783 | 35.2131 | 2960.056 | 44400.8401
2020-06-14 04:00 | 7.253 | 7.6344 | 34.1734 | 2596.2155 | 38943.2328
2020-06-14 05:00 | 6.8192 | 7.1778 | 36.5186 | 2153.7428 | 32306.1427
2020-06-14 06:00 | 6.678 | 7.0292 | 41.4114 | 2015.2381 | 30228.5719
2020-06-14 07:00 | 6.8818 | 7.2437 | 50.9811 | 2215.1256 | 33226.8842
2020-06-14 08:00 | 6.3768 | 6.7122 | 59.3829 | 1754.276 | 26314.1398
2020-06-14 09:00 | 5.8548 | 6.1627 | 67.5748 | 1345.9112 | 20188.6684
2020-06-14 10:00 | 4.4287 | 4.6616 | 44.9491 | 542.2101 | 8133.1509
2020-06-14 11:00 | 4.2871 | 4.5125 | 32.9602 | 479.2869 | 7189.3038
2020-06-14 12:00 | 4.5578 | 4.7976 | 23.6573 | 599.5682 | 8993.5234
2020-06-14 13:00 | 5.2411 | 5.5167 | 12.3518 | 945.8988 | 14188.4824
2020-06-14 14:00 | 5.9664 | 6.2802 | 5.7746 | 1428.1543 | 21422.3152
2020-06-14 15:00 | 5.449 | 5.7356 | 16.8054 | 1075.4725 | 16132.0873
2020-06-14 16:00 | 4.5671 | 4.8073 | 30.5091 | 603.6848 | 9055.2726
2020-06-14 17:00 | 3.9051 | 4.1105 | 43.739 | 336.8938 | 5053.4064
2020-06-14 18:00 | 3.857 | 4.0598 | 53.77 | 319.0552 | 4785.8276
2020-06-14 19:00 | 3.7357 | 3.9321 | 69.1433 | 278.5908 | 4178.8614
2020-06-14 20:00 | 3.7582 | 3.9559 | 88.2816 | 285.3826 | 4280.739
2020-06-14 21:00 | 3.8955 | 4.1004 | 99.7988 | 333.3513 | 5000.2689
2020-06-14 22:00 | 3.6501 | 3.8421 | 111.3833 | 252.8431 | 3792.6465
2020-06-14 23:00 | 3.6213 | 3.8118 | 122.7522 | 244.1742 | 3662.613
2020-06-15 00:00 | 3.3081 | 3.4821 | 125.8067 | 151.1603 | 2267.4045
2020-06-15 01:00 | 2.8557 | 3.0059 | 122.8066 | 49.2644 | 738.9657
2020-06-15 02:00 | 2.2918 | 2.4123 | 123.6599 | 0 | 0
2020-06-15 03:00 | 1.6074 | 1.6919 | 124.2267 | 0 | 0
2020-06-15 04:00 | 1.6508 | 1.7377 | 118.7772 | 0 | 0
2020-06-15 05:00 | 1.7197 | 1.8101 | 129.7247 | 0 | 0
2020-06-15 06:00 | 1.4411 | 1.5169 | 137.7328 | 0 | 0
2020-06-15 07:00 | 1.7176 | 1.8079 | 132.7261 | 0 | 0
2020-06-15 08:00 | 1.7495 | 1.8415 | 126.6188 | 0 | 0
2020-06-15 09:00 | 2.1151 | 2.2263 | 129.3026 | 0 | 0
2020-06-15 10:00 | 3.2429 | 3.4135 | 134.6084 | 136.4873 | 2047.3088
2020-06-15 11:00 | 3.505 | 3.6894 | 128.9517 | 209.1631 | 3137.4464
2020-06-15 12:00 | 4.0235 | 4.2351 | 123.2157 | 380.7682 | 5711.5229
2020-06-15 13:00 | 4.1669 | 4.3861 | 124.3814 | 433.9086 | 6508.6293
2020-06-15 14:00 | 4.0988 | 4.3144 | 128.5823 | 408.66 | 6129.8993
2020-06-15 15:00 | 3.4906 | 3.6742 | 129.1276 | 204.8249 | 3072.3729
2020-06-15 16:00 | 2.9061 | 3.0589 | 132.7054 | 60.6121 | 909.1813
2020-06-15 17:00 | 2.9857 | 3.1427 | 128.7601 | 78.5447 | 1178.1711
2020-06-15 18:00 | 3.1322 | 3.2969 | 114.0946 | 111.5441 | 1673.1622
2020-06-15 19:00 | 3.4228 | 3.6029 | 105.0695 | 184.4182 | 2766.2732
2020-06-15 20:00 | 4.0811 | 4.2957 | 102.6437 | 402.0896 | 6031.3444
2020-06-15 21:00 | 4.4176 | 4.6499 | 108.7628 | 537.2566 | 8058.8494
2020-06-15 22:00 | 2.8282 | 2.9769 | 118.5079 | 0 | 0
2020-06-15 23:00 | 0.68378 | 0.71974 | 97.2381 | 0 | 0
2020-06-16 00:00 | 1.3667 | 1.4386 | 88.3922 | 0 | 0
2020-06-16 01:00 | 1.8991 | 1.999 | 77.3633 | 0 | 0
2020-06-16 02:00 | 2.5344 | 2.6677 | 74.3563 | 0 | 0
2020-06-16 03:00 | 3.5271 | 3.7126 | 90.8765 | 215.7918 | 3236.8763
2020-06-16 04:00 | 3.5416 | 3.7279 | 102.6997 | 220.1751 | 3302.6262
2020-06-16 05:00 | 2.8163 | 2.9644 | 106.7985 | 0 | 0
2020-06-16 06:00 | 3.4846 | 3.6679 | 109.2776 | 203.0243 | 3045.3644
2020-06-16 07:00 | 4.044 | 4.2567 | 110.0869 | 388.3639 | 5825.4587
2020-06-16 08:00 | 4.7714 | 5.0224 | 110.7859 | 696.2372 | 10443.5584
2020-06-16 09:00 | 4.7846 | 5.0363 | 110.7096 | 703.1979 | 10547.9685
2020-06-16 10:00 | 3.6253 | 3.816 | 107.8643 | 245.3796 | 3680.6937
2020-06-16 11:00 | 3.8248 | 4.026 | 93.8189 | 307.1364 | 4607.0467
2020-06-16 12:00 | 4.3046 | 4.531 | 88.8321 | 487.077 | 7306.1553
2020-06-16 13:00 | 4.557 | 4.7967 | 86.0825 | 599.2117 | 8988.1752
2020-06-16 14:00 | 3.6976 | 3.8921 | 88.0797 | 267.1339 | 4007.0084
2020-06-16 15:00 | 3.5591 | 3.7463 | 107.3524 | 225.4359 | 3381.538
2020-06-16 16:00 | 4.0273 | 4.2391 | 103.216 | 382.1632 | 5732.4479
2020-06-16 17:00 | 3.3027 | 3.4764 | 94.2437 | 149.9598 | 2249.3965
2020-06-16 18:00 | 3.1289 | 3.2935 | 97.4173 | 110.8056 | 1662.0842
2020-06-16 19:00 | 3.1958 | 3.3639 | 106.1389 | 125.8669 | 1888.0032
2020-06-16 20:00 | 3.0471 | 3.2073 | 113.5286 | 92.3705 | 1385.5571
2020-06-16 21:00 | 4.1634 | 4.3824 | 88.7824 | 432.6122 | 6489.1825
2020-06-16 22:00 | 4.3316 | 4.5594 | 83.4355 | 499.0774 | 7486.1612
2020-06-16 23:00 | 5.7918 | 6.0964 | 74.8342 | 1299.468 | 19492.0201
2020-06-17 00:00 | 7.1803 | 7.558 | 82.458 | 2515.3374 | 37730.0612
2020-06-17 01:00 | 7.0139 | 7.3828 | 89.8395 | 2344.7762 | 35171.6432
2020-06-17 02:00 | 6.1565 | 6.4803 | 93.8242 | 1568.2092 | 23523.1382
2020-06-17 03:00 | 5.7522 | 6.0548 | 94.0657 | 1270.3428 | 19055.142
2020-06-17 04:00 | 5.3359 | 5.6166 | 91.6896 | 1005.0152 | 15075.2273
2020-06-17 05:00 | 4.8081 | 5.0609 | 95.294 | 715.5915 | 10733.8726
2020-06-17 06:00 | 4.61 | 4.8524 | 96.6216 | 622.7276 | 9340.9146
2020-06-17 07:00 | 5.2102 | 5.4843 | 103.4115 | 928.1001 | 13921.5017
2020-06-17 08:00 | 5.2566 | 5.5331 | 103.0807 | 955.5997 | 14333.9952
2020-06-17 09:00 | 4.882 | 5.1387 | 97.9709 | 754.6479 | 11319.7187
2020-06-17 10:00 | 3.3366 | 3.5121 | 97.5457 | 158.4714 | 2377.0713
2020-06-17 11:00 | 3.3037 | 3.4774 | 95.3545 | 150.1671 | 2252.5059
2020-06-17 12:00 | 4.6611 | 4.9063 | 108.6923 | 645.4483 | 9681.7241
2020-06-17 13:00 | 5.4084 | 5.6929 | 109.8782 | 1050.1971 | 15752.9564
2020-06-17 14:00 | 3.8069 | 4.0071 | 116.7203 | 300.5037 | 4507.5562
2020-06-17 15:00 | 4.8475 | 5.1025 | 115.0276 | 736.4375 | 11046.5618
2020-06-17 16:00 | 5.7047 | 6.0048 | 103.0397 | 1235.3417 | 18530.1255
2020-06-17 17:00 | 5.2094 | 5.4834 | 104.9578 | 927.659 | 13914.8843
2020-06-17 18:00 | 6.3909 | 6.727 | 119.1227 | 1766.3495 | 26495.242
2020-06-17 19:00 | 6.0635 | 6.3824 | 132.4774 | 1499.7082 | 22495.623
2020-06-17 20:00 | 5.6483 | 5.9454 | 135.4589 | 1199.6902 | 17995.3528
2020-06-17 21:00 | 5.7388 | 6.0406 | 137.1262 | 1260.4114 | 18906.1704
2020-06-17 22:00 | 5.5586 | 5.8509 | 145.6626 | 1143.7409 | 17156.113
2020-06-17 23:00 | 5.1033 | 5.3717 | 148.4676 | 871.6116 | 13074.1744
2020-06-18 00:00 | 4.664 | 4.9093 | 147.1118 | 646.7147 | 9700.7209
2020-06-18 01:00 | 4.6174 | 4.8603 | 146.1906 | 626.041 | 9390.6157
2020-06-18 02:00 | 4.7227 | 4.9711 | 144.6987 | 672.8151 | 10092.2262
2020-06-18 03:00 | 4.5381 | 4.7768 | 142.9809 | 590.8205 | 8862.308
2020-06-18 04:00 | 3.7959 | 3.9955 | 140.7379 | 296.714 | 4450.7101
2020-06-18 05:00 | 2.9497 | 3.1049 | 137.6045 | 70.4442 | 1056.6624
2020-06-18 06:00 | 3.2184 | 3.3877 | 131.5824 | 130.9689 | 1964.534
2020-06-18 07:00 | 4.2056 | 4.4268 | 126.832 | 448.2311 | 6723.4667
2020-06-18 08:00 | 4.6264 | 4.8698 | 122.8686 | 630.0375 | 9450.5632
2020-06-18 09:00 | 4.8287 | 5.0827 | 120.4695 | 726.495 | 10897.4248
2020-06-18 10:00 | 4.1369 | 4.3545 | 128.9147 | 422.7672 | 6341.5087
2020-06-18 11:00 | 5.5103 | 5.8002 | 124.1153 | 1113.6935 | 16705.4029
2020-06-18 12:00 | 3.7895 | 3.9888 | 120.5443 | 294.7994 | 4421.9909
2020-06-18 13:00 | 3.3881 | 3.5663 | 116.1103 | 173.9719 | 2609.5778
2020-06-18 14:00 | 3.8606 | 4.0637 | 114.5388 | 320.4189 | 4806.2828
2020-06-18 15:00 | 4.9505 | 5.2109 | 101.5211 | 790.8817 | 11863.226
2020-06-18 16:00 | 7.0803 | 7.4527 | 107.3154 | 2409.9375 | 36149.0628
2020-06-18 17:00 | 4.8873 | 5.1443 | 120.0548 | 757.4569 | 11361.8528
2020-06-18 18:00 | 4.9733 | 5.2349 | 111.1571 | 802.9254 | 12043.8805
2020-06-18 19:00 | 5.1589 | 5.4303 | 107.9251 | 900.9891 | 13514.8358
2020-06-18 20:00 | 5.0888 | 5.3564 | 105.1458 | 863.9166 | 12958.749
2020-06-18 21:00 | 4.7048 | 4.9522 | 98.3846 | 664.8267 | 9972.4007
2020-06-18 22:00 | 5.294 | 5.5724 | 84.2222 | 978.853 | 14682.7952
2020-06-18 23:00 | 5.704 | 6.004 | 85.6967 | 1234.7945 | 18521.9179
2020-06-19 00:00 | 5.6903 | 5.9895 | 91.3377 | 1225.8036 | 18387.054
2020-06-19 01:00 | 5.5207 | 5.811 | 96.9096 | 1120.1385 | 16802.0776
2020-06-19 02:00 | 5.5985 | 5.8929 | 99.9317 | 1168.618 | 17529.2699
2020-06-19 03:00 | 5.8375 | 6.1445 | 98.5603 | 1333.1366 | 19997.0491
2020-06-19 04:00 | 5.9514 | 6.2644 | 95.4576 | 1417.0665 | 21255.9977
2020-06-19 05:00 | 5.0758 | 5.3427 | 98.0189 | 857.0569 | 12855.8528
2020-06-19 06:00 | 4.5998 | 4.8417 | 101.3667 | 618.2167 | 9273.2507
2020-06-19 07:00 | 4.3672 | 4.5969 | 103.1119 | 514.9018 | 7723.5265
2020-06-19 08:00 | 4.6597 | 4.9048 | 103.9313 | 644.8052 | 9672.0773
2020-06-19 09:00 | 4.9684 | 5.2298 | 108.5595 | 800.3383 | 12005.0752
2020-06-19 10:00 | 4.6153 | 4.858 | 111.676 | 625.0932 | 9376.3975
2020-06-19 11:00 | 4.8077 | 5.0605 | 110.9948 | 715.3802 | 10730.7029
2020-06-19 12:00 | 4.6744 | 4.9202 | 113.4934 | 651.3409 | 9770.1141
2020-06-19 13:00 | 4.5041 | 4.741 | 116.385 | 575.7201 | 8635.8008
2020-06-19 14:00 | 4.4016 | 4.6331 | 107.552 | 530.1864 | 7952.7958
2020-06-19 15:00 | 5.6663 | 5.9644 | 96.5377 | 1210.9062 | 18163.5929
2020-06-19 16:00 | 7.3421 | 7.7283 | 94.0389 | 2695.4967 | 40432.4504
2020-06-19 17:00 | 6.789 | 7.1461 | 96.6878 | 2124.157 | 31862.3554
2020-06-19 18:00 | 5.5497 | 5.8416 | 94.3055 | 1138.2395 | 17073.5921
2020-06-19 19:00 | 6.791 | 7.1482 | 85.1003 | 2126.0852 | 31891.2775
2020-06-19 20:00 | 7.47 | 7.8629 | 86.3638 | 2837.9057 | 42568.5861
2020-06-19 21:00 | 6.6223 | 6.9706 | 90.7628 | 1964.1566 | 29462.3486
2020-06-19 22:00 | 6.9688 | 7.3353 | 89.8456 | 2300.4803 | 34507.2042
2020-06-19 23:00 | 7.2697 | 7.6521 | 86.6701 | 2614.871 | 39223.0643
2020-06-20 00:00 | 7.1882 | 7.5662 | 86.1296 | 2524.0786 | 37861.1794
2020-06-20 01:00 | 6.4226 | 6.7604 | 87.7767 | 1793.4707 | 26902.0602
2020-06-20 02:00 | 6.0046 | 6.3204 | 84.8369 | 1456.2553 | 21843.8295
2020-06-20 03:00 | 5.7769 | 6.0807 | 78.2706 | 1288.4869 | 19327.3032
2020-06-20 04:00 | 5.1433 | 5.4138 | 69.0706 | 892.7426 | 13391.1384
2020-06-20 05:00 | 4.5629 | 4.8029 | 61.3414 | 601.8064 | 9027.0962
2020-06-20 06:00 | 3.9439 | 4.1513 | 57.1261 | 351.258 | 5268.87
2020-06-20 07:00 | 4.6742 | 4.92 | 53.9208 | 651.2492 | 9768.7374
2020-06-20 08:00 | 5.1766 | 5.4489 | 58.0175 | 910.3255 | 13654.8822
2020-06-20 09:00 | 5.6417 | 5.9385 | 64.4136 | 1195.573 | 17933.5943
2020-06-20 10:00 | 5.3075 | 5.5867 | 57.0564 | 987.316 | 14809.7407
2020-06-20 11:00 | 6.1285 | 6.4508 | 55.5959 | 1547.5637 | 23213.4549
2020-06-20 12:00 | 7.2336 | 7.6141 | 62.4795 | 2574.6805 | 38620.208
2020-06-20 13:00 | 7.6868 | 8.091 | 65.7583 | 3085.5177 | 46282.7648
2020-06-20 14:00 | 7.2598 | 7.6416 | 64.4597 | 2603.8534 | 39057.8015
2020-06-20 15:00 | 6.8873 | 7.2496 | 70.8214 | 2220.601 | 33309.0152
2020-06-20 16:00 | 6.0093 | 6.3253 | 80.8155 | 1459.7225 | 21895.8382
2020-06-20 17:00 | 6.1761 | 6.5009 | 67.2879 | 1582.7301 | 23740.9522
2020-06-20 18:00 | 5.1494 | 5.4203 | 54.8279 | 895.9822 | 13439.7325
2020-06-20 19:00 | 4.914 | 5.1724 | 53.6152 | 771.5525 | 11573.2868
2020-06-20 20:00 | 5.3845 | 5.6677 | 48.9312 | 1035.2794 | 15529.1907
2020-06-20 21:00 | 6.0587 | 6.3774 | 49.1111 | 1496.1808 | 22442.7115
2020-06-20 22:00 | 6.9023 | 7.2653 | 40.1886 | 2235.2707 | 33529.0607
2020-06-20 23:00 | 7.459 | 7.8513 | 47.6601 | 2825.7228 | 42385.8422
2020-06-21 00:00 | 6.8123 | 7.1706 | 49.8279 | 2146.9603 | 32204.4046
2020-06-21 01:00 | 6.1325 | 6.455 | 49.6117 | 1550.5123 | 23257.684
2020-06-21 02:00 | 5.4679 | 5.7555 | 57.416 | 1087.2455 | 16308.6822
2020-06-21 03:00 | 4.6297 | 4.8732 | 67.0555 | 631.4747 | 9472.1205
2020-06-21 04:00 | 3.3155 | 3.4899 | 71.1933 | 152.8405 | 2292.6078
2020-06-21 05:00 | 1.8573 | 1.955 | 64.5844 | 0 | 0
2020-06-21 06:00 | 1.9819 | 2.0861 | 60.2743 | 0 | 0
2020-06-21 07:00 | 2.7955 | 2.9425 | 65.0146 | 0 | 0
2020-06-21 08:00 | 3.0551 | 3.2158 | 74.4013 | 94.1821 | 1412.7311
2020-06-21 09:00 | 3.4232 | 3.6033 | 77.5474 | 184.5407 | 2768.1102
2020-06-21 10:00 | 3.7271 | 3.9231 | 92.3473 | 276.0172 | 4140.258
2020-06-21 11:00 | 4.3231 | 4.5505 | 89.4261 | 495.3163 | 7429.7442
2020-06-21 12:00 | 5.2421 | 5.5178 | 87.93 | 946.5215 | 14197.8227
2020-06-21 13:00 | 5.6305 | 5.9266 | 83.2085 | 1188.5752 | 17828.6277
2020-06-21 14:00 | 5.738 | 6.0397 | 78.4392 | 1259.8222 | 18897.3328
2020-06-21 15:00 | 5.7993 | 6.1043 | 73.8161 | 1304.9969 | 19574.9538
2020-06-21 16:00 | 6.6375 | 6.9866 | 56.8106 | 1977.1577 | 29657.3661
2020-06-21 17:00 | 6.7507 | 7.1057 | 49.0966 | 2086.547 | 31298.205
2020-06-21 18:00 | 6.3248 | 6.6574 | 47.6131 | 1709.8133 | 25647.1994
2020-06-21 19:00 | 6.0929 | 6.4134 | 47.6251 | 1521.356 | 22820.3401
2020-06-21 20:00 | 6.5905 | 6.9371 | 55.8329 | 1936.9174 | 29053.7605
2020-06-21 21:00 | 6.6725 | 7.0234 | 60.8789 | 2009.7968 | 30146.9514
2020-06-21 22:00 | 6.6465 | 6.9961 | 71.3063 | 1984.8222 | 29772.3331
2020-06-21 23:00 | 6.2557 | 6.5847 | 66.5084 | 1650.8002 | 24762.0033
2020-06-22 00:00 | 5.9811 | 6.2957 | 56.0353 | 1438.9738 | 21584.6073
2020-06-22 01:00 | 6.5781 | 6.9241 | 48.4161 | 1926.3699 | 28895.5489
2020-06-22 02:00 | 6.7818 | 7.1385 | 50.7102 | 2117.1097 | 31756.6455
2020-06-22 03:00 | 6.1151 | 6.4367 | 57.8754 | 1537.6972 | 23065.4578
2020-06-22 04:00 | 5.21 | 5.484 | 58.7661 | 927.9576 | 13919.364
2020-06-22 05:00 | 4.3555 | 4.5846 | 54.0669 | 509.6808 | 7645.2127
2020-06-22 06:00 | 4.5769 | 4.8176 | 51.7785 | 608.0327 | 9120.4899
2020-06-22 07:00 | 4.7835 | 5.0351 | 54.2654 | 702.6269 | 10539.4037
2020-06-22 08:00 | 4.8731 | 5.1295 | 65.4342 | 749.9843 | 11249.7644
2020-06-22 09:00 | 4.9709 | 5.2324 | 74.0448 | 801.6519 | 12024.779
2020-06-22 10:00 | 4.5207 | 4.7584 | 76.6401 | 583.0513 | 8745.7693
2020-06-22 11:00 | 4.497 | 4.7335 | 71.2115 | 572.5357 | 8588.0349
2020-06-22 12:00 | 5.007 | 5.2703 | 61.8236 | 820.7135 | 12310.7025
2020-06-22 13:00 | 4.6573 | 4.9023 | 76.4883 | 643.7558 | 9656.3374
2020-06-22 14:00 | 4.6225 | 4.8656 | 58.876 | 628.2741 | 9424.1114
2020-06-22 15:00 | 4.3923 | 4.6233 | 51.7547 | 526.0276 | 7890.4141
2020-06-22 16:00 | 4.9095 | 5.1677 | 43.3544 | 769.1971 | 11537.9561
2020-06-22 17:00 | 7.0126 | 7.3814 | 64.9658 | 2343.459 | 35151.8856
2020-06-22 18:00 | 5.1775 | 5.4498 | 92.6277 | 910.8211 | 13662.3167
2020-06-22 19:00 | 5.2251 | 5.4999 | 94.0555 | 935.9585 | 14039.3768
2020-06-22 20:00 | 5.3098 | 5.5891 | 94.4125 | 988.7504 | 14831.2565
2020-06-22 21:00 | 4.9588 | 5.2196 | 96.8936 | 795.2538 | 11928.8071
2020-06-22 22:00 | 3.8097 | 4.01 | 101.0034 | 301.5304 | 4522.9562
2020-06-22 23:00 | 2.6076 | 2.7447 | 83.6455 | 0 | 0
2020-06-23 00:00 | 3.0694 | 3.2308 | 67.8378 | 97.3884 | 1460.8255
2020-06-23 01:00 | 3.3583 | 3.535 | 65.1853 | 164.9966 | 2474.9491
2020-06-23 02:00 | 3.132 | 3.2967 | 67.6732 | 111.4958 | 1672.4367
2020-06-23 03:00 | 2.7397 | 2.8838 | 69.427 | 0 | 0
2020-06-23 04:00 | 2.22 | 2.3367 | 70.1025 | 0 | 0
2020-06-23 05:00 | 1.7043 | 1.7939 | 73.8813 | 0 | 0
2020-06-23 06:00 | 1.4044 | 1.4782 | 75.0539 | 0 | 0
2020-06-23 07:00 | 1.1802 | 1.2423 | 75.5751 | 0 | 0
2020-06-23 08:00 | 1.1193 | 1.1782 | 85.8622 | 0 | 0
2020-06-23 09:00 | 1.0184 | 1.072 | 94.7553 | 0 | 0
2020-06-23 10:00 | 0.81987 | 0.86299 | 80.3217 | 0 | 0
2020-06-23 11:00 | 0.60336 | 0.6351 | 34.2193 | 0 | 0
2020-06-23 12:00 | 0.91035 | 0.95823 | 359.7714 | 0 | 0
2020-06-23 13:00 | 1.269 | 1.3358 | 355.7592 | 0 | 0
2020-06-23 14:00 | 0.55836 | 0.58773 | 351.0973 | 0 | 0
2020-06-23 15:00 | 1.4188 | 1.4934 | 21.9281 | 0 | 0
2020-06-23 16:00 | 1.9631 | 2.0663 | 36.9321 | 0 | 0
2020-06-23 17:00 | 1.7803 | 1.874 | 0.16598 | 0 | 0
2020-06-23 18:00 | 2.5054 | 2.6372 | 17.0944 | 0 | 0
2020-06-23 19:00 | 3.2454 | 3.4161 | 48.5558 | 137.0439 | 2055.6583
2020-06-23 20:00 | 4.0626 | 4.2763 | 79.1966 | 395.2437 | 5928.6549
2020-06-23 21:00 | 4.5483 | 4.7875 | 96.7729 | 595.3096 | 8929.6445
2020-06-23 22:00 | 5.0787 | 5.3458 | 105.0402 | 858.5895 | 12878.8426
2020-06-23 23:00 | 4.4575 | 4.692 | 99.6496 | 555.009 | 8325.1344
2020-06-24 00:00 | 4.8917 | 5.149 | 89.1314 | 759.7897 | 11396.8461
2020-06-24 01:00 | 5.5848 | 5.8786 | 71.1233 | 1160.1036 | 17401.5539
2020-06-24 02:00 | 5.6877 | 5.9869 | 71.1779 | 1224.2369 | 18363.5541
2020-06-24 03:00 | 5.8105 | 6.1161 | 70.6138 | 1313.2968 | 19699.4518
2020-06-24 04:00 | 6.1422 | 6.4652 | 72.042 | 1557.6512 | 23364.7683
2020-06-24 05:00 | 6.1878 | 6.5133 | 67.0897 | 1592.7942 | 23891.9127
2020-06-24 06:00 | 6.027 | 6.344 | 66.0504 | 1472.825 | 22092.3747
2020-06-24 07:00 | 5.4441 | 5.7304 | 66.9205 | 1072.4244 | 16086.3665
2020-06-24 08:00 | 5.0112 | 5.2747 | 65.5277 | 822.9046 | 12343.5695
2020-06-24 09:00 | 4.6787 | 4.9248 | 65.2188 | 653.2632 | 9798.9477
2020-06-24 10:00 | 4.0704 | 4.2845 | 60.9432 | 398.1363 | 5972.0441
2020-06-24 11:00 | 4.7825 | 5.034 | 58.2095 | 702.0597 | 10530.8956
2020-06-24 12:00 | 5.4558 | 5.7428 | 55.6917 | 1079.7147 | 16195.7209
2020-06-24 13:00 | 6.2434 | 6.5718 | 57.841 | 1640.2817 | 24604.2251
2020-06-24 14:00 | 6.7645 | 7.1203 | 60.5259 | 2100.1081 | 31501.6213
2020-06-24 15:00 | 6.5002 | 6.8421 | 64.1568 | 1859.7893 | 27896.8394
2020-06-24 16:00 | 6.2994 | 6.6307 | 66.5711 | 1688.1279 | 25321.9186
2020-06-24 17:00 | 6.3104 | 6.6423 | 63.2156 | 1697.5836 | 25463.7535
2020-06-24 18:00 | 6.2927 | 6.6237 | 66.0681 | 1682.4183 | 25236.2745
2020-06-24 19:00 | 6.3955 | 6.7319 | 71.2165 | 1770.2766 | 26554.1488
2020-06-24 20:00 | 6.4213 | 6.759 | 74.413 | 1792.304 | 26884.5606
2020-06-24 21:00 | 6.2939 | 6.6249 | 76.7289 | 1683.415 | 25251.2248
2020-06-24 22:00 | 5.7275 | 6.0287 | 83.2033 | 1252.086 | 18781.2896
2020-06-24 23:00 | 5.1138 | 5.3828 | 84.3419 | 877.1672 | 13157.5083
2020-06-25 00:00 | 4.3164 | 4.5434 | 80.3332 | 492.3025 | 7384.5375
2020-06-25 01:00 | 3.7501 | 3.9474 | 66.1227 | 282.9457 | 4244.1853
2020-06-25 02:00 | 4.6035 | 4.8457 | 53.1941 | 619.869 | 9298.0355
2020-06-25 03:00 | 5.1706 | 5.4426 | 49.8176 | 907.1751 | 13607.6261
2020-06-25 04:00 | 4.7042 | 4.9516 | 52.7253 | 664.5862 | 9968.7926
2020-06-25 05:00 | 3.4997 | 3.6837 | 57.4827 | 207.552 | 3113.2803
2020-06-25 06:00 | 3.5704 | 3.7581 | 62.0145 | 228.8279 | 3432.4182
2020-06-25 07:00 | 4.5484 | 4.7876 | 73.0727 | 595.3871 | 8930.8071
2020-06-25 08:00 | 4.8494 | 5.1045 | 81.522 | 737.44 | 11061.5996
2020-06-25 09:00 | 4.6512 | 4.8958 | 81.118 | 641.0273 | 9615.4097
2020-06-25 10:00 | 3.4168 | 3.5965 | 81.7275 | 182.589 | 2738.8352
2020-06-25 11:00 | 3.6712 | 3.8643 | 75.6464 | 259.1883 | 3887.825
2020-06-25 12:00 | 3.8972 | 4.1021 | 72.5026 | 333.9566 | 5009.349
2020-06-25 13:00 | 4.2296 | 4.452 | 67.9708 | 457.116 | 6856.7393
2020-06-25 14:00 | 4.6743 | 4.9201 | 65.821 | 651.2917 | 9769.3759
2020-06-25 15:00 | 4.6235 | 4.8667 | 63.9096 | 628.7441 | 9431.1613
2020-06-25 16:00 | 3.9408 | 4.148 | 56.1874 | 350.1048 | 5251.5725
2020-06-25 17:00 | 3.8582 | 4.0611 | 47.0421 | 319.5056 | 4792.5841
2020-06-25 18:00 | 4.2571 | 4.481 | 45.0619 | 467.3286 | 7009.9295
2020-06-25 19:00 | 5.0703 | 5.337 | 55.3401 | 854.1751 | 12812.6272
2020-06-25 20:00 | 6.0992 | 6.4199 | 70.663 | 1525.9645 | 22889.4675
2020-06-25 21:00 | 6.498 | 6.8398 | 87.2859 | 1857.8819 | 27868.229
2020-06-25 22:00 | 6.5177 | 6.8605 | 109.4758 | 1874.7515 | 28121.273
2020-06-25 23:00 | 6.0575 | 6.3761 | 118.6504 | 1495.2742 | 22429.1127
2020-06-26 00:00 | 5.4138 | 5.6986 | 125.0879 | 1053.5507 | 15803.2611
2020-06-26 01:00 | 5.0468 | 5.3123 | 125.761 | 841.7648 | 12626.4723
2020-06-26 02:00 | 4.9228 | 5.1817 | 123.8232 | 776.2085 | 11643.1276
2020-06-26 03:00 | 4.5409 | 4.7797 | 124.5125 | 592.0368 | 8880.5527
2020-06-26 04:00 | 4.1613 | 4.3802 | 124.0244 | 431.8232 | 6477.3486
2020-06-26 05:00 | 3.2284 | 3.3982 | 117.4742 | 133.216 | 1998.2407
2020-06-26 06:00 | 2.8163 | 2.9645 | 114.7907 | 0 | 0
2020-06-26 07:00 | 2.9931 | 3.1505 | 112.8444 | 80.2158 | 1203.2364
2020-06-26 08:00 | 3.3298 | 3.505 | 112.0561 | 156.417 | 2346.2554
2020-06-26 09:00 | 3.5111 | 3.6957 | 112.3394 | 210.9842 | 3164.763
2020-06-26 10:00 | 3.1517 | 3.3175 | 125.5112 | 115.9372 | 1739.0575
2020-06-26 11:00 | 3.091 | 3.2535 | 120.3018 | 102.2543 | 1533.8142
2020-06-26 12:00 | 3.2229 | 3.3924 | 117.314 | 131.9691 | 1979.5363
2020-06-26 13:00 | 3.8255 | 4.0267 | 116.1274 | 307.412 | 4611.1803
2020-06-26 14:00 | 4.3558 | 4.5849 | 118.9707 | 509.8387 | 7647.5811
2020-06-26 15:00 | 4.4271 | 4.66 | 125.1563 | 541.5084 | 8122.6263
2020-06-26 16:00 | 4.2243 | 4.4464 | 126.2389 | 455.1473 | 6827.2092
2020-06-26 17:00 | 4.5774 | 4.8182 | 124.6218 | 608.2796 | 9124.1937
2020-06-26 18:00 | 5.1552 | 5.4264 | 128.6424 | 899.047 | 13485.7046
2020-06-26 19:00 | 5.6417 | 5.9384 | 134.9989 | 1195.5365 | 17933.0482
2020-06-26 20:00 | 5.97 | 6.284 | 139.6347 | 1430.7716 | 21461.5746
2020-06-26 21:00 | 6.1431 | 6.4662 | 143.6109 | 1558.3647 | 23375.4704
2020-06-26 22:00 | 6.0419 | 6.3597 | 148.3897 | 1483.7833 | 22256.7489
2020-06-26 23:00 | 5.9163 | 6.2275 | 155.7275 | 1391.2304 | 20868.4556
2020-06-27 00:00 | 5.9059 | 6.2165 | 160.5096 | 1383.5846 | 20753.7687
2020-06-27 01:00 | 5.8496 | 6.1572 | 164.9825 | 1342.0517 | 20130.7761
2020-06-27 02:00 | 5.7029 | 6.0028 | 169.6775 | 1233.9774 | 18509.6612
2020-06-27 03:00 | 5.6707 | 5.969 | 169.6623 | 1213.6336 | 18204.5045
2020-06-27 04:00 | 5.4442 | 5.7305 | 169.9031 | 1072.464 | 16086.96
2020-06-27 05:00 | 4.3415 | 4.5698 | 168.914 | 503.4641 | 7551.9619
2020-06-27 06:00 | 3.8773 | 4.0813 | 169.9569 | 326.6022 | 4899.0335
2020-06-27 07:00 | 3.7013 | 3.896 | 179.0091 | 268.2418 | 4023.6276
2020-06-27 08:00 | 4.4414 | 4.675 | 192.3359 | 547.8317 | 8217.4757
2020-06-27 09:00 | 5.1273 | 5.397 | 198.9755 | 884.2987 | 13264.4809
2020-06-27 10:00 | 5.0694 | 5.336 | 195.2731 | 853.6899 | 12805.3489
2020-06-27 11:00 | 5.1802 | 5.4526 | 189.6162 | 912.2278 | 13683.4176
2020-06-27 12:00 | 5.3379 | 5.6186 | 190.07 | 1006.2324 | 15093.4863
2020-06-27 13:00 | 5.5145 | 5.8046 | 193.4738 | 1116.3102 | 16744.6526
2020-06-27 14:00 | 5.3865 | 5.6698 | 194.6676 | 1036.5273 | 15547.909
2020-06-27 15:00 | 5.3702 | 5.6526 | 199.7211 | 1026.3677 | 15395.5155
2020-06-27 16:00 | 4.8404 | 5.095 | 205.5079 | 732.6911 | 10990.367
2020-06-27 17:00 | 4.7727 | 5.0237 | 211.0612 | 696.8804 | 10453.2066
2020-06-27 18:00 | 5.0489 | 5.3145 | 213.7833 | 842.8554 | 12642.8305
2020-06-27 19:00 | 5.6222 | 5.9179 | 216.6912 | 1183.3696 | 17750.5437
2020-06-27 20:00 | 5.9325 | 6.2445 | 215.4759 | 1403.1661 | 21047.4922
2020-06-27 21:00 | 6.3455 | 6.6793 | 209.3444 | 1727.5631 | 25913.4472
2020-06-27 22:00 | 5.3482 | 5.6295 | 205.0473 | 1012.6346 | 15189.5188
2020-06-27 23:00 | 5.9266 | 6.2383 | 201.5841 | 1398.8266 | 20982.3992
2020-06-28 00:00 | 5.656 | 5.9535 | 208.1295 | 1204.4616 | 18066.9237
2020-06-28 01:00 | 5.8717 | 6.1806 | 219.4559 | 1358.3992 | 20375.9882
2020-06-28 02:00 | 5.8347 | 6.1416 | 225.1009 | 1331.0998 | 19966.4969
2020-06-28 03:00 | 5.6035 | 5.8982 | 224.9109 | 1171.7534 | 17576.3009
2020-06-28 04:00 | 5.3905 | 5.674 | 222.8022 | 1038.9926 | 15584.8887
2020-06-28 05:00 | 4.2898 | 4.5154 | 230.0595 | 480.504 | 7207.5606
2020-06-28 06:00 | 4.0552 | 4.2685 | 233.6575 | 392.5127 | 5887.6909
2020-06-28 07:00 | 3.7985 | 3.9983 | 240.6945 | 297.5087 | 4462.6303
2020-06-28 08:00 | 4.1888 | 4.4091 | 246.2034 | 442.0144 | 6630.2165
2020-06-28 09:00 | 5.1004 | 5.3686 | 244.0729 | 870.0556 | 13050.834
2020-06-28 10:00 | 5.0735 | 5.3403 | 249.5245 | 855.8303 | 12837.455
2020-06-28 11:00 | 5.8923 | 6.2022 | 253.4431 | 1373.5239 | 20602.8588
2020-06-28 12:00 | 5.9001 | 6.2104 | 256.7283 | 1379.2676 | 20689.0139
2020-06-28 13:00 | 5.6543 | 5.9516 | 259.3831 | 1203.3728 | 18050.5918
2020-06-28 14:00 | 6.9779 | 7.3449 | 268.9815 | 2309.4557 | 34641.836
2020-06-28 15:00 | 5.7225 | 6.0235 | 274.5954 | 1248.4515 | 18726.7725
2020-06-28 16:00 | 5.3494 | 5.6308 | 273.9433 | 1013.4198 | 15201.2965
2020-06-28 17:00 | 4.919 | 5.1777 | 276.6098 | 774.2052 | 11613.0775
2020-06-28 18:00 | 5.4162 | 5.7011 | 277.2823 | 1055.0497 | 15825.7457
2020-06-28 19:00 | 5.9567 | 6.27 | 280.689 | 1421.0094 | 21315.1415
2020-06-28 20:00 | 6.4839 | 6.8249 | 287.4447 | 1845.8072 | 27687.1083
2020-06-28 21:00 | 5.9928 | 6.308 | 296.7559 | 1447.5939 | 21713.9079
2020-06-28 22:00 | 6.3651 | 6.6998 | 299.8406 | 1744.273 | 26164.0955
2020-06-28 23:00 | 6.1115 | 6.433 | 299.544 | 1535.0875 | 23026.3123
2020-06-29 00:00 | 6.1044 | 6.4254 | 310.8867 | 1529.7887 | 22946.8305
2020-06-29 01:00 | 5.4753 | 5.7633 | 305.7197 | 1091.8627 | 16377.941
2020-06-29 02:00 | 5.7985 | 6.1035 | 289.6981 | 1304.4301 | 19566.4508
2020-06-29 03:00 | 5.7312 | 6.0326 | 293.4327 | 1254.8502 | 18822.7535
2020-06-29 04:00 | 5.1412 | 5.4116 | 303.9814 | 891.6453 | 13374.6799
2020-06-29 05:00 | 5.183 | 5.4556 | 317.2372 | 913.7321 | 13705.9817
2020-06-29 06:00 | 5.0831 | 5.3504 | 322.6234 | 860.9145 | 12913.7175
2020-06-29 07:00 | 5.5306 | 5.8215 | 326.7313 | 1126.3057 | 16894.5849
2020-06-29 08:00 | 5.5114 | 5.8013 | 332.4265 | 1114.353 | 16715.2945
2020-06-29 09:00 | 5.601 | 5.8956 | 335.2145 | 1170.1924 | 17552.8862
2020-06-29 10:00 | 3.4861 | 3.6695 | 339.4998 | 203.4647 | 3051.9703
2020-06-29 11:00 | 3.3235 | 3.4982 | 333.113 | 154.6254 | 2319.3803
2020-06-29 12:00 | 3.2855 | 3.4583 | 334.6623 | 146.0678 | 2191.0171
2020-06-29 13:00 | 3.3656 | 3.5426 | 342.168 | 167.1893 | 2507.8398
2020-06-29 14:00 | 3.1869 | 3.3545 | 348.6074 | 123.8571 | 1857.856
2020-06-29 15:00 | 2.561 | 2.6957 | 359.8204 | 0 | 0
2020-06-29 16:00 | 2.1201 | 2.2316 | 17.5106 | 0 | 0
2020-06-29 17:00 | 2.225 | 2.342 | 44.3751 | 0 | 0
2020-06-29 18:00 | 2.573 | 2.7083 | 71.7916 | 0 | 0
2020-06-29 19:00 | 3.4607 | 3.6428 | 98.9957 | 195.831 | 2937.4656
2020-06-29 20:00 | 4.1797 | 4.3996 | 122.2979 | 438.6469 | 6579.7039
2020-06-29 21:00 | 4.7627 | 5.0132 | 141.4162 | 691.6156 | 10374.2333
2020-06-29 22:00 | 4.8061 | 5.0589 | 153.4149 | 714.5479 | 10718.2178
2020-06-29 23:00 | 5.2055 | 5.4793 | 163.9206 | 925.5864 | 13883.7953
2020-06-30 00:00 | 5.5992 | 5.8937 | 163.5932 | 1169.0715 | 17536.0731
2020-06-30 01:00 | 6.0497 | 6.3679 | 166.2827 | 1489.508 | 22342.6197
2020-06-30 02:00 | 6.0258 | 6.3427 | 171.7804 | 1471.9175 | 22078.7627
2020-06-30 03:00 | 5.6417 | 5.9384 | 189.1433 | 1195.5402 | 17933.1028
2020-06-30 04:00 | 5.0576 | 5.3236 | 227.5778 | 847.4504 | 12711.7566
2020-06-30 05:00 | 5.5201 | 5.8105 | 270.3652 | 1119.8025 | 16797.0372
2020-06-30 06:00 | 6.5117 | 6.8541 | 292.6628 | 1869.5568 | 28043.3526
2020-06-30 07:00 | 6.3217 | 6.6542 | 303.7683 | 1707.2412 | 25608.6184
2020-06-30 08:00 | 6.3713 | 6.7064 | 304.5187 | 1749.591 | 26243.8647
2020-06-30 09:00 | 6.7507 | 7.1058 | 305.5245 | 2086.5787 | 31298.6801
2020-06-30 10:00 | 5.4913 | 5.7801 | 310.548 | 1101.8234 | 16527.3514
2020-06-30 11:00 | 6.4851 | 6.8262 | 298.2055 | 1846.8407 | 27702.611
2020-06-30 12:00 | 7.0082 | 7.3768 | 292.843 | 2339.1647 | 35087.4709
2020-06-30 13:00 | 6.8256 | 7.1846 | 289.7799 | 2160.0646 | 32400.9696
2020-06-30 14:00 | 6.5115 | 6.854 | 289.1329 | 1869.4075 | 28041.1124
2020-06-30 15:00 | 6.3248 | 6.6575 | 292.9469 | 1709.8764 | 25648.1467
2020-06-30 16:00 | 6.2041 | 6.5304 | 298.4102 | 1606.7056 | 24100.5842
2020-06-30 17:00 | 5.2398 | 5.5154 | 304.5372 | 945.0873 | 14176.3093
2020-06-30 18:00 | 4.5955 | 4.8372 | 308.3482 | 616.3192 | 9244.7873
2020-06-30 19:00 | 4.4326 | 4.6657 | 306.1355 | 543.9397 | 8159.096
2020-06-30 20:00 | 4.5946 | 4.8363 | 300.3841 | 615.9038 | 9238.557
2020-06-30 21:00 | 4.8452 | 5.1 | 295.6199 | 735.2003 | 11028.0044
2020-06-30 22:00 | 4.2366 | 4.4594 | 285.5475 | 459.7039 | 6895.5586
2020-06-30 23:00 | 3.6094 | 3.7993 | 271.2337 | 240.5959 | 3608.9381
2020-07-01 00:00 | 3.9095 | 4.1151 | 261.7751 | 338.5298 | 5077.9471
2020-07-01 01:00 | 4.2706 | 4.4952 | 258.99 | 472.3107 | 7084.6608
2020-07-01 02:00 | 4.4722 | 4.7074 | 255.6041 | 561.5193 | 8422.7896
2020-07-01 03:00 | 4.6319 | 4.8755 | 253.9946 | 632.4663 | 9486.9948
2020-07-01 04:00 | 4.8467 | 5.1016 | 254.0636 | 736.0188 | 11040.2819
2020-07-01 05:00 | 3.9316 | 4.1384 | 249.7368 | 346.7156 | 5200.7345
2020-07-01 06:00 | 3.4597 | 3.6416 | 251.2198 | 195.5026 | 2932.5392
2020-07-01 07:00 | 3.6524 | 3.8445 | 251.8948 | 253.5349 | 3803.023
2020-07-01 08:00 | 4.1006 | 4.3163 | 252.4364 | 409.3385 | 6140.0772
2020-07-01 09:00 | 5.004 | 5.2671 | 262.8051 | 819.1031 | 12286.5459
2020-07-01 10:00 | 5.0652 | 5.3316 | 257.7112 | 851.4809 | 12772.213
2020-07-01 11:00 | 5.811 | 6.1166 | 260.2174 | 1313.6365 | 19704.5481
2020-07-01 12:00 | 5.8621 | 6.1705 | 260.4946 | 1351.3266 | 20269.8987
2020-07-01 13:00 | 5.8081 | 6.1135 | 259.8852 | 1311.4831 | 19672.2467
2020-07-01 14:00 | 5.5468 | 5.8386 | 257.7203 | 1136.4276 | 17046.4143
2020-07-01 15:00 | 5.082 | 5.3492 | 252.8936 | 860.3187 | 12904.7803
2020-07-01 16:00 | 4.8279 | 5.0818 | 247.2136 | 726.0758 | 10891.1366
2020-07-01 17:00 | 4.7407 | 4.99 | 239.9282 | 680.7756 | 10211.6334
2020-07-01 18:00 | 4.8335 | 5.0878 | 234.1846 | 729.0592 | 10935.8883
2020-07-01 19:00 | 5.0393 | 5.3044 | 224.0593 | 837.7847 | 12566.7704
2020-07-01 20:00 | 5.724 | 6.0251 | 216.497 | 1249.537 | 18743.0556
2020-07-01 21:00 | 6.0628 | 6.3817 | 218.1547 | 1499.1675 | 22487.5125
2020-07-01 22:00 | 6.1334 | 6.456 | 222.9719 | 1551.2036 | 23268.0546
2020-07-01 23:00 | 6.1607 | 6.4847 | 223.3557 | 1571.2857 | 23569.2862
2020-07-02 00:00 | 5.989 | 6.304 | 222.073 | 1444.8102 | 21672.1536
2020-07-02 01:00 | 5.9301 | 6.242 | 220.6408 | 1401.4024 | 21021.0355
2020-07-02 02:00 | 5.8306 | 6.1372 | 221.7693 | 1328.0628 | 19920.9413
2020-07-02 03:00 | 5.6051 | 5.8999 | 227.0458 | 1172.745 | 17591.1744
2020-07-02 04:00 | 4.8854 | 5.1424 | 229.4091 | 756.4737 | 11347.1052
2020-07-02 05:00 | 3.5942 | 3.7832 | 225.6973 | 235.9969 | 3539.9533
2020-07-02 06:00 | 2.992 | 3.1493 | 213.9269 | 79.9572 | 1199.3577
2020-07-02 07:00 | 3.1859 | 3.3534 | 206.8844 | 123.6362 | 1854.5425
2020-07-02 08:00 | 4.1186 | 4.3352 | 212.6735 | 415.9885 | 6239.8277
2020-07-02 09:00 | 4.497 | 4.7335 | 213.4657 | 572.5421 | 8588.1316
2020-07-02 10:00 | 4.2783 | 4.5033 | 198.3809 | 475.4067 | 7131.1012
2020-07-02 11:00 | 4.6286 | 4.872 | 199.0811 | 630.9897 | 9464.8461
2020-07-02 12:00 | 4.6316 | 4.8752 | 201.0866 | 632.3546 | 9485.3183
2020-07-02 13:00 | 4.4664 | 4.7013 | 204.5631 | 558.9524 | 8384.2859
2020-07-02 14:00 | 4.4572 | 4.6916 | 205.1329 | 554.8589 | 8322.8842
2020-07-02 15:00 | 4.171 | 4.3904 | 204.4059 | 435.427 | 6531.405
2020-07-02 16:00 | 3.8601 | 4.0631 | 192.5168 | 320.2074 | 4803.111
2020-07-02 17:00 | 4.2808 | 4.506 | 180.6127 | 476.52 | 7147.8003
2020-07-02 18:00 | 5.0088 | 5.2723 | 174.6112 | 821.6872 | 12325.3078
2020-07-02 19:00 | 5.9413 | 6.2538 | 174.4679 | 1409.6751 | 21145.126
2020-07-02 20:00 | 6.5915 | 6.9381 | 175.5907 | 1937.7739 | 29066.6085
2020-07-02 21:00 | 6.8819 | 7.2438 | 177.2339 | 2215.2433 | 33228.649
2020-07-02 22:00 | 6.3293 | 6.6622 | 179.2226 | 1713.6853 | 25705.2801
2020-07-02 23:00 | 6.5357 | 6.8794 | 172.0288 | 1890.0928 | 28351.3924
2020-07-03 00:00 | 7.0378 | 7.4079 | 170.5712 | 2368.1935 | 35522.9026
2020-07-03 01:00 | 7.549 | 7.9461 | 171.5009 | 2925.9555 | 43889.3324
2020-07-03 02:00 | 7.7715 | 8.1803 | 172.5515 | 3185.9617 | 47789.4249
2020-07-03 03:00 | 7.7075 | 8.1129 | 172.1174 | 3110.1144 | 46651.7162
2020-07-03 04:00 | 7.1875 | 7.5655 | 173.0872 | 2523.2759 | 37849.1388
2020-07-03 05:00 | 6.0551 | 6.3736 | 174.8916 | 1493.5094 | 22402.6404
2020-07-03 06:00 | 5.7593 | 6.0622 | 179.2572 | 1275.5707 | 19133.5611
2020-07-03 07:00 | 5.9778 | 6.2922 | 181.8839 | 1436.5362 | 21548.0424
2020-07-03 08:00 | 6.6026 | 6.9499 | 186.5045 | 1947.3054 | 29209.5809
2020-07-03 09:00 | 6.8889 | 7.2512 | 187.2302 | 2222.1193 | 33331.7899
2020-07-03 10:00 | 6.5003 | 6.8422 | 182.4017 | 1859.8449 | 27897.6731
2020-07-03 11:00 | 6.4091 | 6.7461 | 182.1714 | 1781.8599 | 26727.8991
2020-07-03 12:00 | 6.263 | 6.5924 | 179.2012 | 1656.9887 | 24854.8307
2020-07-03 13:00 | 5.9133 | 6.2243 | 176.3848 | 1389.0395 | 20835.593
2020-07-03 14:00 | 5.8048 | 6.1101 | 182.2239 | 1309.0388 | 19635.5821
2020-07-03 15:00 | 4.9474 | 5.2076 | 195.1968 | 789.2285 | 11838.4273
2020-07-03 16:00 | 5.9652 | 6.279 | 228.1284 | 1427.2708 | 21409.0627
2020-07-03 17:00 | 5.6897 | 5.989 | 259.2311 | 1225.4728 | 18382.0914
2020-07-03 18:00 | 4.2938 | 4.5196 | 282.212 | 482.2848 | 7234.2725
2020-07-03 19:00 | 3.9673 | 4.176 | 296.4123 | 359.943 | 5399.1454
2020-07-03 20:00 | 4.3288 | 4.5565 | 306.0832 | 497.8276 | 7467.4147
2020-07-03 21:00 | 4.2063 | 4.4276 | 315.0561 | 448.4994 | 6727.4906
2020-07-03 22:00 | 3.3038 | 3.4776 | 345.2176 | 150.1964 | 2252.9464
2020-07-03 23:00 | 1.9067 | 2.0069 | 335.5584 | 0 | 0
2020-07-04 00:00 | 2.5699 | 2.705 | 315.4518 | 0 | 0
2020-07-04 01:00 | 3.7713 | 3.9696 | 313.6542 | 289.3075 | 4339.6121
2020-07-04 02:00 | 4.7906 | 5.0426 | 313.5857 | 706.3898 | 10595.8472
2020-07-04 03:00 | 5.6921 | 5.9915 | 318.6475 | 1226.9525 | 18404.288
2020-07-04 04:00 | 5.5397 | 5.8311 | 326.7142 | 1132.0102 | 16980.1529
2020-07-04 05:00 | 5.0824 | 5.3497 | 336.9115 | 860.5483 | 12908.2248
2020-07-04 06:00 | 4.1386 | 4.3562 | 343.9037 | 423.3981 | 6350.9715
2020-07-04 07:00 | 3.1186 | 3.2826 | 345.2339 | 108.4783 | 1627.1739
2020-07-04 08:00 | 3.4256 | 3.6058 | 332.3789 | 185.2574 | 2778.8603
2020-07-04 09:00 | 3.6359 | 3.8271 | 324.4656 | 248.5459 | 3728.1884
2020-07-04 10:00 | 3.6792 | 3.8727 | 312.0468 | 261.5797 | 3923.6956
2020-07-04 11:00 | 4.3048 | 4.5312 | 314.8317 | 487.164 | 7307.4598
2020-07-04 12:00 | 4.4414 | 4.675 | 313.7267 | 547.8438 | 8217.6566
2020-07-04 13:00 | 4.5768 | 4.8176 | 318.9717 | 608.0068 | 9120.1023
2020-07-04 14:00 | 4.8828 | 5.1396 | 331.4326 | 755.0836 | 11326.2545
2020-07-04 15:00 | 5.1649 | 5.4366 | 339.2345 | 904.1584 | 13562.3759
2020-07-04 16:00 | 4.8782 | 5.1348 | 350.099 | 752.6673 | 11290.0088
2020-07-04 17:00 | 4.4537 | 4.6879 | 346.6104 | 553.298 | 8299.4697
2020-07-04 18:00 | 4.9128 | 5.1712 | 345.9856 | 770.9364 | 11564.0458
2020-07-04 19:00 | 5.1274 | 5.397 | 346.8646 | 884.3115 | 13264.6727
2020-07-04 20:00 | 5.412 | 5.6967 | 350.5802 | 1052.4392 | 15786.588
2020-07-04 21:00 | 5.4348 | 5.7206 | 354.8833 | 1066.5933 | 15998.8994
2020-07-04 22:00 | 5.0715 | 5.3382 | 337.2013 | 854.7699 | 12821.5491
2020-07-04 23:00 | 5.2576 | 5.5341 | 340.4415 | 956.1805 | 14342.7072
2020-07-05 00:00 | 5.3963 | 5.6801 | 341.0531 | 1042.6291 | 15639.4369
2020-07-05 01:00 | 5.3881 | 5.6714 | 342.4261 | 1037.4979 | 15562.4688
2020-07-05 02:00 | 5.2344 | 5.5098 | 340.2118 | 941.7722 | 14126.5831
2020-07-05 03:00 | 5.2133 | 5.4875 | 338.0045 | 929.7424 | 13946.1361
2020-07-05 04:00 | 5.2494 | 5.5255 | 334.0614 | 951.0708 | 14266.0619
2020-07-05 05:00 | 4.4372 | 4.6705 | 333.2263 | 545.9603 | 8189.4047
2020-07-05 06:00 | 4.6733 | 4.9191 | 338.1999 | 650.8523 | 9762.7843
2020-07-05 07:00 | 4.7022 | 4.9495 | 350.9276 | 663.7053 | 9955.5801
2020-07-05 08:00 | 4.1312 | 4.3485 | 355.582 | 420.6712 | 6310.0675
2020-07-05 09:00 | 3.8524 | 4.055 | 351.9666 | 317.3693 | 4760.5391
2020-07-05 10:00 | 3.1339 | 3.2987 | 350.3523 | 111.9256 | 1678.8845
2020-07-05 11:00 | 2.962 | 3.1178 | 335.8231 | 73.2149 | 1098.2237
2020-07-05 12:00 | 3.0305 | 3.1899 | 326.8098 | 88.6332 | 1329.4985
2020-07-05 13:00 | 3.3686 | 3.5458 | 324.3214 | 168.1048 | 2521.5713
2020-07-05 14:00 | 4.0261 | 4.2378 | 323.9903 | 381.7058 | 5725.5869
2020-07-05 15:00 | 4.3857 | 4.6164 | 325.9744 | 523.1278 | 7846.9174
2020-07-05 16:00 | 4.3821 | 4.6126 | 326.5138 | 521.5239 | 7822.8586
2020-07-05 17:00 | 4.4515 | 4.6856 | 327.9338 | 552.3231 | 8284.8461
2020-07-05 18:00 | 4.7534 | 5.0034 | 334.7114 | 686.707 | 10300.6051
2020-07-05 19:00 | 4.5047 | 4.7417 | 344.0595 | 575.9861 | 8639.7921
2020-07-05 20:00 | 3.9078 | 4.1133 | 351.5715 | 337.8886 | 5068.3292
2020-07-05 21:00 | 3.1844 | 3.3519 | 0.11503 | 123.3117 | 1849.6754
2020-07-05 22:00 | 2.0471 | 2.1548 | 332.7571 | 0 | 0
2020-07-05 23:00 | 1.8077 | 1.9028 | 326.5186 | 0 | 0
2020-07-06 00:00 | 1.8622 | 1.9601 | 313.1114 | 0 | 0
2020-07-06 01:00 | 2.0396 | 2.1469 | 303.6122 | 0 | 0
2020-07-06 02:00 | 2.08 | 2.1894 | 294.5934 | 0 | 0
2020-07-06 03:00 | 1.9508 | 2.0534 | 280.1487 | 0 | 0
2020-07-06 04:00 | 1.7441 | 1.8358 | 267.0998 | 0 | 0
2020-07-06 05:00 | 1.0196 | 1.0733 | 259.4821 | 0 | 0
2020-07-06 06:00 | 0.5481 | 0.57693 | 266.2409 | 0 | 0
2020-07-06 07:00 | 0.40501 | 0.42631 | 182.0339 | 0 | 0
2020-07-06 08:00 | 1.2227 | 1.287 | 178.7936 | 0 | 0
2020-07-06 09:00 | 1.8231 | 1.919 | 183.1969 | 0 | 0
2020-07-06 10:00 | 3.1589 | 3.325 | 175.6764 | 117.5535 | 1763.3026
2020-07-06 11:00 | 3.2789 | 3.4513 | 192.1966 | 144.5836 | 2168.754
2020-07-06 12:00 | 3.0406 | 3.2005 | 203.6023 | 90.9066 | 1363.599
2020-07-06 13:00 | 2.4504 | 2.5793 | 209.743 | 0 | 0
2020-07-06 14:00 | 2.1493 | 2.2623 | 212.378 | 0 | 0
2020-07-06 15:00 | 1.9192 | 2.0201 | 212.1731 | 0 | 0
2020-07-06 16:00 | 1.6135 | 1.6984 | 201.983 | 0 | 0
2020-07-06 17:00 | 1.7722 | 1.8654 | 200.0448 | 0 | 0
2020-07-06 18:00 | 2.1349 | 2.2472 | 201.5782 | 0 | 0
2020-07-06 19:00 | 2.288 | 2.4083 | 200.9025 | 0 | 0
2020-07-06 20:00 | 2.4421 | 2.5705 | 202.4093 | 0 | 0
2020-07-06 21:00 | 2.5371 | 2.6705 | 201.3663 | 0 | 0
2020-07-06 22:00 | 0.65995 | 0.69466 | 72.0393 | 0 | 0
2020-07-06 23:00 | 1.6077 | 1.6923 | 82.4767 | 0 | 0
2020-07-07 00:00 | 0.86465 | 0.91013 | 88.733 | 0 | 0
2020-07-07 01:00 | 1.4546 | 1.5311 | 312.7533 | 0 | 0
2020-07-07 02:00 | 3.4792 | 3.6622 | 327.2957 | 201.3851 | 3020.7764
2020-07-07 03:00 | 3.632 | 3.823 | 0.72986 | 247.3735 | 3710.6029
2020-07-07 04:00 | 3.0659 | 3.2272 | 40.1779 | 96.6182 | 1449.2728
2020-07-07 05:00 | 2.1112 | 2.2223 | 9.9019 | 0 | 0
2020-07-07 06:00 | 2.5256 | 2.6584 | 337.6585 | 0 | 0
2020-07-07 07:00 | 2.4734 | 2.6035 | 338.438 | 0 | 0
2020-07-07 08:00 | 2.0005 | 2.1057 | 344.5822 | 0 | 0
2020-07-07 09:00 | 3.6009 | 3.7902 | 325.0346 | 238.0094 | 3570.1409
2020-07-07 10:00 | 5.8148 | 6.1206 | 316.1433 | 1316.4198 | 19746.2965
2020-07-07 11:00 | 7.7019 | 8.107 | 318.6593 | 3103.4531 | 46551.7972
2020-07-07 12:00 | 8.8678 | 9.3342 | 327.7527 | 4467.6382 | 67014.5724
2020-07-07 13:00 | 8.7516 | 9.2119 | 338.3301 | 4336.708 | 65050.6202
2020-07-07 14:00 | 8.802 | 9.2649 | 335.3122 | 4393.4774 | 65902.1603
2020-07-07 15:00 | 10.0532 | 10.582 | 336.4032 | 5379.3217 | 80689.8256
2020-07-07 16:00 | 10.5924 | 11.1495 | 338.7983 | 5572.7864 | 83591.7956
2020-07-07 17:00 | 10.3673 | 10.9126 | 339.3074 | 5505.6112 | 82584.1673
2020-07-07 18:00 | 9.7466 | 10.2593 | 335.8712 | 5207.4067 | 78111.0999
2020-07-07 19:00 | 10.1775 | 10.7128 | 328.2905 | 5429.2801 | 81439.2011
2020-07-07 20:00 | 10.1627 | 10.6972 | 323.7878 | 5423.3131 | 81349.6971
2020-07-07 21:00 | 10.0952 | 10.6262 | 320.8909 | 5396.1977 | 80942.9655
2020-07-07 22:00 | 10.3436 | 10.8877 | 320.7957 | 5496.0871 | 82441.3071
2020-07-07 23:00 | 8.9141 | 9.383 | 323.4115 | 4519.7936 | 67796.9045
2020-07-08 00:00 | 8.2972 | 8.7336 | 323.5208 | 3809.4464 | 57141.6959
2020-07-08 01:00 | 7.7665 | 8.175 | 319.3917 | 3180.0428 | 47700.6421
2020-07-08 02:00 | 7.7986 | 8.2088 | 316.4787 | 3218.1153 | 48271.7295
2020-07-08 03:00 | 7.8782 | 8.2926 | 313.853 | 3312.4347 | 49686.5203
2020-07-08 04:00 | 9.1402 | 9.6209 | 313.3786 | 4744.3918 | 71165.8777
2020-07-08 05:00 | 9.4338 | 9.93 | 315.521 | 4998.4668 | 74977.0026
2020-07-08 06:00 | 8.7301 | 9.1893 | 316.8897 | 4312.538 | 64688.0697
2020-07-08 07:00 | 8.8981 | 9.3661 | 314.9368 | 4501.7149 | 67525.7236
2020-07-08 08:00 | 8.9115 | 9.3802 | 313.236 | 4516.8184 | 67752.2758
2020-07-08 09:00 | 8.62 | 9.0734 | 311.4205 | 4188.5334 | 62828.0004
2020-07-08 10:00 | 8.5922 | 9.0441 | 311.1189 | 4157.213 | 62358.1947
2020-07-08 11:00 | 8.3959 | 8.8375 | 308.965 | 3926.6461 | 58899.6919
2020-07-08 12:00 | 8.2315 | 8.6644 | 308.1157 | 3731.4461 | 55971.6918
2020-07-08 13:00 | 8.3363 | 8.7748 | 306.7407 | 3855.9704 | 57839.5553
2020-07-08 14:00 | 8.2028 | 8.6342 | 305.8566 | 3697.4032 | 55461.0477
2020-07-08 15:00 | 8.1917 | 8.6225 | 305.097 | 3684.1833 | 55262.7498
2020-07-08 16:00 | 7.6517 | 8.0541 | 305.7418 | 3043.9085 | 45658.6277
2020-07-08 17:00 | 5.9145 | 6.2255 | 304.9921 | 1389.8668 | 20848.0014
2020-07-08 18:00 | 5.5776 | 5.871 | 300.3667 | 1155.6229 | 17334.343
2020-07-08 19:00 | 5.4395 | 5.7256 | 295.4348 | 1069.5599 | 16043.3985
2020-07-08 20:00 | 5.3908 | 5.6744 | 288.2977 | 1039.2272 | 15588.4083
2020-07-08 21:00 | 5.4984 | 5.7875 | 280.0146 | 1106.2246 | 16593.3688
2020-07-08 22:00 | 5.9233 | 6.2349 | 275.916 | 1396.4183 | 20946.2746
2020-07-08 23:00 | 5.7744 | 6.0781 | 271.0076 | 1286.6542 | 19299.8123
2020-07-09 00:00 | 5.6634 | 5.9613 | 266.6849 | 1209.0734 | 18136.1006
2020-07-09 01:00 | 5.8342 | 6.141 | 264.6515 | 1330.7058 | 19960.5872
2020-07-09 02:00 | 5.5222 | 5.8126 | 264.6965 | 1121.0757 | 16816.1356
2020-07-09 03:00 | 4.634 | 4.8777 | 262.1813 | 633.3888 | 9500.8325
2020-07-09 04:00 | 3.9471 | 4.1547 | 258.5399 | 352.4649 | 5286.9741
2020-07-09 05:00 | 3.526 | 3.7115 | 268.4306 | 215.4824 | 3232.2353
2020-07-09 06:00 | 3.6738 | 3.867 | 280.2944 | 259.9616 | 3899.4237
2020-07-09 07:00 | 3.219 | 3.3883 | 282.6061 | 131.09 | 1966.3498
2020-07-09 08:00 | 2.3996 | 2.5258 | 267.8718 | 0 | 0
2020-07-09 09:00 | 2.5346 | 2.6679 | 247.0026 | 0 | 0
2020-07-09 10:00 | 3.1762 | 3.3433 | 250.2129 | 121.4655 | 1821.9823
2020-07-09 11:00 | 3.7706 | 3.9689 | 262.0518 | 289.1085 | 4336.6275
2020-07-09 12:00 | 4.3653 | 4.5949 | 274.6421 | 514.045 | 7710.6754
2020-07-09 13:00 | 3.8573 | 4.0602 | 280.3631 | 319.1905 | 4787.857
2020-07-09 14:00 | 3.4011 | 3.58 | 282.2052 | 177.8772 | 2668.158
2020-07-09 15:00 | 3.163 | 3.3294 | 284.3905 | 118.4842 | 1777.2635
2020-07-09 16:00 | 2.4019 | 2.5282 | 283.3086 | 0 | 0
2020-07-09 17:00 | 1.8507 | 1.9481 | 282.6323 | 0 | 0
2020-07-09 18:00 | 1.7285 | 1.8194 | 284.5769 | 0 | 0
2020-07-09 19:00 | 1.7764 | 1.8698 | 275.4089 | 0 | 0
2020-07-09 20:00 | 1.793 | 1.8873 | 251.4428 | 0 | 0
2020-07-09 21:00 | 1.9383 | 2.0402 | 250.1052 | 0 | 0
2020-07-09 22:00 | 2.6371 | 2.7758 | 207.5294 | 0 | 0
2020-07-09 23:00 | 3.2579 | 3.4293 | 198.4681 | 139.87 | 2098.05
2020-07-10 00:00 | 3.7606 | 3.9584 | 194.465 | 286.1074 | 4291.6116
2020-07-10 01:00 | 4.106 | 4.322 | 189.5188 | 411.3344 | 6170.0159
2020-07-10 02:00 | 4.5845 | 4.8256 | 189.2709 | 611.4099 | 9171.1489
2020-07-10 03:00 | 4.8825 | 5.1393 | 187.8519 | 754.9204 | 11323.806
2020-07-10 04:00 | 4.7298 | 4.9786 | 183.8637 | 675.969 | 10139.5357
2020-07-10 05:00 | 3.9898 | 4.1997 | 176.618 | 368.2787 | 5524.181
2020-07-10 06:00 | 4.7261 | 4.9746 | 180.1793 | 674.3017 | 10114.5257
2020-07-10 07:00 | 4.6717 | 4.9174 | 194.1653 | 650.1512 | 9752.2675
2020-07-10 08:00 | 4.3711 | 4.601 | 204.0891 | 516.6147 | 7749.2206
2020-07-10 09:00 | 4.2596 | 4.4837 | 210.138 | 468.2561 | 7023.8411
2020-07-10 10:00 | 4.0112 | 4.2222 | 212.904 | 376.2047 | 5643.0698
2020-07-10 11:00 | 4.3506 | 4.5794 | 220.7239 | 507.4931 | 7612.3967
2020-07-10 12:00 | 4.5307 | 4.769 | 225.0958 | 587.4982 | 8812.4727
2020-07-10 13:00 | 4.1451 | 4.3632 | 222.3283 | 425.8302 | 6387.4524
2020-07-10 14:00 | 4.3495 | 4.5783 | 224.2137 | 507.026 | 7605.3901
2020-07-10 15:00 | 4.4627 | 4.6974 | 221.3189 | 557.3126 | 8359.6891
2020-07-10 16:00 | 4.1229 | 4.3398 | 201.7034 | 417.5939 | 6263.9081
2020-07-10 17:00 | 4.8399 | 5.0944 | 188.0403 | 732.4097 | 10986.145
2020-07-10 18:00 | 6.117 | 6.4387 | 182.6005 | 1539.1064 | 23086.5965
2020-07-10 19:00 | 6.6016 | 6.9488 | 182.8222 | 1946.4363 | 29196.5442
2020-07-10 20:00 | 6.6259 | 6.9744 | 184.3313 | 1967.1785 | 29507.6779
2020-07-10 21:00 | 6.6479 | 6.9975 | 183.9813 | 1985.9872 | 29789.8078
2020-07-10 22:00 | 6.8585 | 7.2192 | 180.7669 | 2192.2772 | 32884.1587
2020-07-10 23:00 | 6.8281 | 7.1872 | 179.2287 | 2162.508 | 32437.6205
2020-07-11 00:00 | 6.6179 | 6.9659 | 180.8741 | 1960.3222 | 29404.8331
2020-07-11 01:00 | 6.4851 | 6.8262 | 183.5806 | 1846.9001 | 27703.502
2020-07-11 02:00 | 6.7615 | 7.1171 | 182.6158 | 2097.1104 | 31456.6559
2020-07-11 03:00 | 6.5996 | 6.9467 | 184.1721 | 1944.6809 | 29170.2142
2020-07-11 04:00 | 5.9798 | 6.2943 | 186.9109 | 1438.0378 | 21570.5673
2020-07-11 05:00 | 4.8401 | 5.0946 | 185.15 | 732.5106 | 10987.6583
2020-07-11 06:00 | 4.3375 | 4.5656 | 185.681 | 501.6872 | 7525.3074
2020-07-11 07:00 | 4.0536 | 4.2668 | 184.4015 | 391.9227 | 5878.841
2020-07-11 08:00 | 4.4998 | 4.7365 | 186.1242 | 573.7958 | 8606.9368
2020-07-11 09:00 | 5.4939 | 5.7829 | 199.833 | 1103.4664 | 16551.9962
2020-07-11 10:00 | 4.8908 | 5.148 | 203.0185 | 759.294 | 11389.4103
2020-07-11 11:00 | 4.6717 | 4.9174 | 207.036 | 650.1437 | 9752.1557
2020-07-11 12:00 | 4.5095 | 4.7467 | 200.1939 | 578.1119 | 8671.6786
2020-07-11 13:00 | 4.6397 | 4.8837 | 192.767 | 635.9109 | 9538.6641
2020-07-11 14:00 | 4.8403 | 5.0949 | 186.0429 | 732.6406 | 10989.6096
2020-07-11 15:00 | 5.0584 | 5.3244 | 181.795 | 847.8581 | 12717.8712
2020-07-11 16:00 | 4.9155 | 5.174 | 174.9262 | 772.363 | 11585.4451
2020-07-11 17:00 | 5.3165 | 5.5962 | 173.119 | 992.9266 | 14893.8989
2020-07-11 18:00 | 6.2348 | 6.5628 | 174.2038 | 1632.9672 | 24494.5085
2020-07-11 19:00 | 6.5281 | 6.8714 | 179.5918 | 1883.5894 | 28253.841
2020-07-11 20:00 | 6.6772 | 7.0284 | 185.8168 | 2014.473 | 30217.0946
2020-07-11 21:00 | 6.7526 | 7.1077 | 191.9492 | 2088.4042 | 31326.0637
2020-07-11 22:00 | 6.1576 | 6.4814 | 208.6306 | 1569.0066 | 23535.0996
2020-07-11 23:00 | 5.015 | 5.2788 | 210.0769 | 824.9499 | 12374.2484
2020-07-12 00:00 | 3.9101 | 4.1157 | 210.1916 | 338.7361 | 5081.0414
2020-07-12 01:00 | 3.3043 | 3.4781 | 216.7401 | 150.3135 | 2254.7025
2020-07-12 02:00 | 3.224 | 3.3936 | 228.579 | 132.2213 | 1983.3193
2020-07-12 03:00 | 3.4686 | 3.651 | 240.3176 | 198.193 | 2972.8953
2020-07-12 04:00 | 2.8855 | 3.0373 | 256.6637 | 55.9756 | 839.6339
2020-07-12 05:00 | 1.2595 | 1.3257 | 298.3063 | 0 | 0
2020-07-12 06:00 | 1.6116 | 1.6963 | 342.3225 | 0 | 0
2020-07-12 07:00 | 2.6436 | 2.7826 | 341.504 | 0 | 0
2020-07-12 08:00 | 3.3443 | 3.5202 | 343.6373 | 160.7698 | 2411.5464
2020-07-12 09:00 | 3.2475 | 3.4183 | 343.6931 | 137.5114 | 2062.6714
2020-07-12 10:00 | 4.2074 | 4.4287 | 341.4746 | 448.908 | 6733.6199
2020-07-12 11:00 | 6.5451 | 6.8893 | 326.4682 | 1898.1377 | 28472.0654
2020-07-12 12:00 | 8.9463 | 9.4168 | 329.2884 | 4555.9862 | 68339.7923
2020-07-12 13:00 | 10.1608 | 10.6952 | 332.2087 | 5422.5743 | 81338.6144
2020-07-12 14:00 | 10.4274 | 10.9758 | 334.5063 | 5529.7493 | 82946.2391
2020-07-12 15:00 | 10.5105 | 11.0633 | 336.3 | 5553.2961 | 83299.4411
2020-07-12 16:00 | 10.2699 | 10.81 | 337.1599 | 5466.4191 | 81996.2867
2020-07-12 17:00 | 9.9153 | 10.4368 | 339.1923 | 5311.1125 | 79666.6881
2020-07-12 18:00 | 10.0813 | 10.6115 | 339.7497 | 5390.5849 | 80858.7741
2020-07-12 19:00 | 9.8407 | 10.3582 | 340.5705 | 5265.2098 | 78978.1474
2020-07-12 20:00 | 9.2486 | 9.735 | 337.917 | 4838.1542 | 72572.3128
2020-07-12 21:00 | 8.6238 | 9.0774 | 334.7745 | 4192.8293 | 62892.4393
2020-07-12 22:00 | 9.7822 | 10.2966 | 328.7101 | 5229.2425 | 78438.6375
2020-07-12 23:00 | 9.6191 | 10.125 | 332.1185 | 5128.9899 | 76934.849
2020-07-13 00:00 | 9.4885 | 9.9875 | 335.1462 | 5045.7219 | 75685.8283
2020-07-13 01:00 | 9.2122 | 9.6968 | 333.2356 | 4806.734 | 72101.0093
2020-07-13 02:00 | 8.9272 | 9.3967 | 331.6364 | 4534.4798 | 68017.1972
2020-07-13 03:00 | 8.6696 | 9.1256 | 329.7666 | 4244.3584 | 63665.3757
2020-07-13 04:00 | 9.3415 | 9.8328 | 330.415 | 4918.5547 | 73778.3212
2020-07-13 05:00 | 9.4578 | 9.9553 | 337.0585 | 5019.2268 | 75288.4015
2020-07-13 06:00 | 9.3048 | 9.7942 | 345.5122 | 4886.7983 | 73301.9747
2020-07-13 07:00 | 9.287 | 9.7754 | 349.1063 | 4871.3917 | 73070.8752
2020-07-13 08:00 | 9.3914 | 9.8853 | 347.5667 | 4961.7039 | 74425.5578
2020-07-13 09:00 | 9.4699 | 9.968 | 345.4517 | 5029.7098 | 75445.6475
2020-07-13 10:00 | 9.0501 | 9.5261 | 340.5822 | 4666.4842 | 69997.2627
2020-07-13 11:00 | 9.458 | 9.9554 | 338.3946 | 5019.3486 | 75290.2296
2020-07-13 12:00 | 9.677 | 10.1859 | 335.871 | 5164.5927 | 77468.8908
2020-07-13 13:00 | 9.287 | 9.7755 | 334.4896 | 4871.453 | 73071.7944
2020-07-13 14:00 | 9.5093 | 10.0094 | 335.955 | 5061.4945 | 75922.417
2020-07-13 15:00 | 8.6152 | 9.0683 | 338.3071 | 4183.0705 | 62746.0578
2020-07-13 16:00 | 8.0719 | 8.4964 | 338.5707 | 3541.9719 | 53129.5782
2020-07-13 17:00 | 7.6103 | 8.0106 | 337.0264 | 2994.9271 | 44923.9063
2020-07-13 18:00 | 7.6056 | 8.0056 | 332.6653 | 2989.3169 | 44839.7535
2020-07-13 19:00 | 7.7533 | 8.1611 | 328.7146 | 3164.3961 | 47465.942
2020-07-13 20:00 | 7.7759 | 8.1849 | 327.8632 | 3191.2155 | 47868.2325
2020-07-13 21:00 | 7.9684 | 8.3875 | 327.4603 | 3419.3699 | 51290.5478
2020-07-13 22:00 | 8.302 | 8.7387 | 323.3605 | 3815.2254 | 57228.3804
2020-07-13 23:00 | 8.1791 | 8.6093 | 320.9096 | 3669.253 | 55038.7954
2020-07-14 00:00 | 8.27 | 8.7049 | 319.5868 | 3777.1472 | 56657.2085
2020-07-14 01:00 | 8.2857 | 8.7215 | 317.5784 | 3795.8459 | 56937.6886
2020-07-14 02:00 | 8.2488 | 8.6826 | 317.2581 | 3751.9844 | 56279.7662
2020-07-14 03:00 | 8.3293 | 8.7674 | 318.0424 | 3847.6228 | 57714.3414
2020-07-14 04:00 | 8.3085 | 8.7454 | 318.3725 | 3822.8533 | 57342.7999
2020-07-14 05:00 | 7.6713 | 8.0748 | 321.522 | 3067.1732 | 46007.5982
2020-07-14 06:00 | 7.6005 | 8.0002 | 325.3847 | 2983.2768 | 44749.1525
2020-07-14 07:00 | 8.0301 | 8.4524 | 331.1031 | 3492.3978 | 52385.9672
2020-07-14 08:00 | 8.6858 | 9.1426 | 338.1768 | 4262.6322 | 63939.483
2020-07-14 09:00 | 8.655 | 9.1102 | 341.6688 | 4227.8745 | 63418.1179
2020-07-14 10:00 | 7.5133 | 7.9085 | 334.7022 | 2886.1735 | 43292.603
2020-07-14 11:00 | 7.648 | 8.0503 | 331.9439 | 3039.5826 | 45593.7395
2020-07-14 12:00 | 7.9751 | 8.3945 | 328.5253 | 3427.2149 | 51408.2234
2020-07-14 13:00 | 8.2645 | 8.6992 | 325.862 | 3770.6558 | 56559.8372
2020-07-14 14:00 | 8.3829 | 8.8238 | 326.9876 | 3911.2539 | 58668.8082
2020-07-14 15:00 | 8.3506 | 8.7898 | 327.7515 | 3872.8992 | 58093.488
2020-07-14 16:00 | 7.9842 | 8.4041 | 326.8924 | 3438.0591 | 51570.8862
2020-07-14 17:00 | 7.8784 | 8.2928 | 323.7576 | 3312.6482 | 49689.7235
2020-07-14 18:00 | 7.7831 | 8.1925 | 318.6385 | 3199.7173 | 47995.7597
2020-07-14 19:00 | 7.7002 | 8.1052 | 313.6006 | 3101.4515 | 46521.7731
2020-07-14 20:00 | 7.5658 | 7.9638 | 310.4382 | 2944.6602 | 44169.9025
2020-07-14 21:00 | 7.3359 | 7.7217 | 308.8494 | 2688.5847 | 40328.7701
2020-07-14 22:00 | 7.2577 | 7.6394 | 306.9083 | 2601.4593 | 39021.8888
2020-07-14 23:00 | 6.9787 | 7.3458 | 302.0165 | 2310.2799 | 34654.1982
2020-07-15 00:00 | 7.1155 | 7.4897 | 295.9639 | 2444.4082 | 36666.1232
2020-07-15 01:00 | 7.137 | 7.5123 | 293.5696 | 2467.0468 | 37005.7025
2020-07-15 02:00 | 7.1227 | 7.4973 | 292.1822 | 2451.5172 | 36772.7583
2020-07-15 03:00 | 6.805 | 7.1629 | 290.787 | 2139.8207 | 32097.3098
2020-07-15 04:00 | 6.5799 | 6.926 | 286.6493 | 1927.8846 | 28918.269
2020-07-15 05:00 | 5.8787 | 6.1879 | 286.4918 | 1363.5358 | 20453.0364
2020-07-15 06:00 | 5.8525 | 6.1603 | 287.2325 | 1344.2391 | 20163.5869
2020-07-15 07:00 | 6.3388 | 6.6722 | 292.0199 | 1721.7969 | 25826.9536
2020-07-15 08:00 | 6.9941 | 7.362 | 296.94 | 2325.3386 | 34880.0785
2020-07-15 09:00 | 6.8531 | 7.2135 | 297.9592 | 2186.9874 | 32804.8108
2020-07-15 10:00 | 6.1173 | 6.4391 | 302.5841 | 1539.3558 | 23090.3377
2020-07-15 11:00 | 5.7339 | 6.0354 | 300.3084 | 1256.8008 | 18852.0118
2020-07-15 12:00 | 5.7234 | 6.0244 | 296.4771 | 1249.0843 | 18736.2641
2020-07-15 13:00 | 5.7397 | 6.0416 | 294.7829 | 1261.1054 | 18916.5811
2020-07-15 14:00 | 5.4969 | 5.7861 | 295.0198 | 1105.3462 | 16580.1929
2020-07-15 15:00 | 5.635 | 5.9314 | 294.3815 | 1191.376 | 17870.6399
2020-07-15 16:00 | 4.6722 | 4.918 | 299.1443 | 650.3878 | 9755.8165
2020-07-15 17:00 | 3.9166 | 4.1226 | 308.5308 | 341.1702 | 5117.5525
2020-07-15 18:00 | 3.431 | 3.6115 | 318.2081 | 186.8843 | 2803.2638
2020-07-15 19:00 | 3.1678 | 3.3345 | 328.9323 | 119.5728 | 1793.5914
2020-07-15 20:00 | 3.023 | 3.182 | 342.6745 | 86.9518 | 1304.2773
2020-07-15 21:00 | 3.0285 | 3.1878 | 352.7841 | 88.1792 | 1322.6875
2020-07-15 22:00 | 2.7313 | 2.8749 | 346.333 | 0 | 0
2020-07-15 23:00 | 1.8018 | 1.8965 | 337.9448 | 0 | 0
2020-07-16 00:00 | 1.233 | 1.2978 | 301.0661 | 0 | 0
2020-07-16 01:00 | 1.482 | 1.5599 | 259.4107 | 0 | 0
2020-07-16 02:00 | 1.9095 | 2.0099 | 244.8838 | 0 | 0
2020-07-16 03:00 | 2.3034 | 2.4245 | 245.3915 | 0 | 0
2020-07-16 04:00 | 3.0697 | 3.2311 | 249.089 | 97.4562 | 1461.8437
2020-07-16 05:00 | 2.5975 | 2.7342 | 244.7374 | 0 | 0
2020-07-16 06:00 | 1.7439 | 1.8356 | 242.6655 | 0 | 0
2020-07-16 07:00 | 1.4048 | 1.4786 | 259.9864 | 0 | 0
2020-07-16 08:00 | 1.1008 | 1.1587 | 299.6534 | 0 | 0
2020-07-16 09:00 | 1.1877 | 1.2502 | 304.522 | 0 | 0
2020-07-16 10:00 | 0.78163 | 0.82274 | 292.8699 | 0 | 0
2020-07-16 11:00 | 1.4537 | 1.5302 | 276.5078 | 0 | 0
2020-07-16 12:00 | 1.1072 | 1.1654 | 270.5022 | 0 | 0
2020-07-16 13:00 | 0.89643 | 0.94358 | 263.632 | 0 | 0
2020-07-16 14:00 | 0.48482 | 0.51032 | 210.6904 | 0 | 0
2020-07-16 15:00 | 0.54809 | 0.57691 | 134.3074 | 0 | 0
2020-07-16 16:00 | 0.86404 | 0.90949 | 135.4937 | 0 | 0
2020-07-16 17:00 | 1.4584 | 1.5351 | 144.0652 | 0 | 0
2020-07-16 18:00 | 1.9549 | 2.0577 | 155.8519 | 0 | 0
2020-07-16 19:00 | 2.0596 | 2.1679 | 165.6208 | 0 | 0
2020-07-16 20:00 | 2.1668 | 2.2808 | 185.5598 | 0 | 0
2020-07-16 21:00 | 2.2629 | 2.3819 | 218.4702 | 0 | 0
2020-07-16 22:00 | 1.6153 | 1.7003 | 210.9635 | 0 | 0
2020-07-16 23:00 | 1.5436 | 1.6248 | 228.5586 | 0 | 0
2020-07-17 00:00 | 1.6341 | 1.7201 | 246.6116 | 0 | 0
2020-07-17 01:00 | 1.4984 | 1.5772 | 248.2525 | 0 | 0
2020-07-17 02:00 | 1.7022 | 1.7917 | 243.3957 | 0 | 0
2020-07-17 03:00 | 1.7328 | 1.824 | 257.5813 | 0 | 0
2020-07-17 04:00 | 1.4844 | 1.5624 | 285.2846 | 0 | 0
2020-07-17 05:00 | 1.0628 | 1.1187 | 315.2658 | 0 | 0
2020-07-17 06:00 | 0.45678 | 0.4808 | 336.1879 | 0 | 0
2020-07-17 07:00 | 0.24831 | 0.26137 | 353.0929 | 0 | 0
2020-07-17 08:00 | 0.42257 | 0.44479 | 70.3271 | 0 | 0
2020-07-17 09:00 | 1.0598 | 1.1155 | 112.532 | 0 | 0
2020-07-17 10:00 | 1.3432 | 1.4138 | 119.2029 | 0 | 0
2020-07-17 11:00 | 1.3552 | 1.4265 | 99.8515 | 0 | 0
2020-07-17 12:00 | 1.6591 | 1.7464 | 82.6001 | 0 | 0
2020-07-17 13:00 | 1.9411 | 2.0432 | 76.3817 | 0 | 0
2020-07-17 14:00 | 2.2824 | 2.4024 | 76.0874 | 0 | 0
2020-07-17 15:00 | 2.2669 | 2.3861 | 82.9767 | 0 | 0
2020-07-17 16:00 | 2.8268 | 2.9754 | 58.0725 | 0 | 0
2020-07-17 17:00 | 3.518 | 3.703 | 62.6493 | 213.0605 | 3195.9079
2020-07-17 18:00 | 3.8298 | 4.0312 | 62.9143 | 308.9741 | 4634.6115
2020-07-17 19:00 | 4.6748 | 4.9207 | 61.4854 | 651.5151 | 9772.7261
2020-07-17 20:00 | 4.895 | 5.1524 | 65.0321 | 761.5192 | 11422.7873
2020-07-17 21:00 | 4.9079 | 5.1661 | 69.2183 | 768.367 | 11525.5051
2020-07-17 22:00 | 3.8656 | 4.0689 | 87.5775 | 322.2531 | 4833.796
2020-07-17 23:00 | 3.2948 | 3.4681 | 99.2608 | 148.1689 | 2222.5334
2020-07-18 00:00 | 2.1359 | 2.2483 | 108.49 | 0 | 0
2020-07-18 01:00 | 1.5053 | 1.5845 | 86.6284 | 0 | 0
2020-07-18 02:00 | 2.3155 | 2.4373 | 56.7666 | 0 | 0
2020-07-18 03:00 | 3.3646 | 3.5416 | 57.6467 | 166.8932 | 2503.3986
2020-07-18 04:00 | 3.296 | 3.4693 | 63.7811 | 148.4402 | 2226.6023
2020-07-18 05:00 | 2.3205 | 2.4426 | 61.9007 | 0 | 0
2020-07-18 06:00 | 2.3594 | 2.4835 | 57.3127 | 0 | 0
2020-07-18 07:00 | 2.7971 | 2.9442 | 60.2894 | 0 | 0
2020-07-18 08:00 | 3.0362 | 3.1959 | 65.707 | 89.9185 | 1348.7782
2020-07-18 09:00 | 3.0413 | 3.2013 | 65.3993 | 91.0685 | 1366.0278
2020-07-18 10:00 | 2.0413 | 2.1487 | 64.3712 | 0 | 0
2020-07-18 11:00 | 2.4871 | 2.6179 | 47.9281 | 0 | 0
2020-07-18 12:00 | 3.2823 | 3.4549 | 42.1829 | 145.3476 | 2180.2137
2020-07-18 13:00 | 3.8516 | 4.0542 | 46.087 | 317.0636 | 4755.9538
2020-07-18 14:00 | 4.1475 | 4.3656 | 50.7606 | 426.6962 | 6400.4431
2020-07-18 15:00 | 4.615 | 4.8577 | 55.1464 | 624.9516 | 9374.2741
2020-07-18 16:00 | 4.8105 | 5.0635 | 61.5244 | 716.855 | 10752.8245
2020-07-18 17:00 | 4.9477 | 5.2079 | 69.9551 | 789.3883 | 11840.8251
2020-07-18 18:00 | 5.4796 | 5.7678 | 73.1731 | 1094.513 | 16417.6954
2020-07-18 19:00 | 6.2049 | 6.5313 | 75.5298 | 1607.3879 | 24110.8184
2020-07-18 20:00 | 6.6416 | 6.9909 | 78.1391 | 1980.6376 | 29709.5643
2020-07-18 21:00 | 6.5991 | 6.9462 | 81.9632 | 1944.3354 | 29165.0304
2020-07-18 22:00 | 6.2545 | 6.5834 | 94.0646 | 1649.7389 | 24746.0833
2020-07-18 23:00 | 5.8056 | 6.1109 | 90.9254 | 1309.6246 | 19644.3692
2020-07-19 00:00 | 5.5055 | 5.7951 | 90.3773 | 1110.698 | 16660.4697
2020-07-19 01:00 | 5.3696 | 5.652 | 92.4264 | 1026.0043 | 15390.0644
2020-07-19 02:00 | 4.9248 | 5.1839 | 91.2575 | 777.3011 | 11659.5167
2020-07-19 03:00 | 4.9632 | 5.2242 | 86.6548 | 797.5428 | 11963.1419
2020-07-19 04:00 | 4.8216 | 5.0752 | 82.9149 | 722.7415 | 10841.122
2020-07-19 05:00 | 3.6626 | 3.8552 | 80.5021 | 256.5979 | 3848.9687
2020-07-19 06:00 | 3.4922 | 3.6758 | 81.939 | 205.2922 | 3079.3836
2020-07-19 07:00 | 4.0523 | 4.2654 | 83.6237 | 391.4329 | 5871.4941
2020-07-19 08:00 | 4.0186 | 4.23 | 80.5191 | 378.9473 | 5684.2089
2020-07-19 09:00 | 3.9476 | 4.1552 | 77.9161 | 352.6244 | 5289.3666
2020-07-19 10:00 | 3.4416 | 3.6226 | 69.0523 | 190.0535 | 2850.8022
2020-07-19 11:00 | 3.7931 | 3.9926 | 68.7527 | 295.8771 | 4438.1572
2020-07-19 12:00 | 4.1269 | 4.3439 | 71.1764 | 419.0631 | 6285.9472
2020-07-19 13:00 | 4.2913 | 4.517 | 70.8491 | 481.1553 | 7217.3296
2020-07-19 14:00 | 4.1283 | 4.3454 | 73.7342 | 419.5858 | 6293.7876
2020-07-19 15:00 | 4.0026 | 4.2131 | 75.8039 | 373.0059 | 5595.0892
2020-07-19 16:00 | 4.1601 | 4.3789 | 68.7394 | 431.3734 | 6470.6003
2020-07-19 17:00 | 4.3843 | 4.6149 | 70.5238 | 522.5019 | 7837.5284
2020-07-19 18:00 | 5.216 | 5.4903 | 75.7965 | 931.1397 | 13967.0953
2020-07-19 19:00 | 5.4615 | 5.7488 | 81.8355 | 1083.266 | 16248.9901
2020-07-19 20:00 | 5.5524 | 5.8444 | 88.7237 | 1139.8926 | 17098.3891
2020-07-19 21:00 | 5.6028 | 5.8974 | 97.3058 | 1171.2766 | 17569.1491
2020-07-19 22:00 | 4.8112 | 5.0642 | 98.7463 | 717.224 | 10758.3603
2020-07-19 23:00 | 4.6741 | 4.9199 | 107.2532 | 651.1951 | 9767.9269
2020-07-20 00:00 | 4.6648 | 4.9102 | 118.2477 | 647.0963 | 9706.4446
2020-07-20 01:00 | 4.2162 | 4.4379 | 126.8487 | 452.1476 | 6782.2145
2020-07-20 02:00 | 3.5156 | 3.7005 | 132.4254 | 212.3317 | 3184.976
2020-07-20 03:00 | 2.8651 | 3.0158 | 139.4762 | 51.3764 | 770.6462
2020-07-20 04:00 | 2.4832 | 2.6138 | 133.2481 | 0 | 0
2020-07-20 05:00 | 1.5784 | 1.6614 | 109.2381 | 0 | 0
2020-07-20 06:00 | 1.2152 | 1.2791 | 109.6319 | 0 | 0
2020-07-20 07:00 | 1.5472 | 1.6285 | 109.1885 | 0 | 0
2020-07-20 08:00 | 2.3485 | 2.472 | 103.4094 | 0 | 0
2020-07-20 09:00 | 2.3723 | 2.497 | 103.6332 | 0 | 0
2020-07-20 10:00 | 1.1804 | 1.2425 | 76.5032 | 0 | 0
2020-07-20 11:00 | 1.0965 | 1.1541 | 55.3994 | 0 | 0
2020-07-20 12:00 | 1.0696 | 1.1258 | 44.9468 | 0 | 0
2020-07-20 13:00 | 1.1645 | 1.2257 | 43.4847 | 0 | 0
2020-07-20 14:00 | 1.0316 | 1.0858 | 42.5338 | 0 | 0
2020-07-20 15:00 | 1.098 | 1.1557 | 28.417 | 0 | 0
2020-07-20 16:00 | 0.66377 | 0.69868 | 344.3976 | 0 | 0
2020-07-20 17:00 | 1.5304 | 1.6109 | 290.2139 | 0 | 0
2020-07-20 18:00 | 2.9081 | 3.0611 | 280.0051 | 61.0756 | 916.1345
2020-07-20 19:00 | 4.28 | 4.5051 | 278.8137 | 476.1548 | 7142.3219
2020-07-20 20:00 | 5.7159 | 6.0165 | 282.7268 | 1243.5335 | 18653.0018
2020-07-20 21:00 | 6.2429 | 6.5713 | 290.6346 | 1639.8857 | 24598.2862
2020-07-20 22:00 | 6.0454 | 6.3634 | 293.5909 | 1486.3716 | 22295.5743
2020-07-20 23:00 | 4.8795 | 5.1361 | 300.4728 | 753.3188 | 11299.7818
2020-07-21 00:00 | 5.9244 | 6.236 | 286.3969 | 1397.2227 | 20958.3412
2020-07-21 01:00 | 5.7513 | 6.0538 | 285.9638 | 1269.6427 | 19044.6408
2020-07-21 02:00 | 5.897 | 6.2072 | 283.1751 | 1377.0372 | 20655.558
2020-07-21 03:00 | 5.9505 | 6.2635 | 279.9949 | 1416.4317 | 21246.4752
2020-07-21 04:00 | 5.2181 | 5.4926 | 279.9865 | 932.273 | 13984.0957
2020-07-21 05:00 | 3.9456 | 4.1532 | 277.2842 | 351.9146 | 5278.7195
2020-07-21 06:00 | 3.9639 | 4.1724 | 274.5434 | 358.6842 | 5380.2636
2020-07-21 07:00 | 4.4065 | 4.6383 | 273.982 | 532.3434 | 7985.1515
2020-07-21 08:00 | 5.0748 | 5.3417 | 277.9619 | 856.5114 | 12847.6708
2020-07-21 09:00 | 5.7765 | 6.0803 | 275.0808 | 1288.2161 | 19323.2415
2020-07-21 10:00 | 6.2668 | 6.5964 | 274.9536 | 1660.2898 | 24904.3468
2020-07-21 11:00 | 6.6475 | 6.9971 | 279.6637 | 1985.6539 | 29784.8082
2020-07-21 12:00 | 7.2655 | 7.6477 | 284.7679 | 2610.2293 | 39153.4398
2020-07-21 13:00 | 8.1078 | 8.5342 | 293.9037 | 3584.5964 | 53768.9463
2020-07-21 14:00 | 6.9996 | 7.3678 | 297.5491 | 2330.7833 | 34961.7502
2020-07-21 15:00 | 7.0601 | 7.4314 | 296.539 | 2390.0677 | 35851.016
2020-07-21 16:00 | 7.6413 | 8.0432 | 298.126 | 3031.6245 | 45474.3671
2020-07-21 17:00 | 7.3279 | 7.7133 | 300.6523 | 2679.6502 | 40194.7524
2020-07-21 18:00 | 7.203 | 7.5818 | 305.5417 | 2540.5588 | 38108.3826
2020-07-21 19:00 | 6.9907 | 7.3584 | 305.6286 | 2322.0039 | 34830.0581
2020-07-21 20:00 | 6.9054 | 7.2686 | 305.0088 | 2238.3173 | 33574.7602
2020-07-21 21:00 | 6.8563 | 7.2169 | 303.7585 | 2190.1204 | 32851.8054
2020-07-21 22:00 | 7.1164 | 7.4907 | 299.9118 | 2445.3531 | 36680.2961
2020-07-21 23:00 | 7.0206 | 7.3898 | 300.9698 | 2351.311 | 35269.665
2020-07-22 00:00 | 7.0483 | 7.419 | 301.4665 | 2378.466 | 35676.9895
2020-07-22 01:00 | 7.0062 | 7.3747 | 301.2491 | 2337.2483 | 35058.7251
2020-07-22 02:00 | 6.9086 | 7.2719 | 301.0388 | 2241.4284 | 33621.4261
2020-07-22 03:00 | 6.4794 | 6.8202 | 301.1666 | 1842.017 | 27630.2556
2020-07-22 04:00 | 5.7017 | 6.0016 | 298.7497 | 1233.1119 | 18496.6788
2020-07-22 05:00 | 5.2198 | 5.4944 | 295.0902 | 933.1717 | 13997.5753
2020-07-22 06:00 | 5.7502 | 6.0526 | 293.5476 | 1268.8458 | 19032.6863
2020-07-22 07:00 | 7.1052 | 7.4789 | 297.2917 | 2434.3422 | 36515.1331
2020-07-22 08:00 | 8.1433 | 8.5715 | 298.0432 | 3626.7001 | 54400.502
2020-07-22 09:00 | 8.444 | 8.8881 | 300.5918 | 3983.7308 | 59755.9616
2020-07-22 10:00 | 8.1764 | 8.6065 | 302.3451 | 3666.0828 | 54991.2427
2020-07-22 11:00 | 8.6115 | 9.0644 | 302.0857 | 4178.9422 | 62684.1326
2020-07-22 12:00 | 9.0609 | 9.5375 | 297.9857 | 4675.8299 | 70137.4479
2020-07-22 13:00 | 8.8269 | 9.2911 | 298.1525 | 4421.4926 | 66322.3895
2020-07-22 14:00 | 8.7752 | 9.2367 | 299.02 | 4363.2804 | 65449.2055
2020-07-22 15:00 | 8.3241 | 8.7619 | 298.9239 | 3841.4386 | 57621.5795
2020-07-22 16:00 | 7.4954 | 7.8896 | 301.5018 | 2866.2202 | 42993.3032
2020-07-22 17:00 | 6.5494 | 6.8939 | 304.9556 | 1901.8438 | 28527.6574
2020-07-22 18:00 | 6.0778 | 6.3975 | 309.3682 | 1510.2294 | 22653.4414
2020-07-22 19:00 | 5.8792 | 6.1884 | 312.8425 | 1363.8568 | 20457.8518
2020-07-22 20:00 | 5.7451 | 6.0473 | 318.3056 | 1265.0999 | 18976.4992
2020-07-22 21:00 | 5.3475 | 5.6287 | 321.4747 | 1012.1978 | 15182.9669
2020-07-22 22:00 | 4.817 | 5.0703 | 308.4909 | 720.3101 | 10804.6521
2020-07-22 23:00 | 4.8113 | 5.0643 | 298.5944 | 717.2889 | 10759.3328
2020-07-23 00:00 | 4.94 | 5.1998 | 293.1697 | 785.3212 | 11779.8176
2020-07-23 01:00 | 5.082 | 5.3492 | 293.2044 | 860.3179 | 12904.7684
2020-07-23 02:00 | 4.8357 | 5.09 | 298.7404 | 730.2028 | 10953.0418
2020-07-23 03:00 | 4.2822 | 4.5074 | 305.7646 | 477.1231 | 7156.8468
2020-07-23 04:00 | 3.5251 | 3.7105 | 304.2051 | 215.1954 | 3227.9311
2020-07-23 05:00 | 2.1017 | 2.2122 | 296.8296 | 0 | 0
2020-07-23 06:00 | 1.4688 | 1.5461 | 279.8541 | 0 | 0
2020-07-23 07:00 | 1.8725 | 1.971 | 257.273 | 0 | 0
2020-07-23 08:00 | 3.5011 | 3.6853 | 276.4022 | 207.9821 | 3119.7318
2020-07-23 09:00 | 3.8361 | 4.0378 | 283.7514 | 311.3112 | 4669.6676
2020-07-23 10:00 | 3.5361 | 3.722 | 268.5995 | 218.5028 | 3277.542
2020-07-23 11:00 | 4.3362 | 4.5642 | 264.9033 | 501.1001 | 7516.5016
2020-07-23 12:00 | 4.5459 | 4.785 | 268.5529 | 594.2855 | 8914.2827
2020-07-23 13:00 | 4.4 | 4.6315 | 270.5854 | 529.4757 | 7942.136
2020-07-23 14:00 | 3.9965 | 4.2067 | 272.1756 | 370.7461 | 5561.1917
2020-07-23 15:00 | 3.9662 | 4.1748 | 273.2186 | 359.5363 | 5393.0448
2020-07-23 16:00 | 4.0289 | 4.2408 | 276.099 | 382.747 | 5741.2047
2020-07-23 17:00 | 4.052 | 4.2651 | 289.1754 | 391.3295 | 5869.9428
2020-07-23 18:00 | 4.2955 | 4.5214 | 319.8193 | 483.0459 | 7245.6882
2020-07-23 19:00 | 5.0994 | 5.3676 | 344.6805 | 869.5147 | 13042.7202
2020-07-23 20:00 | 5.4074 | 5.6918 | 353.8019 | 1049.5186 | 15742.7791
2020-07-23 21:00 | 5.0941 | 5.362 | 2.0043 | 866.7457 | 13001.1848
2020-07-23 22:00 | 4.0186 | 4.2299 | 0.050255 | 378.9342 | 5684.0134
2020-07-23 23:00 | 3.7038 | 3.8986 | 354.3365 | 268.9932 | 4034.8982
2020-07-24 00:00 | 2.7595 | 2.9046 | 349.7066 | 0 | 0
2020-07-24 01:00 | 2.1957 | 2.3111 | 339.7048 | 0 | 0
2020-07-24 02:00 | 2.1758 | 2.2903 | 326.1777 | 0 | 0
2020-07-24 03:00 | 2.2141 | 2.3305 | 322.0632 | 0 | 0
2020-07-24 04:00 | 2.0356 | 2.1427 | 325.3549 | 0 | 0
2020-07-24 05:00 | 1.3129 | 1.3819 | 326.9948 | 0 | 0
2020-07-24 06:00 | 1.4885 | 1.5668 | 343.6357 | 0 | 0
2020-07-24 07:00 | 0.98591 | 1.0378 | 5.2481 | 0 | 0
2020-07-24 08:00 | 0.62917 | 0.66226 | 357.0849 | 0 | 0
2020-07-24 09:00 | 0.9349 | 0.98408 | 312.2376 | 0 | 0
2020-07-24 10:00 | 0.47735 | 0.50246 | 292.8718 | 0 | 0
2020-07-24 11:00 | 1.6632 | 1.7507 | 291.6433 | 0 | 0
2020-07-24 12:00 | 1.9521 | 2.0547 | 300.2022 | 0 | 0
2020-07-24 13:00 | 1.9532 | 2.056 | 304.1151 | 0 | 0
2020-07-24 14:00 | 1.0823 | 1.1392 | 319.4719 | 0 | 0
2020-07-24 15:00 | 0.48521 | 0.51073 | 342.7457 | 0 | 0
2020-07-24 16:00 | 1.242 | 1.3073 | 66.1405 | 0 | 0
2020-07-24 17:00 | 3.4693 | 3.6518 | 79.6491 | 198.4058 | 2976.0877
2020-07-24 18:00 | 5.5691 | 5.862 | 93.555 | 1150.3141 | 17254.712
2020-07-24 19:00 | 7.0308 | 7.4006 | 103.454 | 2361.3484 | 35420.2263
2020-07-24 20:00 | 7.5567 | 7.9542 | 113.5721 | 2934.5154 | 44017.7304
2020-07-24 21:00 | 7.844 | 8.2566 | 122.6443 | 3271.914 | 49078.7097
2020-07-24 22:00 | 7.8124 | 8.2233 | 129.0622 | 3234.4085 | 48516.1278
2020-07-24 23:00 | 7.0982 | 7.4715 | 135.0612 | 2427.4286 | 36411.4289
2020-07-25 00:00 | 6.6929 | 7.0449 | 138.656 | 2029.8644 | 30447.9665
2020-07-25 01:00 | 6.2749 | 6.6049 | 139.1625 | 1667.2038 | 25008.0576
2020-07-25 02:00 | 5.8467 | 6.1543 | 138.6222 | 1339.9773 | 20099.659
2020-07-25 03:00 | 5.996 | 6.3114 | 128.6424 | 1449.9813 | 21749.7193
2020-07-25 04:00 | 6.2742 | 6.6042 | 123.318 | 1666.6419 | 24999.629
2020-07-25 05:00 | 5.6042 | 5.8989 | 129.9801 | 1172.1744 | 17582.6166
2020-07-25 06:00 | 4.7581 | 5.0084 | 136.7127 | 689.1991 | 10337.9867
2020-07-25 07:00 | 4.2814 | 4.5066 | 133.1416 | 476.7782 | 7151.6726
2020-07-25 08:00 | 4.2451 | 4.4684 | 135.6868 | 462.8754 | 6943.1307
2020-07-25 09:00 | 4.2252 | 4.4474 | 143.0987 | 455.4925 | 6832.3869
2020-07-25 10:00 | 3.4781 | 3.661 | 120.1652 | 201.0437 | 3015.6558
2020-07-25 11:00 | 4.3965 | 4.6277 | 117.0808 | 527.8939 | 7918.409
2020-07-25 12:00 | 4.9277 | 5.1868 | 117.8683 | 778.7877 | 11681.816
2020-07-25 13:00 | 5.2832 | 5.5611 | 121.6892 | 972.1623 | 14582.4345
2020-07-25 14:00 | 6.1628 | 6.4869 | 139.7844 | 1572.8526 | 23592.7884
2020-07-25 15:00 | 6.3371 | 6.6704 | 138.9886 | 1720.3455 | 25805.1823
2020-07-25 16:00 | 6.5167 | 6.8594 | 142.1913 | 1873.8483 | 28107.7251
2020-07-25 17:00 | 6.1107 | 6.4321 | 148.2413 | 1534.4352 | 23016.5278
2020-07-25 18:00 | 5.7866 | 6.0909 | 147.7594 | 1295.658 | 19434.8706
2020-07-25 19:00 | 5.1313 | 5.4011 | 141.3764 | 886.3711 | 13295.5667
2020-07-25 20:00 | 4.6667 | 4.9121 | 141.5398 | 647.9091 | 9718.6372
2020-07-25 21:00 | 3.975 | 4.1841 | 145.739 | 362.7893 | 5441.8397
2020-07-25 22:00 | 2.6517 | 2.7911 | 184.4221 | 0 | 0
2020-07-25 23:00 | 2.1173 | 2.2286 | 186.2915 | 0 | 0
2020-07-26 00:00 | 1.7593 | 1.8518 | 148.9563 | 0 | 0
2020-07-26 01:00 | 2.5825 | 2.7183 | 113.3992 | 0 | 0
2020-07-26 02:00 | 3.6185 | 3.8088 | 108.4343 | 243.3281 | 3649.9212
2020-07-26 03:00 | 3.5408 | 3.7271 | 109.7782 | 219.9436 | 3299.1535
2020-07-26 04:00 | 3.0499 | 3.2103 | 110.2552 | 93.0032 | 1395.0477
2020-07-26 05:00 | 2.6497 | 2.7891 | 110.7731 | 0 | 0
2020-07-26 06:00 | 2.7291 | 2.8726 | 109.9389 | 0 | 0
2020-07-26 07:00 | 3.0069 | 3.1651 | 110.4554 | 83.3291 | 1249.9358
2020-07-26 08:00 | 2.987 | 3.1441 | 107.9671 | 78.8273 | 1182.4098
2020-07-26 09:00 | 3.3907 | 3.569 | 101.6372 | 174.7329 | 2620.9941
2020-07-26 10:00 | 3.8548 | 4.0575 | 95.9234 | 318.2473 | 4773.709
2020-07-26 11:00 | 3.6079 | 3.7977 | 107.6227 | 240.1297 | 3601.9449
2020-07-26 12:00 | 3.5211 | 3.7063 | 116.9842 | 214.0124 | 3210.1858
2020-07-26 13:00 | 3.8308 | 4.0322 | 109.9791 | 309.3493 | 4640.2395
2020-07-26 14:00 | 3.8867 | 4.0911 | 106.1177 | 330.0762 | 4951.143
2020-07-26 15:00 | 4.43 | 4.663 | 115.9403 | 542.7876 | 8141.8135
2020-07-26 16:00 | 5.0624 | 5.3287 | 138.9261 | 850.0092 | 12750.1377
2020-07-26 17:00 | 4.6391 | 4.8831 | 133.3057 | 635.6857 | 9535.2856
2020-07-26 18:00 | 5.2885 | 5.5666 | 123.8488 | 975.4393 | 14631.5888
2020-07-26 19:00 | 5.1194 | 5.3886 | 125.4014 | 880.0972 | 13201.4576
2020-07-26 20:00 | 5.3323 | 5.6127 | 124.3447 | 1002.7189 | 15040.7835
2020-07-26 21:00 | 5.6715 | 5.9698 | 124.0951 | 1214.1118 | 18211.6763
2020-07-26 22:00 | 4.9571 | 5.2178 | 112.229 | 794.3519 | 11915.2782
2020-07-26 23:00 | 4.8624 | 5.1181 | 115.8434 | 744.3082 | 11164.6236
2020-07-27 00:00 | 4.7216 | 4.97 | 118.0501 | 672.3296 | 10084.9439
2020-07-27 01:00 | 4.7097 | 4.9574 | 117.4972 | 667.0309 | 10005.4635
2020-07-27 02:00 | 4.4676 | 4.7026 | 123.1652 | 559.4812 | 8392.2186
2020-07-27 03:00 | 3.9773 | 4.1864 | 128.123 | 363.6279 | 5454.4182
2020-07-27 04:00 | 2.9684 | 3.1245 | 134.3056 | 74.6458 | 1119.6877
2020-07-27 05:00 | 1.0483 | 1.1034 | 144.6368 | 0 | 0
2020-07-27 06:00 | 0.25126 | 0.26448 | 333.7228 | 0 | 0
2020-07-27 07:00 | 0.89004 | 0.93685 | 358.0891 | 0 | 0
2020-07-27 08:00 | 1.4044 | 1.4783 | 24.2022 | 0 | 0
2020-07-27 09:00 | 1.7657 | 1.8586 | 42.206 | 0 | 0
2020-07-27 10:00 | 1.4372 | 1.5128 | 52.1014 | 0 | 0
2020-07-27 11:00 | 1.7154 | 1.8056 | 44.6472 | 0 | 0
2020-07-27 12:00 | 2.2248 | 2.3418 | 25.8037 | 0 | 0
2020-07-27 13:00 | 3.4834 | 3.6667 | 0.70175 | 202.6638 | 3039.9567
2020-07-27 14:00 | 4.24 | 4.4629 | 11.6481 | 460.9583 | 6914.3748
2020-07-27 15:00 | 4.2675 | 4.4919 | 45.4075 | 471.1615 | 7067.4226
2020-07-27 16:00 | 3.1818 | 3.3492 | 56.9979 | 122.7237 | 1840.8549
2020-07-27 17:00 | 3.1812 | 3.3486 | 58.7098 | 122.5912 | 1838.8682
2020-07-27 18:00 | 3.4241 | 3.6042 | 39.1758 | 184.8114 | 2772.1716
2020-07-27 19:00 | 4.1037 | 4.3195 | 30.1209 | 410.4715 | 6157.0729
2020-07-27 20:00 | 4.0568 | 4.2702 | 33.1151 | 393.0987 | 5896.4799
2020-07-27 21:00 | 4.068 | 4.2819 | 41.577 | 397.2308 | 5958.4615
2020-07-27 22:00 | 1.7827 | 1.8765 | 12.381 | 0 | 0
2020-07-27 23:00 | 2.1812 | 2.2959 | 357.3958 | 0 | 0
2020-07-28 00:00 | 2.6336 | 2.7721 | 8.0306 | 0 | 0
2020-07-28 01:00 | 3.1262 | 3.2906 | 26.389 | 110.1939 | 1652.9081
2020-07-28 02:00 | 3.731 | 3.9272 | 40.2007 | 277.1854 | 4157.7806
2020-07-28 03:00 | 3.816 | 4.0167 | 42.6109 | 303.8879 | 4558.3188
2020-07-28 04:00 | 3.2013 | 3.3697 | 33.969 | 127.1105 | 1906.6569
2020-07-28 05:00 | 2.0853 | 2.195 | 21.3595 | 0 | 0
2020-07-28 06:00 | 1.3914 | 1.4646 | 20.2533 | 0 | 0
2020-07-28 07:00 | 1.4441 | 1.52 | 36.3972 | 0 | 0
2020-07-28 08:00 | 1.3996 | 1.4733 | 41.6316 | 0 | 0
2020-07-28 09:00 | 0.99371 | 1.046 | 26.7382 | 0 | 0
2020-07-28 10:00 | 0.62556 | 0.65846 | 62.7318 | 0 | 0
2020-07-28 11:00 | 0.25577 | 0.26922 | 72.8666 | 0 | 0
2020-07-28 12:00 | 0.2325 | 0.24473 | 215.5311 | 0 | 0
2020-07-28 13:00 | 0.35386 | 0.37247 | 176.4499 | 0 | 0
2020-07-28 14:00 | 0.73755 | 0.77634 | 169.1436 | 0 | 0
2020-07-28 15:00 | 1.0921 | 1.1496 | 176.8139 | 0 | 0
2020-07-28 16:00 | 1.0906 | 1.148 | 166.4854 | 0 | 0
2020-07-28 17:00 | 0.80751 | 0.84998 | 87.9522 | 0 | 0
2020-07-28 18:00 | 0.77971 | 0.82072 | 87.6671 | 0 | 0
2020-07-28 19:00 | 1.2152 | 1.2791 | 94.0532 | 0 | 0
2020-07-28 20:00 | 1.8931 | 1.9927 | 104.6262 | 0 | 0
2020-07-28 21:00 | 2.2479 | 2.3661 | 121.6855 | 0 | 0
2020-07-28 22:00 | 2.0891 | 2.199 | 126.4741 | 0 | 0
2020-07-28 23:00 | 1.872 | 1.9704 | 130.4479 | 0 | 0
2020-07-29 00:00 | 1.9147 | 2.0154 | 149.8987 | 0 | 0
2020-07-29 01:00 | 1.8408 | 1.9376 | 190.2531 | 0 | 0
2020-07-29 02:00 | 2.1863 | 2.3013 | 224.9683 | 0 | 0
2020-07-29 03:00 | 2.0641 | 2.1726 | 228.7251 | 0 | 0
2020-07-29 04:00 | 1.9484 | 2.0509 | 202.1481 | 0 | 0
2020-07-29 05:00 | 2.7329 | 2.8767 | 181.9956 | 0 | 0
2020-07-29 06:00 | 2.7548 | 2.8996 | 196.7796 | 0 | 0
2020-07-29 07:00 | 3.4781 | 3.661 | 216.9367 | 201.0479 | 3015.7192
2020-07-29 08:00 | 4.4004 | 4.6318 | 224.9091 | 529.6358 | 7944.5364
2020-07-29 09:00 | 5.6248 | 5.9207 | 219.4113 | 1185.0351 | 17775.5263
2020-07-29 10:00 | 4.0715 | 4.2857 | 210.7623 | 398.5515 | 5978.2721
2020-07-29 11:00 | 4.6099 | 4.8524 | 211.4277 | 622.6944 | 9340.4162
2020-07-29 12:00 | 4.7806 | 5.032 | 219.9983 | 701.0817 | 10516.2251
2020-07-29 13:00 | 4.6915 | 4.9383 | 228.6805 | 658.958 | 9884.3698
2020-07-29 14:00 | 4.3419 | 4.5703 | 227.099 | 503.6665 | 7554.9981
2020-07-29 15:00 | 6.4281 | 6.7662 | 249.0142 | 1798.1165 | 26971.748
2020-07-29 16:00 | 7.3294 | 7.7149 | 297.8151 | 2681.3863 | 40220.795
2020-07-29 17:00 | 5.3458 | 5.6269 | 320.217 | 1011.1374 | 15167.0604
2020-07-29 18:00 | 4.4432 | 4.6769 | 312.7558 | 548.6452 | 8229.6786
2020-07-29 19:00 | 4.9299 | 5.1892 | 312.514 | 779.9973 | 11699.96
2020-07-29 20:00 | 4.3937 | 4.6248 | 312.4397 | 526.6739 | 7900.108
2020-07-29 21:00 | 4.5668 | 4.807 | 316.4173 | 603.534 | 9053.0105
2020-07-29 22:00 | 4.2557 | 4.4795 | 327.0144 | 466.7953 | 7001.929
2020-07-29 23:00 | 3.7737 | 3.9722 | 321.5495 | 290.052 | 4350.7807
2020-07-30 00:00 | 3.9123 | 4.118 | 308.4754 | 339.5476 | 5093.2145
2020-07-30 01:00 | 4.6387 | 4.8826 | 304.8354 | 635.4734 | 9532.101
2020-07-30 02:00 | 4.5179 | 4.7555 | 314.6337 | 581.8187 | 8727.2799
2020-07-30 03:00 | 3.8654 | 4.0687 | 326.0563 | 322.1937 | 4832.9062
2020-07-30 04:00 | 2.9803 | 3.137 | 328.2573 | 77.3191 | 1159.7867
2020-07-30 05:00 | 2.4588 | 2.5881 | 325.3576 | 0 | 0
2020-07-30 06:00 | 1.9139 | 2.0146 | 332.1963 | 0 | 0
2020-07-30 07:00 | 1.0903 | 1.1477 | 349.7654 | 0 | 0
2020-07-30 08:00 | 0.37525 | 0.39498 | 307.0321 | 0 | 0
2020-07-30 09:00 | 0.98725 | 1.0392 | 268.4014 | 0 | 0
2020-07-30 10:00 | 1.8561 | 1.9537 | 283.4491 | 0 | 0
2020-07-30 11:00 | 2.6956 | 2.8374 | 283.0776 | 0 | 0
2020-07-30 12:00 | 3.5206 | 3.7058 | 274.3175 | 213.852 | 3207.7798
2020-07-30 13:00 | 4.0408 | 4.2533 | 268.3284 | 387.1692 | 5807.5381
2020-07-30 14:00 | 4.6357 | 4.8795 | 270.7708 | 634.1562 | 9512.3423
2020-07-30 15:00 | 3.7179 | 3.9134 | 273.4515 | 273.2382 | 4098.5728
2020-07-30 16:00 | 2.9992 | 3.1569 | 284.3748 | 81.5787 | 1223.68
2020-07-30 17:00 | 2.7706 | 2.9163 | 295.8157 | 0 | 0
2020-07-30 18:00 | 3.1614 | 3.3277 | 308.6696 | 118.1195 | 1771.7923
2020-07-30 19:00 | 3.6995 | 3.894 | 313.5507 | 267.6954 | 4015.4305
2020-07-30 20:00 | 4.0174 | 4.2287 | 306.7263 | 378.4883 | 5677.3245
2020-07-30 21:00 | 4.4941 | 4.7305 | 297.78 | 571.2758 | 8569.1368
2020-07-30 22:00 | 5.1295 | 5.3993 | 299.3108 | 885.4511 | 13281.7663
2020-07-30 23:00 | 5.1356 | 5.4057 | 304.2485 | 888.6487 | 13329.7303
2020-07-31 00:00 | 5.5243 | 5.8148 | 303.4751 | 1122.3652 | 16835.4783
2020-07-31 01:00 | 5.9558 | 6.269 | 309.7965 | 1420.3298 | 21304.9468
2020-07-31 02:00 | 5.6901 | 5.9894 | 318.1361 | 1225.7028 | 18385.5425
2020-07-31 03:00 | 4.7416 | 4.991 | 321.6985 | 681.1967 | 10217.9503
2020-07-31 04:00 | 3.4832 | 3.6664 | 320.5512 | 202.5943 | 3038.9147
2020-07-31 05:00 | 3.224 | 3.3936 | 324.094 | 132.2265 | 1983.3973
2020-07-31 06:00 | 3.4595 | 3.6415 | 322.2738 | 195.4657 | 2931.9856
2020-07-31 07:00 | 2.9452 | 3.1001 | 323.0103 | 69.4183 | 1041.2745
2020-07-31 08:00 | 3.5865 | 3.7751 | 309.4457 | 233.681 | 3505.2143
2020-07-31 09:00 | 4.7548 | 5.0048 | 296.5623 | 687.4251 | 10311.3762
2020-07-31 10:00 | 5.4399 | 5.726 | 289.5652 | 1069.7794 | 16046.6913
2020-07-31 11:00 | 5.5207 | 5.811 | 291.1651 | 1120.129 | 16801.935
2020-07-31 12:00 | 5.4298 | 5.7154 | 293.4194 | 1063.5167 | 15952.7508
2020-07-31 13:00 | 5.9723 | 6.2864 | 299.9077 | 1432.465 | 21486.9757
2020-07-31 14:00 | 6.8659 | 7.227 | 306.8122 | 2199.5608 | 32993.4127
2020-07-31 15:00 | 6.8995 | 7.2624 | 312.9455 | 2232.5698 | 33488.5468
2020-07-31 16:00 | 5.9364 | 6.2486 | 321.6227 | 1406.0326 | 21090.4896
2020-07-31 17:00 | 4.849 | 5.104 | 333.7977 | 737.2074 | 11058.1104
2020-07-31 18:00 | 4.9682 | 5.2295 | 342.2834 | 800.1918 | 12002.8763
2020-07-31 19:00 | 5.3888 | 5.6723 | 350.423 | 1037.9811 | 15569.7169
2020-07-31 20:00 | 5.1418 | 5.4122 | 353.7375 | 891.9145 | 13378.7181
2020-07-31 21:00 | 4.5841 | 4.8252 | 347.1808 | 611.2229 | 9168.3437
2020-07-31 22:00 | 4.7085 | 4.9561 | 330.4167 | 666.4696 | 9997.0444
2020-07-31 23:00 | 5.0651 | 5.3315 | 321.9663 | 851.4202 | 12771.3031
2020-08-01 00:00 | 5.5213 | 5.8117 | 319.166 | 1120.4975 | 16807.4623
2020-08-01 01:00 | 5.7865 | 6.0908 | 315.5824 | 1295.5942 | 19433.9126
2020-08-01 02:00 | 5.8693 | 6.178 | 309.4586 | 1356.5899 | 20348.848
2020-08-01 03:00 | 6.0795 | 6.3993 | 303.6323 | 1511.4834 | 22672.2514
2020-08-01 04:00 | 5.7573 | 6.0601 | 300.1909 | 1274.0572 | 19110.8587
2020-08-01 05:00 | 5.3904 | 5.6739 | 301.775 | 1038.9666 | 15584.4996
2020-08-01 06:00 | 6.0518 | 6.3701 | 304.3457 | 1491.09 | 22366.3506
2020-08-01 07:00 | 6.1423 | 6.4654 | 301.0588 | 1557.7782 | 23366.6725
2020-08-01 08:00 | 6.2161 | 6.5431 | 300.2207 | 1616.9773 | 24254.6601
2020-08-01 09:00 | 6.2109 | 6.5376 | 300.98 | 1612.5048 | 24187.5726
2020-08-01 10:00 | 6.4308 | 6.769 | 297.5234 | 1800.4162 | 27006.2429
2020-08-01 11:00 | 6.5193 | 6.8622 | 298.966 | 1876.1323 | 28141.9843
2020-08-01 12:00 | 6.4648 | 6.8048 | 303.5471 | 1829.4947 | 27442.4199
2020-08-01 13:00 | 6.8132 | 7.1715 | 311.4053 | 2147.8415 | 32217.6228
2020-08-01 14:00 | 6.4008 | 6.7374 | 319.2321 | 1774.7733 | 26621.5995
2020-08-01 15:00 | 6.5958 | 6.9427 | 323.3128 | 1941.5073 | 29122.61
2020-08-01 16:00 | 7.0737 | 7.4457 | 321.154 | 2403.3968 | 36050.9522
2020-08-01 17:00 | 5.9834 | 6.2981 | 329.0574 | 1440.6452 | 21609.6774
2020-08-01 18:00 | 5.9852 | 6.3 | 330.4469 | 1441.9853 | 21629.7796
2020-08-01 19:00 | 6.1159 | 6.4375 | 329.2617 | 1538.2805 | 23074.2071
2020-08-01 20:00 | 7.0414 | 7.4117 | 330.6204 | 2371.7364 | 35576.0464
2020-08-01 21:00 | 7.1014 | 7.4749 | 333.3928 | 2430.5702 | 36458.5531
2020-08-01 22:00 | 6.8398 | 7.1995 | 338.8267 | 2173.9766 | 32609.6487
2020-08-01 23:00 | 6.3664 | 6.7013 | 336.8497 | 1745.437 | 26181.5555
2020-08-02 00:00 | 6.2169 | 6.5438 | 332.7859 | 1617.6011 | 24264.0162
2020-08-02 01:00 | 6.1202 | 6.4421 | 328.6647 | 1541.4698 | 23122.0465
2020-08-02 02:00 | 6.2267 | 6.5542 | 325.2373 | 1626.0308 | 24390.4618
2020-08-02 03:00 | 6.2462 | 6.5747 | 322.2137 | 1642.6749 | 24640.1231
2020-08-02 04:00 | 6.0591 | 6.3777 | 324.3133 | 1496.4239 | 22446.3583
2020-08-02 05:00 | 5.4671 | 5.7546 | 334.0456 | 1086.7406 | 16301.1087
2020-08-02 06:00 | 6.6705 | 7.0214 | 341.9241 | 2007.9032 | 30118.548
2020-08-02 07:00 | 7.2894 | 7.6728 | 340.8275 | 2636.8576 | 39552.864
2020-08-02 08:00 | 7.1664 | 7.5433 | 340.9228 | 2499.804 | 37497.0602
2020-08-02 09:00 | 6.6342 | 6.9831 | 344.8489 | 1974.2543 | 29613.8145
2020-08-02 10:00 | 5.4657 | 5.7531 | 348.2111 | 1085.8492 | 16287.7381
2020-08-02 11:00 | 5.6372 | 5.9337 | 348.578 | 1192.7332 | 17890.9983
2020-08-02 12:00 | 5.4031 | 5.6872 | 346.1552 | 1046.8351 | 15702.526
2020-08-02 13:00 | 4.9586 | 5.2194 | 343.4465 | 795.1513 | 11927.2696
2020-08-02 14:00 | 4.3813 | 4.6118 | 342.4792 | 521.172 | 7817.5795
2020-08-02 15:00 | 3.8797 | 4.0838 | 340.7599 | 327.4887 | 4912.331
2020-08-02 16:00 | 3.2756 | 3.4479 | 348.1687 | 143.8456 | 2157.6838
2020-08-02 17:00 | 2.7898 | 2.9366 | 13.2324 | 0 | 0
2020-08-02 18:00 | 2.5359 | 2.6692 | 45.3986 | 0 | 0
2020-08-02 19:00 | 2.1048 | 2.2155 | 78.8514 | 0 | 0
2020-08-02 20:00 | 2.1945 | 2.31 | 124.0693 | 0 | 0
2020-08-02 21:00 | 3.0351 | 3.1948 | 150.7829 | 89.6781 | 1345.1721
2020-08-02 22:00 | 3.4381 | 3.619 | 178.6906 | 189.0243 | 2835.3641
2020-08-02 23:00 | 4.3007 | 4.5269 | 194.9034 | 485.3672 | 7280.5087
2020-08-03 00:00 | 4.909 | 5.1672 | 211.4356 | 768.9179 | 11533.7681
2020-08-03 01:00 | 4.9721 | 5.2336 | 220.8821 | 802.2755 | 12034.1331
2020-08-03 02:00 | 4.759 | 5.0093 | 220.8294 | 689.6435 | 10344.6527
2020-08-03 03:00 | 4.4926 | 4.7289 | 216.6547 | 570.5958 | 8558.9375
2020-08-03 04:00 | 4.1039 | 4.3198 | 209.8982 | 410.5641 | 6158.4622
2020-08-03 05:00 | 2.9289 | 3.083 | 202.9116 | 65.7541 | 986.3121
2020-08-03 06:00 | 2.4016 | 2.5279 | 195.6802 | 0 | 0
2020-08-03 07:00 | 2.8496 | 2.9995 | 187.9732 | 0 | 0
2020-08-03 08:00 | 3.4136 | 3.5932 | 179.6724 | 181.6508 | 2724.7621
2020-08-03 09:00 | 3.3178 | 3.4923 | 177.877 | 153.355 | 2300.3249
2020-08-03 10:00 | 4.1449 | 4.3629 | 166.1171 | 425.7405 | 6386.1073
2020-08-03 11:00 | 4.6477 | 4.8922 | 166.4427 | 639.4884 | 9592.3267
2020-08-03 12:00 | 4.6949 | 4.9418 | 170.3108 | 660.4374 | 9906.5612
2020-08-03 13:00 | 4.6556 | 4.9005 | 167.9946 | 642.9937 | 9644.9052
2020-08-03 14:00 | 4.7301 | 4.9788 | 168.2075 | 676.0715 | 10141.0718
2020-08-03 15:00 | 4.5344 | 4.7729 | 169.8364 | 589.1559 | 8837.3379
2020-08-03 16:00 | 4.4895 | 4.7256 | 162.843 | 569.2064 | 8538.0961
2020-08-03 17:00 | 4.8751 | 5.1315 | 154.8054 | 751.0143 | 11265.2152
2020-08-03 18:00 | 5.7013 | 6.0011 | 151.9144 | 1232.8047 | 18492.0699
2020-08-03 19:00 | 6.1794 | 6.5044 | 152.2589 | 1585.5533 | 23783.2995
2020-08-03 20:00 | 6.8395 | 7.1993 | 150.7307 | 2173.7048 | 32605.5722
2020-08-03 21:00 | 7.3583 | 7.7454 | 147.0144 | 2713.5895 | 40703.8428
2020-08-03 22:00 | 7.0671 | 7.4388 | 149.8019 | 2396.9505 | 35954.2578
2020-08-03 23:00 | 7.1132 | 7.4873 | 147.2862 | 2442.194 | 36632.9098
2020-08-04 00:00 | 7.6671 | 8.0703 | 144.7933 | 3062.1943 | 45932.9148
2020-08-04 01:00 | 8.0273 | 8.4495 | 147.6133 | 3489.1022 | 52336.5332
2020-08-04 02:00 | 7.7672 | 8.1757 | 155.2312 | 3180.8845 | 47713.2668
2020-08-04 03:00 | 7.4573 | 7.8495 | 160.7501 | 2823.7313 | 42355.969
2020-08-04 04:00 | 6.9866 | 7.354 | 165.8914 | 2317.9469 | 34769.203
2020-08-04 05:00 | 6.2343 | 6.5622 | 167.2146 | 1632.5008 | 24487.5113
2020-08-04 06:00 | 5.8542 | 6.1621 | 168.5618 | 1345.4579 | 20181.8692
2020-08-04 07:00 | 6.1967 | 6.5227 | 168.0901 | 1600.4036 | 24006.0543
2020-08-04 08:00 | 6.8724 | 7.2338 | 169.257 | 2205.9083 | 33088.6244
2020-08-04 09:00 | 7.4102 | 7.7999 | 168.2825 | 2771.2862 | 41569.2931
2020-08-04 10:00 | 7.6934 | 8.0981 | 161.5335 | 3093.4161 | 46401.2416
2020-08-04 11:00 | 7.9021 | 8.3177 | 158.4531 | 3340.7838 | 50111.7575
2020-08-04 12:00 | 7.9907 | 8.411 | 157.9088 | 3445.7832 | 51686.7479
2020-08-04 13:00 | 7.9106 | 8.3267 | 160.6246 | 3350.8142 | 50262.2128
2020-08-04 14:00 | 7.5966 | 7.9961 | 163.4808 | 2978.887 | 44683.3046
2020-08-04 15:00 | 6.9576 | 7.3235 | 165.413 | 2289.4917 | 34342.3758
2020-08-04 16:00 | 5.9891 | 6.3041 | 164.2651 | 1444.8971 | 21673.4568
2020-08-04 17:00 | 5.5684 | 5.8612 | 163.1399 | 1149.846 | 17247.6903
2020-08-04 18:00 | 5.8238 | 6.1301 | 158.0148 | 1323.0713 | 19846.0701
2020-08-04 19:00 | 5.8105 | 6.1161 | 159.4798 | 1313.2487 | 19698.7302
2020-08-04 20:00 | 5.7935 | 6.0982 | 160.1284 | 1300.7659 | 19511.4891
2020-08-04 21:00 | 5.7261 | 6.0273 | 157.4574 | 1251.1159 | 18766.7378
2020-08-04 22:00 | 5.6599 | 5.9576 | 159.2062 | 1206.8729 | 18103.0934
2020-08-04 23:00 | 5.6398 | 5.9364 | 153.6666 | 1194.332 | 17914.9796
2020-08-05 00:00 | 5.6806 | 5.9794 | 150.8918 | 1219.8033 | 18297.0502
2020-08-05 01:00 | 5.2045 | 5.4782 | 160.2148 | 925.0764 | 13876.1463
2020-08-05 02:00 | 4.7546 | 5.0047 | 173.505 | 687.3623 | 10310.434
2020-08-05 03:00 | 4.4082 | 4.64 | 178.7159 | 533.0849 | 7996.2728
2020-08-05 04:00 | 3.9919 | 4.2019 | 181.0395 | 369.0628 | 5535.9417
2020-08-05 05:00 | 3.1905 | 3.3583 | 185.6542 | 124.6862 | 1870.2931
2020-08-05 06:00 | 1.9711 | 2.0748 | 191.763 | 0 | 0
2020-08-05 07:00 | 2.004 | 2.1094 | 196.2519 | 0 | 0
2020-08-05 08:00 | 2.3472 | 2.4706 | 197.5181 | 0 | 0
2020-08-05 09:00 | 2.2199 | 2.3367 | 177.6482 | 0 | 0
2020-08-05 10:00 | 2.7779 | 2.924 | 154.4427 | 0 | 0
2020-08-05 11:00 | 3.0374 | 3.1972 | 146.1292 | 90.1902 | 1352.8537
2020-08-05 12:00 | 2.9621 | 3.1178 | 141.2769 | 73.2181 | 1098.2713
2020-08-05 13:00 | 2.1959 | 2.3113 | 132.5835 | 0 | 0
2020-08-05 14:00 | 2.1343 | 2.2466 | 122.0583 | 0 | 0
2020-08-05 15:00 | 2.2882 | 2.4085 | 110.1039 | 0 | 0
2020-08-05 16:00 | 2.2695 | 2.3888 | 96.4842 | 0 | 0
2020-08-05 17:00 | 2.6689 | 2.8093 | 77.7806 | 0 | 0
2020-08-05 18:00 | 4.1831 | 4.4032 | 76.6142 | 439.9116 | 6598.6742
2020-08-05 19:00 | 5.5322 | 5.8231 | 82.275 | 1127.2942 | 16909.4134
2020-08-05 20:00 | 5.9759 | 6.2902 | 91.9906 | 1435.1713 | 21527.5698
2020-08-05 21:00 | 5.9167 | 6.2279 | 106.9486 | 1391.5162 | 20872.743
2020-08-05 22:00 | 5.528 | 5.8187 | 119.4719 | 1124.6784 | 16870.1754
2020-08-05 23:00 | 4.5977 | 4.8395 | 133.3829 | 617.2709 | 9259.063
2020-08-06 00:00 | 3.8368 | 4.0386 | 142.3819 | 311.5748 | 4673.622
2020-08-06 01:00 | 3.195 | 3.363 | 135.9048 | 125.6911 | 1885.3667
2020-08-06 02:00 | 2.7296 | 2.8732 | 118.8867 | 0 | 0
2020-08-06 03:00 | 2.4873 | 2.6181 | 101.3226 | 0 | 0
2020-08-06 04:00 | 2.3901 | 2.5158 | 89.688 | 0 | 0
2020-08-06 05:00 | 2.2588 | 2.3776 | 79.7882 | 0 | 0
2020-08-06 06:00 | 1.6981 | 1.7874 | 66.3728 | 0 | 0
2020-08-06 07:00 | 2.0353 | 2.1423 | 63.8998 | 0 | 0
2020-08-06 08:00 | 2.9141 | 3.0674 | 61.1194 | 62.4238 | 936.3576
2020-08-06 09:00 | 4.0958 | 4.3112 | 67.3072 | 407.5498 | 6113.2474
2020-08-06 10:00 | 4.5334 | 4.7718 | 68.4101 | 588.7015 | 8830.5228
2020-08-06 11:00 | 4.8357 | 5.09 | 63.8156 | 730.1919 | 10952.8791
2020-08-06 12:00 | 5.104 | 5.3724 | 61.8535 | 871.9687 | 13079.5312
2020-08-06 13:00 | 5.3847 | 5.6679 | 60.9459 | 1035.4075 | 15531.1121
2020-08-06 14:00 | 5.6435 | 5.9403 | 61.6604 | 1196.6531 | 17949.7964
2020-08-06 15:00 | 5.7953 | 6.1001 | 63.4162 | 1302.0644 | 19530.9654
2020-08-06 16:00 | 5.598 | 5.8924 | 65.6031 | 1168.2934 | 17524.4008
2020-08-06 17:00 | 5.602 | 5.8967 | 67.0963 | 1170.8291 | 17562.4368
2020-08-06 18:00 | 5.9062 | 6.2168 | 69.2332 | 1383.7796 | 20756.6944
2020-08-06 19:00 | 5.8043 | 6.1096 | 73.9523 | 1308.6855 | 19630.2824
2020-08-06 20:00 | 5.4486 | 5.7352 | 78.9317 | 1075.2341 | 16128.5121
2020-08-06 21:00 | 5.1838 | 5.4565 | 83.8907 | 914.1565 | 13712.348
2020-08-06 22:00 | 4.3519 | 4.5808 | 90.1728 | 508.1134 | 7621.7016
2020-08-06 23:00 | 4.0714 | 4.2855 | 82.6607 | 398.4897 | 5977.3453
2020-08-07 00:00 | 4.259 | 4.4831 | 68.8938 | 468.0342 | 7020.5123
2020-08-07 01:00 | 4.6297 | 4.8732 | 60.9948 | 631.4749 | 9472.1239
2020-08-07 02:00 | 4.7999 | 5.0524 | 57.8555 | 711.2969 | 10669.453
2020-08-07 03:00 | 4.7117 | 4.9595 | 57.4069 | 667.8933 | 10018.3999
2020-08-07 04:00 | 4.3588 | 4.5881 | 55.0669 | 511.16 | 7667.4007
2020-08-07 05:00 | 3.3549 | 3.5314 | 48.163 | 163.9796 | 2459.6945
2020-08-07 06:00 | 2.9757 | 3.1322 | 43.5998 | 76.2916 | 1144.3739
2020-08-07 07:00 | 3.4089 | 3.5882 | 44.1208 | 180.2154 | 2703.2307
2020-08-07 08:00 | 3.9608 | 4.1692 | 49.3992 | 357.5413 | 5363.1193
2020-08-07 09:00 | 4.7369 | 4.986 | 54.8261 | 679.1091 | 10186.6358
2020-08-07 10:00 | 3.8744 | 4.0782 | 58.297 | 325.5251 | 4882.8768
2020-08-07 11:00 | 4.1965 | 4.4172 | 52.2498 | 444.8423 | 6672.6346
2020-08-07 12:00 | 4.5106 | 4.7478 | 44.6558 | 578.5644 | 8678.4655
2020-08-07 13:00 | 4.9316 | 5.1909 | 39.2565 | 780.8553 | 11712.8297
2020-08-07 14:00 | 5.2581 | 5.5346 | 36.5524 | 956.4949 | 14347.4228
2020-08-07 15:00 | 5.4978 | 5.787 | 37.7707 | 1105.8782 | 16588.1729
2020-08-07 16:00 | 5.439 | 5.7251 | 41.3096 | 1069.2395 | 16038.5932
2020-08-07 17:00 | 5.5273 | 5.818 | 47.8989 | 1124.2657 | 16863.9851
2020-08-07 18:00 | 6.12 | 6.4419 | 51.0249 | 1541.3378 | 23120.0672
2020-08-07 19:00 | 6.8795 | 7.2413 | 52.2884 | 2212.8687 | 33193.0305
2020-08-07 20:00 | 7.6419 | 8.0438 | 52.4049 | 3032.2929 | 45484.3935
2020-08-07 21:00 | 7.955 | 8.3733 | 55.0023 | 3403.3796 | 51050.6943
2020-08-07 22:00 | 7.2242 | 7.6041 | 62.643 | 2564.1536 | 38462.3038
2020-08-07 23:00 | 6.8092 | 7.1673 | 63.4312 | 2143.9339 | 32159.0078
2020-08-08 00:00 | 6.3715 | 6.7066 | 62.0048 | 1749.7906 | 26246.8583
2020-08-08 01:00 | 5.8657 | 6.1742 | 58.8024 | 1353.9741 | 20309.611
2020-08-08 02:00 | 5.6499 | 5.9471 | 53.5365 | 1200.6682 | 18010.0231
2020-08-08 03:00 | 5.679 | 5.9777 | 48.2913 | 1218.8076 | 18282.114
2020-08-08 04:00 | 5.6192 | 5.9148 | 44.8074 | 1181.5381 | 17723.0711
2020-08-08 05:00 | 4.9521 | 5.2125 | 44.8787 | 791.6963 | 11875.4439
2020-08-08 06:00 | 4.6665 | 4.912 | 47.7382 | 647.844 | 9717.6598
2020-08-08 07:00 | 4.6738 | 4.9196 | 46.2141 | 651.081 | 9766.2154
2020-08-08 08:00 | 5.6401 | 5.9368 | 47.3661 | 1194.5594 | 17918.3907
2020-08-08 09:00 | 5.9739 | 6.2881 | 47.1352 | 1433.6905 | 21505.3575
2020-08-08 10:00 | 5.2562 | 5.5327 | 47.9888 | 955.3481 | 14330.2214
2020-08-08 11:00 | 5.7443 | 6.0464 | 42.8247 | 1264.5016 | 18967.5236
2020-08-08 12:00 | 6.2362 | 6.5642 | 38.2105 | 1634.1079 | 24511.6191
2020-08-08 13:00 | 6.8908 | 7.2533 | 36.4786 | 2224.031 | 33360.4646
2020-08-08 14:00 | 7.6128 | 8.0132 | 39.9306 | 2997.895 | 44968.4247
2020-08-08 15:00 | 7.9904 | 8.4107 | 48.2564 | 3445.4497 | 51681.7461
2020-08-08 16:00 | 7.3334 | 7.7191 | 54.4645 | 2685.8364 | 40287.5458
2020-08-08 17:00 | 5.9424 | 6.255 | 61.6102 | 1410.4908 | 21157.362
2020-08-08 18:00 | 5.2306 | 5.5057 | 66.854 | 939.387 | 14090.8052
2020-08-08 19:00 | 4.6911 | 4.9378 | 67.2679 | 658.7719 | 9881.5788
2020-08-08 20:00 | 3.9878 | 4.1976 | 64.269 | 367.5505 | 5513.2577
2020-08-08 21:00 | 3.2435 | 3.4141 | 55.2128 | 136.6133 | 2049.1997
2020-08-08 22:00 | 2.4161 | 2.5431 | 49.403 | 0 | 0
2020-08-08 23:00 | 2.0621 | 2.1705 | 33.5864 | 0 | 0
2020-08-09 00:00 | 2.1933 | 2.3086 | 18.8349 | 0 | 0
2020-08-09 01:00 | 2.5534 | 2.6877 | 14.7897 | 0 | 0
2020-08-09 02:00 | 2.6145 | 2.752 | 21.2124 | 0 | 0
2020-08-09 03:00 | 2.4582 | 2.5875 | 29.623 | 0 | 0
2020-08-09 04:00 | 2.1875 | 2.3025 | 35.4361 | 0 | 0
2020-08-09 05:00 | 1.7272 | 1.8181 | 31.8175 | 0 | 0
2020-08-09 06:00 | 1.9154 | 2.0161 | 34.4997 | 0 | 0
2020-08-09 07:00 | 2.6721 | 2.8127 | 38.4983 | 0 | 0
2020-08-09 08:00 | 3.5164 | 3.7013 | 37.7829 | 212.5791 | 3188.6864
2020-08-09 09:00 | 3.736 | 3.9325 | 39.2812 | 278.6826 | 4180.2388
2020-08-09 10:00 | 3.5087 | 3.6932 | 36.6457 | 210.2589 | 3153.8837
2020-08-09 11:00 | 3.8963 | 4.1012 | 36.4312 | 333.6286 | 5004.4286
2020-08-09 12:00 | 3.8956 | 4.1005 | 39.0475 | 333.3802 | 5000.7034
2020-08-09 13:00 | 4.0415 | 4.2541 | 39.4386 | 387.4385 | 5811.5775
2020-08-09 14:00 | 4.1429 | 4.3608 | 43.962 | 425.0043 | 6375.064
2020-08-09 15:00 | 4.2337 | 4.4564 | 50.559 | 458.6544 | 6879.8156
2020-08-09 16:00 | 3.9519 | 4.1597 | 61.5421 | 354.2187 | 5313.2807
2020-08-09 17:00 | 3.8955 | 4.1004 | 72.1122 | 333.3499 | 5000.2489
2020-08-09 18:00 | 3.9279 | 4.1344 | 79.5945 | 345.3256 | 5179.8846
2020-08-09 19:00 | 3.9009 | 4.1061 | 92.0679 | 335.3473 | 5030.2091
2020-08-09 20:00 | 3.5601 | 3.7473 | 100.4491 | 225.7326 | 3385.9895
2020-08-09 21:00 | 2.9955 | 3.153 | 98.4078 | 80.7444 | 1211.1655
2020-08-09 22:00 | 1.6355 | 1.7216 | 75.0692 | 0 | 0
2020-08-09 23:00 | 1.502 | 1.581 | 49.6317 | 0 | 0
2020-08-10 00:00 | 2.7524 | 2.8972 | 36.2009 | 0 | 0
2020-08-10 01:00 | 3.2932 | 3.4664 | 35.3974 | 147.8096 | 2217.1444
2020-08-10 02:00 | 3.7454 | 3.9424 | 38.9802 | 281.5208 | 4222.8126
2020-08-10 03:00 | 3.9389 | 4.1461 | 47.0095 | 349.4259 | 5241.3883
2020-08-10 04:00 | 2.9929 | 3.1503 | 47.3355 | 80.1732 | 1202.5973
2020-08-10 05:00 | 2.1287 | 2.2407 | 37.8661 | 0 | 0
2020-08-10 06:00 | 1.7471 | 1.839 | 37.1727 | 0 | 0
2020-08-10 07:00 | 2.1805 | 2.2952 | 21.1936 | 0 | 0
2020-08-10 08:00 | 2.6038 | 2.7407 | 16.2629 | 0 | 0
2020-08-10 09:00 | 2.8323 | 2.9813 | 20.8617 | 0 | 0
2020-08-10 10:00 | 2.3055 | 2.4268 | 12.3142 | 0 | 0
2020-08-10 11:00 | 2.8199 | 2.9682 | 9.9729 | 0 | 0
2020-08-10 12:00 | 2.9919 | 3.1492 | 16.1609 | 79.9378 | 1199.0668
2020-08-10 13:00 | 3.5935 | 3.7825 | 17.9429 | 235.8014 | 3537.0209
2020-08-10 14:00 | 4.0317 | 4.2437 | 16.1546 | 383.7894 | 5756.8414
2020-08-10 15:00 | 4.2716 | 4.4962 | 14.2744 | 472.6696 | 7090.0442
2020-08-10 16:00 | 2.261 | 2.3799 | 73.1691 | 0 | 0
2020-08-10 17:00 | 1.3955 | 1.4689 | 64.0595 | 0 | 0
2020-08-10 18:00 | 1.8423 | 1.9392 | 30.1832 | 0 | 0
2020-08-10 19:00 | 2.1642 | 2.278 | 9.6434 | 0 | 0
2020-08-10 20:00 | 2.8649 | 3.0156 | 12.6874 | 51.3384 | 770.0764
2020-08-10 21:00 | 3.1072 | 3.2706 | 13.1498 | 105.9099 | 1588.6491
2020-08-10 22:00 | 3.8857 | 4.0901 | 1.6645 | 329.7104 | 4945.6567
2020-08-10 23:00 | 3.3056 | 3.4795 | 356.7343 | 150.6037 | 2259.0562
2020-08-11 00:00 | 3.1568 | 3.3228 | 347.1231 | 117.0781 | 1756.1721
2020-08-11 01:00 | 3.5645 | 3.752 | 340.0645 | 227.0695 | 3406.0432
2020-08-11 02:00 | 4.493 | 4.7293 | 332.0723 | 570.7761 | 8561.6408
2020-08-11 03:00 | 4.835 | 5.0893 | 331.6582 | 729.8241 | 10947.3616
2020-08-11 04:00 | 4.4505 | 4.6845 | 335.1337 | 551.8751 | 8278.1262
2020-08-11 05:00 | 3.0284 | 3.1877 | 335.5245 | 88.1575 | 1322.3621
2020-08-11 06:00 | 2.6586 | 2.7984 | 338.371 | 0 | 0
2020-08-11 07:00 | 2.837 | 2.9862 | 341.8923 | 0 | 0
2020-08-11 08:00 | 3.3831 | 3.561 | 345.1183 | 172.4407 | 2586.6105
2020-08-11 09:00 | 3.4764 | 3.6592 | 342.6244 | 200.5332 | 3007.9973
2020-08-11 10:00 | 2.8024 | 2.9498 | 328.0109 | 0 | 0
2020-08-11 11:00 | 3.1278 | 3.2923 | 322.179 | 110.5587 | 1658.38
2020-08-11 12:00 | 3.4403 | 3.6212 | 315.3384 | 189.6718 | 2845.0772
2020-08-11 13:00 | 3.9707 | 4.1795 | 308.1978 | 361.1829 | 5417.744
2020-08-11 14:00 | 5.0343 | 5.2991 | 353.7041 | 835.1285 | 12526.9278
2020-08-11 15:00 | 4.4086 | 4.6404 | 348.3033 | 533.268 | 7999.0197
2020-08-11 16:00 | 4.168 | 4.3873 | 334.661 | 434.3167 | 6514.7499
2020-08-11 17:00 | 4.0518 | 4.2649 | 329.7802 | 391.2378 | 5868.5672
2020-08-11 18:00 | 4.3716 | 4.6015 | 338.4565 | 516.8478 | 7752.7165
2020-08-11 19:00 | 4.9988 | 5.2617 | 348.6617 | 816.3729 | 12245.5939
2020-08-11 20:00 | 5.4676 | 5.7552 | 356.8242 | 1087.0838 | 16306.2573
2020-08-11 21:00 | 5.4724 | 5.7602 | 3.6911 | 1090.0565 | 16350.8468
2020-08-11 22:00 | 6.2127 | 6.5395 | 8.52 | 1614.06 | 24210.9006
2020-08-11 23:00 | 6.1855 | 6.5109 | 12.6271 | 1590.8112 | 23862.1685
2020-08-12 00:00 | 6.3917 | 6.7278 | 14.7771 | 1766.9894 | 26504.8404
2020-08-12 01:00 | 6.2626 | 6.592 | 14.3217 | 1656.7194 | 24850.7916
2020-08-12 02:00 | 6.0672 | 6.3863 | 11.4652 | 1502.4251 | 22536.3765
2020-08-12 03:00 | 6.1565 | 6.4803 | 10.6894 | 1568.1982 | 23522.9734
2020-08-12 04:00 | 6.1098 | 6.4311 | 12.2663 | 1533.768 | 23006.5205
2020-08-12 05:00 | 5.9428 | 6.2554 | 14.9103 | 1410.7758 | 21161.6369
2020-08-12 06:00 | 5.5232 | 5.8137 | 14.6771 | 1121.7331 | 16825.9965
2020-08-12 07:00 | 5.6407 | 5.9374 | 10.3769 | 1194.9362 | 17924.0436
2020-08-12 08:00 | 5.9855 | 6.3003 | 4.4734 | 1442.2162 | 21633.243
2020-08-12 09:00 | 6.2812 | 6.6116 | 3.7295 | 1672.5982 | 25088.9734
2020-08-12 10:00 | 5.9734 | 6.2876 | 4.5911 | 1433.2909 | 21499.3632
2020-08-12 11:00 | 6.0363 | 6.3538 | 0.75982 | 1479.6756 | 22195.1344
2020-08-12 12:00 | 6.3687 | 6.7036 | 357.9721 | 1747.3358 | 26210.0375
2020-08-12 13:00 | 7.0942 | 7.4673 | 357.2989 | 2423.495 | 36352.4254
2020-08-12 14:00 | 7.6424 | 8.0443 | 358.5602 | 3032.9157 | 45493.7361
2020-08-12 15:00 | 7.5162 | 7.9115 | 4.1334 | 2889.406 | 43341.0901
2020-08-12 16:00 | 7.0184 | 7.3875 | 8.2727 | 2349.1523 | 35237.2838
2020-08-12 17:00 | 5.6949 | 5.9945 | 11.7375 | 1228.7178 | 18430.7663
2020-08-12 18:00 | 4.5477 | 4.7868 | 15.3545 | 595.0452 | 8925.6775
2020-08-12 19:00 | 4.0756 | 4.2899 | 16.2587 | 400.0488 | 6000.7327
2020-08-12 20:00 | 3.8764 | 4.0803 | 16.8779 | 326.2698 | 4894.0476
2020-08-12 21:00 | 3.6162 | 3.8064 | 17.1716 | 242.6413 | 3639.6189
2020-08-12 22:00 | 3.2145 | 3.3835 | 2.931 | 130.0731 | 1951.0963
2020-08-12 23:00 | 2.9629 | 3.1188 | 351.007 | 73.4169 | 1101.2536
2020-08-13 00:00 | 2.9528 | 3.1081 | 341.5555 | 71.1411 | 1067.1163
2020-08-13 01:00 | 3.4176 | 3.5974 | 341.1359 | 182.8429 | 2742.6439
2020-08-13 02:00 | 3.7259 | 3.9218 | 341.25 | 275.6481 | 4134.7212
2020-08-13 03:00 | 3.8826 | 4.0868 | 336.6554 | 328.5596 | 4928.3943
2020-08-13 04:00 | 3.6732 | 3.8664 | 335.1767 | 259.7962 | 3896.9426
2020-08-13 05:00 | 3.3046 | 3.4784 | 335.5995 | 150.3703 | 2255.5548
2020-08-13 06:00 | 3.6061 | 3.7957 | 337.3545 | 239.5805 | 3593.7081
2020-08-13 07:00 | 4.3078 | 4.5344 | 340.9211 | 488.5091 | 7327.6362
2020-08-13 08:00 | 5.2608 | 5.5375 | 342.2795 | 958.2019 | 14373.0278
2020-08-13 09:00 | 5.391 | 5.6746 | 344.8173 | 1039.339 | 15590.0844
2020-08-13 10:00 | 4.1909 | 4.4114 | 349.0827 | 442.796 | 6641.9402
2020-08-13 11:00 | 4.1831 | 4.4031 | 335.7121 | 439.8924 | 6598.3857
2020-08-13 12:00 | 4.6542 | 4.899 | 330.024 | 642.357 | 9635.3549
2020-08-13 13:00 | 4.8987 | 5.1563 | 332.822 | 763.4605 | 11451.9072
2020-08-13 14:00 | 5.2642 | 5.5411 | 331.594 | 960.3373 | 14405.059
2020-08-13 15:00 | 5.3959 | 5.6797 | 331.3154 | 1042.358 | 15635.3697
2020-08-13 16:00 | 4.9687 | 5.23 | 335.3663 | 800.476 | 12007.1397
2020-08-13 17:00 | 4.1439 | 4.3618 | 356.2812 | 425.3655 | 6380.4824
2020-08-13 18:00 | 4.6597 | 4.9048 | 27.3311 | 644.8055 | 9672.0822
2020-08-13 19:00 | 5.0504 | 5.3161 | 47.576 | 843.6687 | 12655.0308
2020-08-13 20:00 | 4.8043 | 5.057 | 54.1517 | 713.5948 | 10703.9222
2020-08-13 21:00 | 4.3174 | 4.5445 | 52.3584 | 492.7844 | 7391.7663
2020-08-13 22:00 | 3.6381 | 3.8295 | 49.2427 | 249.2342 | 3738.5126
2020-08-13 23:00 | 3.0082 | 3.1664 | 45.1595 | 83.6065 | 1254.0973
2020-08-14 00:00 | 3.0408 | 3.2007 | 39.0358 | 90.9572 | 1364.3577
2020-08-14 01:00 | 3.2618 | 3.4334 | 37.0036 | 140.7488 | 2111.2315
2020-08-14 02:00 | 3.5134 | 3.6981 | 38.3978 | 211.6677 | 3175.0162
2020-08-14 03:00 | 3.902 | 4.1072 | 39.9931 | 335.7437 | 5036.1561
2020-08-14 04:00 | 4.0009 | 4.2113 | 42.0943 | 372.3816 | 5585.7233
2020-08-14 05:00 | 2.9598 | 3.1155 | 45.0647 | 72.7112 | 1090.6677
2020-08-14 06:00 | 2.6978 | 2.8397 | 44.5158 | 0 | 0
2020-08-14 07:00 | 3.0819 | 3.244 | 40.3806 | 100.2081 | 1503.1208
2020-08-14 08:00 | 3.8767 | 4.0806 | 34.9583 | 326.3575 | 4895.3627
2020-08-14 09:00 | 4.1983 | 4.4191 | 29.343 | 445.5076 | 6682.6134
2020-08-14 10:00 | 3.4415 | 3.6225 | 28.6842 | 190.0452 | 2850.6777
2020-08-14 11:00 | 3.3476 | 3.5237 | 29.6535 | 161.7753 | 2426.6298
2020-08-14 12:00 | 3.1482 | 3.3138 | 31.3262 | 115.1477 | 1727.2158
2020-08-14 13:00 | 2.9146 | 3.0679 | 31.9194 | 62.5376 | 938.0637
2020-08-14 14:00 | 2.7487 | 2.8933 | 37.5285 | 0 | 0
2020-08-14 15:00 | 2.756 | 2.901 | 41.3294 | 0 | 0
2020-08-14 16:00 | 2.8902 | 3.0422 | 42.0962 | 57.0247 | 855.3712
2020-08-14 17:00 | 3.8368 | 4.0385 | 47.5807 | 311.5684 | 4673.5253
2020-08-14 18:00 | 5.6513 | 5.9485 | 66.3949 | 1201.5272 | 18022.9074
2020-08-14 19:00 | 6.3611 | 6.6957 | 82.4427 | 1740.8757 | 26113.1361
2020-08-14 20:00 | 6.4033 | 6.7401 | 93.2172 | 1776.9274 | 26653.9109
2020-08-14 21:00 | 5.9598 | 6.2732 | 100.6115 | 1423.2563 | 21348.845
2020-08-14 22:00 | 4.9079 | 5.166 | 116.167 | 768.3509 | 11525.2629
2020-08-14 23:00 | 4.3561 | 4.5852 | 127.3182 | 509.9505 | 7649.2581
2020-08-15 00:00 | 4.1232 | 4.34 | 135.863 | 417.6898 | 6265.3475
2020-08-15 01:00 | 3.7699 | 3.9681 | 142.9088 | 288.885 | 4333.2756
2020-08-15 02:00 | 3.5547 | 3.7416 | 142.7282 | 224.111 | 3361.6656
2020-08-15 03:00 | 3.5313 | 3.717 | 140.4216 | 217.0618 | 3255.9273
2020-08-15 04:00 | 3.5424 | 3.7288 | 135.0831 | 220.4243 | 3306.3649
2020-08-15 05:00 | 3.2384 | 3.4087 | 120.7724 | 135.4593 | 2031.8894
2020-08-15 06:00 | 3.0142 | 3.1728 | 114.0708 | 84.9716 | 1274.5744
2020-08-15 07:00 | 3.2759 | 3.4481 | 114.5176 | 143.9036 | 2158.5534
2020-08-15 08:00 | 3.5569 | 3.744 | 110.0485 | 224.7787 | 3371.6812
2020-08-15 09:00 | 3.2693 | 3.4412 | 108.7978 | 142.4172 | 2136.2574
2020-08-15 10:00 | 3.2522 | 3.4233 | 103.3707 | 138.5787 | 2078.6807
2020-08-15 11:00 | 3.2278 | 3.3976 | 96.3108 | 133.0885 | 1996.3277
2020-08-15 12:00 | 3.4069 | 3.5861 | 94.9519 | 179.6329 | 2694.4932
2020-08-15 13:00 | 3.5227 | 3.7079 | 93.557 | 214.472 | 3217.0801
2020-08-15 14:00 | 3.3492 | 3.5253 | 92.1669 | 162.2491 | 2433.7358
2020-08-15 15:00 | 3.5897 | 3.7785 | 88.7883 | 234.6508 | 3519.7623
2020-08-15 16:00 | 3.8545 | 4.0572 | 89.5275 | 318.1327 | 4771.9899
2020-08-15 17:00 | 4.17 | 4.3894 | 86.7765 | 435.0533 | 6525.8
2020-08-15 18:00 | 4.9456 | 5.2057 | 86.4502 | 788.2676 | 11824.0141
2020-08-15 19:00 | 5.2797 | 5.5574 | 87.5507 | 969.9968 | 14549.9516
2020-08-15 20:00 | 5.2647 | 5.5416 | 91.1399 | 960.6518 | 14409.7766
2020-08-15 21:00 | 5.3221 | 5.6021 | 97.2314 | 996.4227 | 14946.3402
2020-08-15 22:00 | 3.9535 | 4.1614 | 100.5595 | 354.8142 | 5322.2124
2020-08-15 23:00 | 3.4606 | 3.6426 | 119.2838 | 195.7847 | 2936.7705
2020-08-16 00:00 | 3.1641 | 3.3306 | 135.4724 | 118.7378 | 1781.0675
2020-08-16 01:00 | 2.6422 | 2.7812 | 141.6611 | 0 | 0
2020-08-16 02:00 | 2.1571 | 2.2706 | 144.4755 | 0 | 0
2020-08-16 03:00 | 1.6696 | 1.7574 | 138.8039 | 0 | 0
2020-08-16 04:00 | 1.0972 | 1.1549 | 117.3412 | 0 | 0
2020-08-16 05:00 | 0.619 | 0.65156 | 87.3056 | 0 | 0
2020-08-16 06:00 | 0.32097 | 0.33785 | 17.459 | 0 | 0
2020-08-16 07:00 | 0.59403 | 0.62528 | 39.0135 | 0 | 0
2020-08-16 08:00 | 1.1786 | 1.2405 | 64.633 | 0 | 0
2020-08-16 09:00 | 1.2039 | 1.2672 | 73.0274 | 0 | 0
2020-08-16 10:00 | 1.0196 | 1.0732 | 51.8908 | 0 | 0
2020-08-16 11:00 | 1.0853 | 1.1424 | 47.9679 | 0 | 0
2020-08-16 12:00 | 1.1712 | 1.2328 | 48.4721 | 0 | 0
2020-08-16 13:00 | 1.3696 | 1.4416 | 49.3297 | 0 | 0
2020-08-16 14:00 | 1.3841 | 1.4569 | 51.6672 | 0 | 0
2020-08-16 15:00 | 1.4312 | 1.5065 | 50.4694 | 0 | 0
2020-08-16 16:00 | 1.1803 | 1.2424 | 56.8642 | 0 | 0
2020-08-16 17:00 | 0.62032 | 0.65294 | 87.0672 | 0 | 0
2020-08-16 18:00 | 0.88166 | 0.92803 | 176.9622 | 0 | 0
2020-08-16 19:00 | 1.7678 | 1.8608 | 207.703 | 0 | 0
2020-08-16 20:00 | 2.649 | 2.7884 | 225.3484 | 0 | 0
2020-08-16 21:00 | 2.9577 | 3.1132 | 240.4558 | 72.2277 | 1083.4157
2020-08-16 22:00 | 2.7839 | 2.9304 | 268.5543 | 0 | 0
2020-08-16 23:00 | 2.8826 | 3.0342 | 280.3076 | 55.32 | 829.7998
2020-08-17 00:00 | 2.5263 | 2.6592 | 289.8499 | 0 | 0
2020-08-17 01:00 | 2.3496 | 2.4732 | 295.3943 | 0 | 0
2020-08-17 02:00 | 2.2489 | 2.3672 | 295.5356 | 0 | 0
2020-08-17 03:00 | 2.2104 | 2.3266 | 288.1774 | 0 | 0
2020-08-17 04:00 | 2.3225 | 2.4446 | 276.0535 | 0 | 0
2020-08-17 05:00 | 2.2962 | 2.4169 | 267.8006 | 0 | 0
2020-08-17 06:00 | 1.2541 | 1.3201 | 259.7068 | 0 | 0
2020-08-17 07:00 | 0.52661 | 0.55431 | 234.0914 | 0 | 0
2020-08-17 08:00 | 0.87952 | 0.92578 | 189.8526 | 0 | 0
2020-08-17 09:00 | 1.6711 | 1.759 | 181.7613 | 0 | 0
2020-08-17 10:00 | 2.5998 | 2.7365 | 183.8487 | 0 | 0
2020-08-17 11:00 | 2.5852 | 2.7212 | 186.8111 | 0 | 0
2020-08-17 12:00 | 2.5895 | 2.7257 | 192.1864 | 0 | 0
2020-08-17 13:00 | 2.5104 | 2.6425 | 198.22 | 0 | 0
2020-08-17 14:00 | 2.5046 | 2.6363 | 208.917 | 0 | 0
2020-08-17 15:00 | 2.0664 | 2.1751 | 216.6149 | 0 | 0
2020-08-17 16:00 | 1.5943 | 1.6781 | 204.2864 | 0 | 0
2020-08-17 17:00 | 1.5604 | 1.6425 | 172.8605 | 0 | 0
2020-08-17 18:00 | 2.2755 | 2.3952 | 143.7588 | 0 | 0
2020-08-17 19:00 | 3.2278 | 3.3976 | 144.4668 | 133.0853 | 1996.2796
2020-08-17 20:00 | 4.3829 | 4.6134 | 151.3721 | 521.8472 | 7827.7079
2020-08-17 21:00 | 5.1666 | 5.4384 | 163.8283 | 905.0581 | 13575.8714
2020-08-17 22:00 | 5.2368 | 5.5122 | 172.7961 | 943.2215 | 14148.3226
2020-08-17 23:00 | 5.2542 | 5.5306 | 185.1408 | 954.1082 | 14311.6229
2020-08-18 00:00 | 5.2427 | 5.5184 | 190.1541 | 946.8851 | 14203.2766
2020-08-18 01:00 | 5.2952 | 5.5737 | 191.5704 | 979.607 | 14694.105
2020-08-18 02:00 | 5.4473 | 5.7338 | 196.239 | 1074.385 | 16115.7744
2020-08-18 03:00 | 5.7481 | 6.0504 | 200.4298 | 1267.2732 | 19009.0985
2020-08-18 04:00 | 5.7536 | 6.0562 | 197.839 | 1271.3351 | 19070.0259
2020-08-18 05:00 | 5.2295 | 5.5046 | 198.8153 | 938.7032 | 14080.5474
2020-08-18 06:00 | 3.9417 | 4.149 | 201.0407 | 350.4537 | 5256.8054
2020-08-18 07:00 | 3.3414 | 3.5171 | 198.2643 | 159.9023 | 2398.5338
2020-08-18 08:00 | 3.2437 | 3.4143 | 197.2591 | 136.6521 | 2049.782
2020-08-18 09:00 | 3.7384 | 3.935 | 205.9456 | 279.4194 | 4191.2914
2020-08-18 10:00 | 3.9512 | 4.1591 | 208.272 | 353.986 | 5309.7894
2020-08-18 11:00 | 4.2441 | 4.4673 | 195.6742 | 462.5058 | 6937.5863
2020-08-18 12:00 | 4.4649 | 4.6997 | 188.6981 | 558.2903 | 8374.3551
2020-08-18 13:00 | 4.3867 | 4.6174 | 189.4444 | 523.5503 | 7853.2538
2020-08-18 14:00 | 4.5162 | 4.7537 | 185.5931 | 581.0553 | 8715.8293
2020-08-18 15:00 | 4.3853 | 4.616 | 184.321 | 522.9477 | 7844.215
2020-08-18 16:00 | 3.9709 | 4.1797 | 186.8273 | 361.268 | 5419.0205
2020-08-18 17:00 | 4.5098 | 4.747 | 188.303 | 578.221 | 8673.3145
2020-08-18 18:00 | 5.0919 | 5.3597 | 192.4475 | 865.5829 | 12983.7434
2020-08-18 19:00 | 5.5532 | 5.8453 | 196.5617 | 1140.4079 | 17106.1192
2020-08-18 20:00 | 5.8898 | 6.1995 | 195.8988 | 1371.6702 | 20575.0535
2020-08-18 21:00 | 6.2614 | 6.5908 | 193.3728 | 1655.7025 | 24835.5375
2020-08-18 22:00 | 6.2088 | 6.5353 | 189.0936 | 1610.6795 | 24160.1928
2020-08-18 23:00 | 6.499 | 6.8409 | 193.011 | 1858.7818 | 27881.7267
2020-08-19 00:00 | 6.8236 | 7.1825 | 196.3871 | 2158.1165 | 32371.748
2020-08-19 01:00 | 7.0929 | 7.4659 | 195.6146 | 2422.2184 | 36333.2759
2020-08-19 02:00 | 7.2684 | 7.6507 | 202.1942 | 2613.3955 | 39200.9322
2020-08-19 03:00 | 7.0403 | 7.4106 | 208.3222 | 2370.6412 | 35559.618
2020-08-19 04:00 | 6.4247 | 6.7626 | 209.7639 | 1795.2552 | 26928.8275
2020-08-19 05:00 | 5.6271 | 5.9231 | 211.2913 | 1186.4659 | 17796.9882
2020-08-19 06:00 | 4.1035 | 4.3193 | 208.7565 | 410.4084 | 6156.1255
2020-08-19 07:00 | 3.4856 | 3.6689 | 205.0769 | 203.3166 | 3049.7495
2020-08-19 08:00 | 3.4197 | 3.5995 | 195.2978 | 183.4708 | 2752.0617
2020-08-19 09:00 | 4.0824 | 4.2971 | 188.5442 | 402.5903 | 6038.8545
2020-08-19 10:00 | 5.1473 | 5.4181 | 188.2366 | 894.8717 | 13423.0754
2020-08-19 11:00 | 4.7864 | 5.0382 | 184.2766 | 704.169 | 10562.5355
2020-08-19 12:00 | 4.5388 | 4.7776 | 179.7465 | 591.133 | 8866.995
2020-08-19 13:00 | 4.2313 | 4.4539 | 176.8748 | 457.7582 | 6866.3733
2020-08-19 14:00 | 4.0457 | 4.2584 | 168.4556 | 388.9728 | 5834.5923
2020-08-19 15:00 | 4.3186 | 4.5457 | 160.4608 | 493.3056 | 7399.5841
2020-08-19 16:00 | 4.3834 | 4.6139 | 158.3365 | 522.0771 | 7831.1562
2020-08-19 17:00 | 4.5129 | 4.7502 | 159.4935 | 579.5925 | 8693.888
2020-08-19 18:00 | 4.8943 | 5.1517 | 163.3028 | 761.1449 | 11417.1735
2020-08-19 19:00 | 4.9602 | 5.221 | 168.7304 | 795.9592 | 11939.3887
2020-08-19 20:00 | 4.9142 | 5.1727 | 175.9546 | 771.6788 | 11575.1813
2020-08-19 21:00 | 4.8522 | 5.1074 | 175.9366 | 738.9111 | 11083.6666
2020-08-19 22:00 | 3.6791 | 3.8726 | 174.1661 | 261.5698 | 3923.5464
2020-08-19 23:00 | 3.5982 | 3.7875 | 180.8735 | 237.2222 | 3558.3335
2020-08-20 00:00 | 3.2278 | 3.3976 | 197.1317 | 133.0887 | 1996.33
2020-08-20 01:00 | 2.7665 | 2.912 | 221.4667 | 0 | 0
2020-08-20 02:00 | 2.2043 | 2.3203 | 258.7655 | 0 | 0
2020-08-20 03:00 | 2.2739 | 2.3935 | 294.2553 | 0 | 0
2020-08-20 04:00 | 2.6229 | 2.7609 | 321.8585 | 0 | 0
2020-08-20 05:00 | 3.0689 | 3.2303 | 344.3326 | 97.2757 | 1459.1357
2020-08-20 06:00 | 2.6413 | 2.7802 | 354.1397 | 0 | 0
2020-08-20 07:00 | 1.8645 | 1.9626 | 359.0941 | 0 | 0
2020-08-20 08:00 | 1.8187 | 1.9143 | 357.588 | 0 | 0
2020-08-20 09:00 | 1.9581 | 2.0611 | 354.7958 | 0 | 0
2020-08-20 10:00 | 3.0679 | 3.2293 | 345.912 | 97.0617 | 1455.9261
2020-08-20 11:00 | 2.7244 | 2.8677 | 346.2529 | 0 | 0
2020-08-20 12:00 | 3.0413 | 3.2013 | 334.8517 | 91.0736 | 1366.1047
2020-08-20 13:00 | 3.8562 | 4.059 | 331.8613 | 318.7765 | 4781.6469
2020-08-20 14:00 | 4.5878 | 4.8291 | 333.5744 | 612.86 | 9192.9002
2020-08-20 15:00 | 5.562 | 5.8545 | 336.8873 | 1145.8666 | 17187.9996
2020-08-20 16:00 | 7.0269 | 7.3965 | 326.6132 | 2357.5129 | 35362.6936
2020-08-20 17:00 | 8.0172 | 8.4388 | 329.7457 | 3477.1054 | 52156.5804
2020-08-20 18:00 | 8.0349 | 8.4575 | 331.6277 | 3498.1345 | 52472.0178
2020-08-20 19:00 | 7.5897 | 7.9889 | 333.8815 | 2971.2683 | 44569.0244
2020-08-20 20:00 | 6.9635 | 7.3297 | 336.0884 | 2295.2951 | 34429.426
2020-08-20 21:00 | 6.4166 | 6.754 | 336.0506 | 1788.2777 | 26824.1651
2020-08-20 22:00 | 6.2351 | 6.5631 | 329.431 | 1633.2129 | 24498.1938
2020-08-20 23:00 | 6.4748 | 6.8153 | 324.2778 | 1838.0145 | 27570.2175
2020-08-21 00:00 | 7.2553 | 7.6368 | 323.0131 | 2598.7756 | 38981.6339
2020-08-21 01:00 | 7.1632 | 7.5399 | 327.11 | 2496.2252 | 37443.3773
2020-08-21 02:00 | 6.8657 | 7.2268 | 327.1703 | 2199.3568 | 32990.3524
2020-08-21 03:00 | 6.349 | 6.6829 | 326.3732 | 1730.5194 | 25957.7904
2020-08-21 04:00 | 5.561 | 5.8535 | 321.2102 | 1145.2488 | 17178.7317
2020-08-21 05:00 | 5.525 | 5.8155 | 320.5835 | 1122.7997 | 16841.9955
2020-08-21 06:00 | 5.2269 | 5.5018 | 316.3654 | 937.0529 | 14055.7935
2020-08-21 07:00 | 5.5111 | 5.801 | 310.9869 | 1114.1662 | 16712.493
2020-08-21 08:00 | 5.4979 | 5.7871 | 312.3057 | 1105.9562 | 16589.3425
2020-08-21 09:00 | 4.9418 | 5.2017 | 310.2748 | 786.2667 | 11794.001
2020-08-21 10:00 | 4.2895 | 4.5151 | 312.0054 | 480.3591 | 7205.3871
2020-08-21 11:00 | 4.5847 | 4.8258 | 306.5223 | 611.4871 | 9172.3072
2020-08-21 12:00 | 5.4578 | 5.7449 | 306.3661 | 1080.9654 | 16214.4804
2020-08-21 13:00 | 5.8928 | 6.2028 | 311.1904 | 1373.9416 | 20609.1246
2020-08-21 14:00 | 6.3029 | 6.6344 | 313.8673 | 1691.1261 | 25366.8915
2020-08-21 15:00 | 6.5805 | 6.9266 | 321.4257 | 1928.4186 | 28926.2785
2020-08-21 16:00 | 6.6507 | 7.0005 | 329.7356 | 1988.4346 | 29826.5184
2020-08-21 17:00 | 6.2486 | 6.5772 | 337.8103 | 1644.6879 | 24670.3178
2020-08-21 18:00 | 5.8673 | 6.1758 | 346.9259 | 1355.0877 | 20326.316
2020-08-21 19:00 | 5.4246 | 5.7099 | 353.7171 | 1060.261 | 15903.9152
2020-08-21 20:00 | 5.1637 | 5.4353 | 355.4358 | 903.5031 | 13552.5469
2020-08-21 21:00 | 5.0308 | 5.2954 | 356.8671 | 833.3135 | 12499.7024
2020-08-21 22:00 | 5.1754 | 5.4476 | 10.6607 | 909.688 | 13645.3194
2020-08-21 23:00 | 5.0182 | 5.2822 | 8.5581 | 826.655 | 12399.8246
2020-08-22 00:00 | 4.5449 | 4.7839 | 9.5872 | 593.8045 | 8907.0675
2020-08-22 01:00 | 3.9207 | 4.1269 | 9.5637 | 342.6612 | 5139.9177
2020-08-22 02:00 | 4.0864 | 4.3014 | 7.068 | 404.0814 | 6061.2209
2020-08-22 03:00 | 4.5342 | 4.7727 | 9.9396 | 589.0749 | 8836.1228
2020-08-22 04:00 | 4.6465 | 4.8909 | 19.6732 | 638.9521 | 9584.2811
2020-08-22 05:00 | 3.7978 | 3.9976 | 32.3094 | 297.2994 | 4459.4904
2020-08-22 06:00 | 3.7749 | 3.9735 | 35.7183 | 290.4162 | 4356.2423
2020-08-22 07:00 | 4.1425 | 4.3604 | 28.7131 | 424.8549 | 6372.8231
2020-08-22 08:00 | 4.3263 | 4.5539 | 26.5533 | 496.7394 | 7451.0909
2020-08-22 09:00 | 4.2212 | 4.4433 | 24.9709 | 454.0242 | 6810.3635
2020-08-22 10:00 | 3.3069 | 3.4808 | 43.218 | 150.9001 | 2263.5017
2020-08-22 11:00 | 3.2482 | 3.419 | 39.2441 | 137.6703 | 2065.055
2020-08-22 12:00 | 3.3646 | 3.5415 | 37.4206 | 166.8731 | 2503.0961
2020-08-22 13:00 | 3.6301 | 3.821 | 45.6633 | 246.803 | 3702.0448
2020-08-22 14:00 | 3.7834 | 3.9824 | 62.161 | 292.9676 | 4394.5136
2020-08-22 15:00 | 4.1803 | 4.4001 | 73.965 | 438.844 | 6582.66
2020-08-22 16:00 | 4.7375 | 4.9866 | 81.3332 | 679.3561 | 10190.3416
2020-08-22 17:00 | 5.4916 | 5.7804 | 88.2315 | 1101.9941 | 16529.9109
2020-08-22 18:00 | 6.0447 | 6.3626 | 96.6418 | 1485.8355 | 22287.5319
2020-08-22 19:00 | 6.2097 | 6.5363 | 106.5735 | 1611.4363 | 24171.5438
2020-08-22 20:00 | 6.1963 | 6.5222 | 118.8929 | 1600.0387 | 24000.5803
2020-08-22 21:00 | 6.1558 | 6.4796 | 132.2235 | 1567.7054 | 23515.5804
2020-08-22 22:00 | 5.8096 | 6.1152 | 140.796 | 1312.6384 | 19689.5767
2020-08-22 23:00 | 5.6628 | 5.9606 | 151.6072 | 1208.6853 | 18130.279
2020-08-23 00:00 | 5.3306 | 5.611 | 160.5138 | 1001.6867 | 15025.2999
2020-08-23 01:00 | 5.139 | 5.4093 | 165.8644 | 890.471 | 13357.0645
2020-08-23 02:00 | 5.0111 | 5.2747 | 165.96 | 822.9039 | 12343.5578
2020-08-23 03:00 | 5.3883 | 5.6717 | 160.501 | 1037.6557 | 15564.8349
2020-08-23 04:00 | 5.546 | 5.8377 | 159.0745 | 1135.906 | 17038.5893
2020-08-23 05:00 | 4.4761 | 4.7116 | 164.0247 | 563.2762 | 8449.1431
2020-08-23 06:00 | 4.194 | 4.4146 | 168.4827 | 443.9239 | 6658.8583
2020-08-23 07:00 | 3.954 | 4.1619 | 169.6363 | 354.9992 | 5324.9876
2020-08-23 08:00 | 3.9249 | 4.1314 | 168.0162 | 344.2426 | 5163.6387
2020-08-23 09:00 | 3.8476 | 4.0499 | 167.8986 | 315.57 | 4733.5502
2020-08-23 10:00 | 3.9762 | 4.1853 | 168.6819 | 363.226 | 5448.3899
2020-08-23 11:00 | 3.5543 | 3.7412 | 176.7026 | 223.9802 | 3359.7027
2020-08-23 12:00 | 3.2001 | 3.3684 | 184.0503 | 126.8292 | 1902.4373
2020-08-23 13:00 | 2.8605 | 3.011 | 191.2687 | 50.3472 | 755.2086
2020-08-23 14:00 | 2.571 | 2.7062 | 200.738 | 0 | 0
2020-08-23 15:00 | 2.4993 | 2.6308 | 193.6355 | 0 | 0
2020-08-23 16:00 | 2.8737 | 3.0248 | 169.8678 | 53.3136 | 799.704
2020-08-23 17:00 | 4.408 | 4.6398 | 157.7952 | 533.0121 | 7995.1813
2020-08-23 18:00 | 5.9026 | 6.2131 | 155.6729 | 1381.1634 | 20717.4504
2020-08-23 19:00 | 6.7594 | 7.1149 | 161.4911 | 2095.1023 | 31426.5339
2020-08-23 20:00 | 7.3165 | 7.7013 | 167.1992 | 2667.0198 | 40005.2969
2020-08-23 21:00 | 7.6738 | 8.0774 | 176.8659 | 3070.136 | 46052.0404
2020-08-23 22:00 | 6.4494 | 6.7886 | 194.5413 | 1816.3791 | 27245.6861
2020-08-23 23:00 | 6.2325 | 6.5603 | 205.0802 | 1630.9703 | 24464.5552
2020-08-24 00:00 | 6.017 | 6.3334 | 218.8391 | 1465.4139 | 21981.2085
2020-08-24 01:00 | 5.5881 | 5.882 | 237.4435 | 1162.1232 | 17431.8483
2020-08-24 02:00 | 5.0562 | 5.3222 | 258.506 | 846.7351 | 12701.0261
2020-08-24 03:00 | 3.9451 | 4.1526 | 267.5398 | 351.702 | 5275.5304
2020-08-24 04:00 | 2.5365 | 2.6699 | 266.326 | 0 | 0
2020-08-24 05:00 | 1.7665 | 1.8594 | 244.7646 | 0 | 0
2020-08-24 06:00 | 1.6791 | 1.7674 | 224.1355 | 0 | 0
2020-08-24 07:00 | 1.9344 | 2.0361 | 223.14 | 0 | 0
2020-08-24 08:00 | 1.9062 | 2.0065 | 218.6185 | 0 | 0
2020-08-24 09:00 | 2.564 | 2.6988 | 225.7786 | 0 | 0
2020-08-24 10:00 | 3.1234 | 3.2877 | 215.2257 | 109.5634 | 1643.4514
2020-08-24 11:00 | 2.6643 | 2.8044 | 239.6206 | 0 | 0
2020-08-24 12:00 | 2.7133 | 2.856 | 265.9842 | 0 | 0
2020-08-24 13:00 | 3.0566 | 3.2173 | 283.5384 | 94.5041 | 1417.5609
2020-08-24 14:00 | 2.5713 | 2.7065 | 297.0483 | 0 | 0
2020-08-24 15:00 | 1.9356 | 2.0374 | 299.2289 | 0 | 0
2020-08-24 16:00 | 1.5873 | 1.6707 | 310.6071 | 0 | 0
2020-08-24 17:00 | 1.524 | 1.6042 | 321.0374 | 0 | 0
2020-08-24 18:00 | 1.3772 | 1.4496 | 324.9187 | 0 | 0
2020-08-24 19:00 | 1.3001 | 1.3685 | 330.0405 | 0 | 0
2020-08-24 20:00 | 0.56859 | 0.59849 | 342.9174 | 0 | 0
2020-08-24 21:00 | 0.34458 | 0.3627 | 15.3108 | 0 | 0
2020-08-24 22:00 | 0.41574 | 0.4376 | 348.6072 | 0 | 0
2020-08-24 23:00 | 0.30765 | 0.32383 | 7.8765 | 0 | 0
2020-08-25 00:00 | 0.12257 | 0.12902 | 173.3518 | 0 | 0
2020-08-25 01:00 | 0.39814 | 0.41908 | 119.597 | 0 | 0
2020-08-25 02:00 | 0.68117 | 0.717 | 103.3676 | 0 | 0
2020-08-25 03:00 | 0.63572 | 0.66915 | 87.7055 | 0 | 0
2020-08-25 04:00 | 0.60687 | 0.63879 | 68.3412 | 0 | 0
2020-08-25 05:00 | 0.83632 | 0.8803 | 103.0243 | 0 | 0
2020-08-25 06:00 | 1.377 | 1.4494 | 143.5325 | 0 | 0
2020-08-25 07:00 | 1.9875 | 2.092 | 151.6897 | 0 | 0
2020-08-25 08:00 | 2.4755 | 2.6057 | 164.028 | 0 | 0
2020-08-25 09:00 | 1.9945 | 2.0994 | 172.144 | 0 | 0
2020-08-25 10:00 | 2.8913 | 3.0434 | 150.866 | 57.2792 | 859.1885
2020-08-25 11:00 | 4.2498 | 4.4733 | 149.9249 | 464.6126 | 6969.1895
2020-08-25 12:00 | 4.8315 | 5.0857 | 160.0926 | 727.9994 | 10919.991
2020-08-25 13:00 | 4.6906 | 4.9374 | 172.3425 | 658.5622 | 9878.4326
2020-08-25 14:00 | 4.183 | 4.403 | 175.5903 | 439.8597 | 6597.8959
2020-08-25 15:00 | 4.2561 | 4.48 | 209.6902 | 466.9546 | 7004.319
2020-08-25 16:00 | 6.6779 | 7.0291 | 255.2062 | 2015.1341 | 30227.0109
2020-08-25 17:00 | 6.379 | 6.7145 | 289.2381 | 1756.1486 | 26342.2291
2020-08-25 18:00 | 5.777 | 6.0808 | 303.427 | 1288.5542 | 19328.3129
2020-08-25 19:00 | 5.6641 | 5.962 | 299.4367 | 1209.5277 | 18142.9149
2020-08-25 20:00 | 6.2188 | 6.5458 | 295.6932 | 1619.2111 | 24288.1667
2020-08-25 21:00 | 7.0478 | 7.4185 | 293.664 | 2378.0212 | 35670.3175
2020-08-25 22:00 | 7.5097 | 7.9047 | 289.8074 | 2882.1919 | 43232.879
2020-08-25 23:00 | 7.6086 | 8.0088 | 292.5083 | 2992.933 | 44893.9946
2020-08-26 00:00 | 7.0347 | 7.4047 | 295.4111 | 2365.1375 | 35477.062
2020-08-26 01:00 | 6.9806 | 7.3477 | 295.3184 | 2312.0579 | 34680.8692
2020-08-26 02:00 | 6.3881 | 6.724 | 292.8597 | 1763.9225 | 26458.838
2020-08-26 03:00 | 6.8536 | 7.214 | 291.6942 | 2187.4809 | 32812.2137
2020-08-26 04:00 | 7.6751 | 8.0788 | 295.2499 | 3071.7138 | 46075.707
2020-08-26 05:00 | 7.1124 | 7.4864 | 302.4455 | 2441.3571 | 36620.3558
2020-08-26 06:00 | 5.7694 | 6.0729 | 306.4828 | 1283.0059 | 19245.0891
2020-08-26 07:00 | 4.5768 | 4.8175 | 306.4127 | 608.0048 | 9120.0716
2020-08-26 08:00 | 4.1761 | 4.3957 | 303.5242 | 437.2869 | 6559.3031
2020-08-26 09:00 | 3.9114 | 4.1171 | 296.8867 | 339.2256 | 5088.3835
2020-08-26 10:00 | 3.2486 | 3.4195 | 279.8273 | 137.7736 | 2066.6037
2020-08-26 11:00 | 3.7573 | 3.9549 | 266.5595 | 285.0933 | 4276.3997
2020-08-26 12:00 | 4.1342 | 4.3516 | 255.4972 | 421.7668 | 6326.5016
2020-08-26 13:00 | 4.3202 | 4.5474 | 247.738 | 494.0222 | 7410.3331
2020-08-26 14:00 | 5.0426 | 5.3078 | 243.9157 | 839.535 | 12593.0257
2020-08-26 15:00 | 4.4285 | 4.6614 | 235.7981 | 542.1255 | 8131.8824
2020-08-26 16:00 | 4.032 | 4.2441 | 210.5704 | 383.9172 | 5758.7587
2020-08-26 17:00 | 5.2627 | 5.5395 | 189.7888 | 959.3681 | 14390.5215
2020-08-26 18:00 | 6.4847 | 6.8258 | 186.8939 | 1846.5467 | 27698.2006
2020-08-26 19:00 | 7.537 | 7.9334 | 186.6789 | 2912.4971 | 43687.4562
2020-08-26 20:00 | 8.2858 | 8.7216 | 191.6554 | 3795.9441 | 56939.1614
2020-08-26 21:00 | 8.4901 | 8.9366 | 206.1382 | 4038.4678 | 60577.017
2020-08-26 22:00 | 7.8663 | 8.28 | 221.2191 | 3298.31 | 49474.6495
2020-08-26 23:00 | 7.6419 | 8.0439 | 227.5086 | 3032.3819 | 45485.7281
2020-08-27 00:00 | 7.6878 | 8.0922 | 234.4198 | 3086.7857 | 46301.7851
2020-08-27 01:00 | 7.9837 | 8.4036 | 244.6506 | 3437.456 | 51561.8405
2020-08-27 02:00 | 8.0208 | 8.4427 | 255.3666 | 3481.4402 | 52221.6037
2020-08-27 03:00 | 7.1657 | 7.5426 | 262.7701 | 2499.0382 | 37485.5726
2020-08-27 04:00 | 6.1412 | 6.4642 | 267.8296 | 1556.9362 | 23354.0432
2020-08-27 05:00 | 5.9839 | 6.2986 | 268.3305 | 1441.0075 | 21615.1129
2020-08-27 06:00 | 5.785 | 6.0893 | 270.5338 | 1294.4785 | 19417.177
2020-08-27 07:00 | 5.4605 | 5.7477 | 268.9083 | 1082.6117 | 16239.1749
2020-08-27 08:00 | 5.5218 | 5.8123 | 262.6644 | 1120.8626 | 16812.9388
2020-08-27 09:00 | 5.9756 | 6.2899 | 254.8174 | 1434.9552 | 21524.3285
2020-08-27 10:00 | 6.2917 | 6.6226 | 246.5299 | 1681.5209 | 25222.814
2020-08-27 11:00 | 8.582 | 9.0334 | 254.3867 | 4145.7119 | 62185.6788
2020-08-27 12:00 | 7.2857 | 7.6688 | 255.3147 | 2632.6338 | 39489.5071
2020-08-27 13:00 | 7.2675 | 7.6498 | 251.4314 | 2612.466 | 39186.99
2020-08-27 14:00 | 8.3751 | 8.8156 | 257.7512 | 3901.9836 | 58529.7543
2020-08-27 15:00 | 8.4651 | 8.9104 | 267.1592 | 4008.8749 | 60133.1231
2020-08-27 16:00 | 8.0466 | 8.4699 | 265.6261 | 3512.056 | 52680.8407
2020-08-27 17:00 | 8.3055 | 8.7423 | 265.4893 | 3819.3179 | 57289.7681
2020-08-27 18:00 | 8.5442 | 8.9936 | 263.3374 | 4102.791 | 61541.8652
2020-08-27 19:00 | 8.9828 | 9.4552 | 263.5882 | 4597.1065 | 68956.5978
2020-08-27 20:00 | 9.0459 | 9.5217 | 264.9294 | 4662.8205 | 69942.3074
2020-08-27 21:00 | 9.2027 | 9.6868 | 267.4769 | 4798.5109 | 71977.663
2020-08-27 22:00 | 10.1299 | 10.6627 | 270.466 | 5410.1604 | 81152.4054
2020-08-27 23:00 | 9.2312 | 9.7167 | 275.4898 | 4823.123 | 72346.8451
2020-08-28 00:00 | 8.4079 | 8.8502 | 273.9346 | 3940.9723 | 59114.5847
2020-08-28 01:00 | 9.1107 | 9.5899 | 275.3722 | 4718.9138 | 70783.7077
2020-08-28 02:00 | 8.7368 | 9.1964 | 271.2257 | 4320.1033 | 64801.5494
2020-08-28 03:00 | 8.7411 | 9.2008 | 272.2954 | 4324.8751 | 64873.1259
2020-08-28 04:00 | 8.2114 | 8.6433 | 269.9249 | 3707.6171 | 55614.2567
2020-08-28 05:00 | 8.8825 | 9.3497 | 273.7581 | 4484.1875 | 67262.8122
2020-08-28 06:00 | 9.3607 | 9.853 | 280.1085 | 4935.1556 | 74027.3342
2020-08-28 07:00 | 9.2372 | 9.7231 | 287.1677 | 4828.37 | 72425.5507
2020-08-28 08:00 | 7.9292 | 8.3462 | 288.7614 | 3372.8371 | 50592.5571
2020-08-28 09:00 | 7.293 | 7.6765 | 283.3962 | 2640.7887 | 39611.8305
2020-08-28 10:00 | 6.8792 | 7.2411 | 282.5454 | 2212.6633 | 33189.9498
2020-08-28 11:00 | 7.013 | 7.3819 | 282.2412 | 2343.8921 | 35158.382
2020-08-28 12:00 | 6.9865 | 7.3539 | 281.6843 | 2317.8445 | 34767.667
2020-08-28 13:00 | 6.1289 | 6.4513 | 284.339 | 1547.8886 | 23218.329
2020-08-28 14:00 | 5.5315 | 5.8224 | 286.3949 | 1126.8641 | 16902.9612
2020-08-28 15:00 | 5.4431 | 5.7294 | 288.3173 | 1071.7791 | 16076.6863
2020-08-28 16:00 | 4.4332 | 4.6663 | 282.9532 | 544.1899 | 8162.8488
2020-08-28 17:00 | 4.4352 | 4.6685 | 282.1698 | 545.0988 | 8176.4818
2020-08-28 18:00 | 3.812 | 4.0125 | 288.9331 | 302.3885 | 4535.8281
2020-08-28 19:00 | 3.4959 | 3.6798 | 290.4376 | 206.4095 | 3096.1418
2020-08-28 20:00 | 2.8611 | 3.0116 | 286.1882 | 50.4863 | 757.2938
2020-08-28 21:00 | 2.3367 | 2.4596 | 269.2891 | 0 | 0
2020-08-28 22:00 | 3.2978 | 3.4712 | 258.2848 | 148.8413 | 2232.6195
2020-08-28 23:00 | 2.7731 | 2.919 | 235.6742 | 0 | 0
2020-08-29 00:00 | 3.1876 | 3.3552 | 211.7947 | 124.0162 | 1860.2428
2020-08-29 01:00 | 3.5592 | 3.7463 | 198.4948 | 225.4558 | 3381.8377
2020-08-29 02:00 | 4.6756 | 4.9215 | 184.1373 | 651.8737 | 9778.1049
2020-08-29 03:00 | 6.059 | 6.3777 | 178.0429 | 1496.3696 | 22445.5446
2020-08-29 04:00 | 6.576 | 6.9218 | 174.8843 | 1924.5253 | 28867.879
2020-08-29 05:00 | 6.1952 | 6.521 | 173.3152 | 1599.0481 | 23985.7216
2020-08-29 06:00 | 5.2281 | 5.5031 | 171.5427 | 937.8083 | 14067.1244
2020-08-29 07:00 | 5.1998 | 5.4733 | 174.444 | 922.5779 | 13838.6678
2020-08-29 08:00 | 4.9243 | 5.1833 | 171.6588 | 776.9954 | 11654.9303
2020-08-29 09:00 | 5.0827 | 5.35 | 171.5268 | 860.6872 | 12910.3083
2020-08-29 10:00 | 5.8793 | 6.1885 | 166.5779 | 1363.9792 | 20459.6883
2020-08-29 11:00 | 6.6134 | 6.9612 | 170.8893 | 1956.5318 | 29347.9769
2020-08-29 12:00 | 7.0924 | 7.4654 | 175.7481 | 2421.7848 | 36326.7724
2020-08-29 13:00 | 7.114 | 7.4882 | 177.636 | 2442.9587 | 36644.381
2020-08-29 14:00 | 6.7637 | 7.1195 | 179.6001 | 2099.3419 | 31490.1282
2020-08-29 15:00 | 5.7781 | 6.082 | 178.1133 | 1289.4283 | 19341.4244
2020-08-29 16:00 | 5.8282 | 6.1348 | 174.205 | 1326.3467 | 19895.201
2020-08-29 17:00 | 6.5716 | 6.9172 | 171.6061 | 1920.7791 | 28811.6861
2020-08-29 18:00 | 7.4778 | 7.871 | 173.4098 | 2846.5647 | 42698.4703
2020-08-29 19:00 | 7.775 | 8.184 | 178.0126 | 3190.1537 | 47852.3049
2020-08-29 20:00 | 7.99 | 8.4102 | 184.9965 | 3444.8873 | 51673.3089
2020-08-29 21:00 | 8.0876 | 8.513 | 191.8343 | 3560.6205 | 53409.3078
2020-08-29 22:00 | 8.2944 | 8.7306 | 195.659 | 3806.1083 | 57091.6249
2020-08-29 23:00 | 8.5201 | 8.9682 | 195.4826 | 4074.1845 | 61112.7681
2020-08-30 00:00 | 8.5259 | 8.9743 | 196.4596 | 4081.0205 | 61215.3081
2020-08-30 01:00 | 8.3546 | 8.794 | 196.0316 | 3877.6878 | 58165.3167
2020-08-30 02:00 | 8.2384 | 8.6717 | 197.3346 | 3739.6434 | 56094.6507
2020-08-30 03:00 | 8.2423 | 8.6758 | 196.0684 | 3744.3185 | 56164.778
2020-08-30 04:00 | 7.962 | 8.3808 | 194.3726 | 3411.744 | 51176.16
2020-08-30 05:00 | 7.3869 | 7.7754 | 193.6686 | 2745.361 | 41180.4146
2020-08-30 06:00 | 6.3394 | 6.6729 | 190.6137 | 1722.3548 | 25835.3216
2020-08-30 07:00 | 6.2167 | 6.5437 | 188.4843 | 1617.4822 | 24262.2334
2020-08-30 08:00 | 6.2828 | 6.6132 | 184.3919 | 1673.9324 | 25108.9856
2020-08-30 09:00 | 6.6648 | 7.0154 | 181.4428 | 2002.3371 | 30035.0572
2020-08-30 10:00 | 6.9163 | 7.2801 | 178.8494 | 2249.0574 | 33735.8604
2020-08-30 11:00 | 7.1927 | 7.571 | 180.4163 | 2529.1261 | 37936.8918
2020-08-30 12:00 | 7.3498 | 7.7364 | 182.5348 | 2704.0995 | 40561.4932
2020-08-30 13:00 | 7.3661 | 7.7535 | 183.0097 | 2722.2409 | 40833.6139
2020-08-30 14:00 | 7.2806 | 7.6635 | 182.422 | 2627.0359 | 39405.5379
2020-08-30 15:00 | 7.111 | 7.485 | 177.3158 | 2440.0628 | 36600.9418
2020-08-30 16:00 | 7.6959 | 8.1006 | 175.9195 | 3096.3104 | 46444.6559
2020-08-30 17:00 | 8.1101 | 8.5366 | 176.911 | 3587.2798 | 53809.1977
2020-08-30 18:00 | 8.5445 | 8.9939 | 179.1805 | 4103.112 | 61546.6801
2020-08-30 19:00 | 8.6333 | 9.0873 | 182.9743 | 4203.4503 | 63051.7539
2020-08-30 20:00 | 8.816 | 9.2797 | 184.8412 | 4409.2317 | 66138.4752
2020-08-30 21:00 | 8.9536 | 9.4245 | 187.2654 | 4564.1954 | 68462.9304
2020-08-30 22:00 | 8.8348 | 9.2995 | 193.437 | 4430.4623 | 66456.9347
2020-08-30 23:00 | 8.9112 | 9.3799 | 191.282 | 4516.5215 | 67747.8226
2020-08-31 00:00 | 8.97 | 9.4418 | 191.7617 | 4582.6786 | 68740.1784
2020-08-31 01:00 | 8.8498 | 9.3152 | 192.7644 | 4447.2957 | 66709.4356
2020-08-31 02:00 | 8.8304 | 9.2948 | 191.9947 | 4425.4351 | 66381.5258
2020-08-31 03:00 | 8.8249 | 9.289 | 190.5042 | 4419.2505 | 66288.757
2020-08-31 04:00 | 8.8938 | 9.3615 | 189.3214 | 4496.8299 | 67452.4478
2020-08-31 05:00 | 8.7003 | 9.1579 | 187.1368 | 4278.9705 | 64184.557
2020-08-31 06:00 | 8.0867 | 8.512 | 187.067 | 3559.5405 | 53393.1075
2020-08-31 07:00 | 7.8863 | 8.3011 | 190.4013 | 3322.0397 | 49830.5952
2020-08-31 08:00 | 7.868 | 8.2819 | 193.608 | 3300.3736 | 49505.6044
2020-08-31 09:00 | 7.6922 | 8.0967 | 197.9591 | 3091.9049 | 46378.5731
2020-08-31 10:00 | 6.9568 | 7.3227 | 197.0347 | 2288.7104 | 34330.6555
2020-08-31 11:00 | 6.8655 | 7.2266 | 201.0561 | 2199.169 | 32987.5346
2020-08-31 12:00 | 6.7989 | 7.1565 | 201.9109 | 2133.8804 | 32008.2063
2020-08-31 13:00 | 6.8737 | 7.2352 | 199.2246 | 2207.1909 | 33107.8641
2020-08-31 14:00 | 6.7249 | 7.0786 | 201.0386 | 2061.2354 | 30918.5312
2020-08-31 15:00 | 6.2734 | 6.6034 | 198.9696 | 1665.9268 | 24988.9021
2020-08-31 16:00 | 6.4983 | 6.84 | 197.1417 | 1858.1154 | 27871.731
2020-08-31 17:00 | 7.3223 | 7.7074 | 195.4555 | 2673.3931 | 40100.8967
2020-08-31 18:00 | 7.2519 | 7.6333 | 204.4351 | 2595.0153 | 38925.2296
2020-08-31 19:00 | 6.0888 | 6.409 | 232.547 | 1518.2937 | 22774.4056
2020-08-31 20:00 | 5.3987 | 5.6826 | 276.6304 | 1044.1165 | 15661.7471
2020-08-31 21:00 | 5.736 | 6.0377 | 318.2954 | 1258.3756 | 18875.6335
2020-08-31 22:00 | 5.6135 | 5.9087 | 343.58 | 1177.9726 | 17669.5896
2020-08-31 23:00 | 6.1821 | 6.5072 | 355.6685 | 1587.8716 | 23818.0742
2020-09-01 00:00 | 6.0294 | 6.3465 | 5.3121 | 1474.575 | 22118.625
2020-09-01 01:00 | 5.826 | 6.1324 | 12.5921 | 1324.6799 | 19870.1989
2020-09-01 02:00 | 5.8743 | 6.1832 | 18.8112 | 1360.2672 | 20404.0086
2020-09-01 03:00 | 5.9941 | 6.3093 | 23.2943 | 1448.5134 | 21727.7008
2020-09-01 04:00 | 6.0753 | 6.3949 | 33.3073 | 1508.3974 | 22625.9611
2020-09-01 05:00 | 5.4628 | 5.7501 | 46.5928 | 1084.0804 | 16261.2067
2020-09-01 06:00 | 4.7707 | 5.0216 | 58.3524 | 695.8257 | 10437.3858
2020-09-01 07:00 | 4.1966 | 4.4173 | 70.1738 | 444.8949 | 6673.4237
2020-09-01 08:00 | 3.2826 | 3.4552 | 74.3958 | 145.4143 | 2181.2144
2020-09-01 09:00 | 2.9292 | 3.0832 | 75.0051 | 65.8129 | 987.193
2020-09-01 10:00 | 2.4469 | 2.5756 | 110.0278 | 0 | 0
2020-09-01 11:00 | 1.5633 | 1.6455 | 121.1859 | 0 | 0
2020-09-01 12:00 | 1.6006 | 1.6848 | 111.4505 | 0 | 0
2020-09-01 13:00 | 1.9229 | 2.0241 | 101.3435 | 0 | 0
2020-09-01 14:00 | 2.599 | 2.7357 | 92.8197 | 0 | 0
2020-09-01 15:00 | 3.1762 | 3.3433 | 75.1731 | 121.4572 | 1821.8586
2020-09-01 16:00 | 5.1591 | 5.4304 | 53.5703 | 901.0814 | 13516.2205
2020-09-01 17:00 | 7.1242 | 7.4989 | 54.1793 | 2452.9502 | 36794.2537
2020-09-01 18:00 | 7.491 | 7.885 | 63.9067 | 2861.2771 | 42919.1569
2020-09-01 19:00 | 7.5377 | 7.9342 | 81.8404 | 2913.3435 | 43700.1528
2020-09-01 20:00 | 7.7588 | 8.1669 | 103.1559 | 3170.9484 | 47564.2255
2020-09-01 21:00 | 7.7391 | 8.1461 | 117.6551 | 3147.5452 | 47213.1786
2020-09-01 22:00 | 5.6249 | 5.9207 | 131.4686 | 1185.0674 | 17776.0109
2020-09-01 23:00 | 4.8248 | 5.0786 | 137.8093 | 724.4523 | 10866.7839
2020-09-02 00:00 | 4.0199 | 4.2313 | 139.1142 | 379.411 | 5691.1653
2020-09-02 01:00 | 3.1685 | 3.3351 | 142.0278 | 119.7206 | 1795.8092
2020-09-02 02:00 | 2.4471 | 2.5758 | 136.1657 | 0 | 0
2020-09-02 03:00 | 2.9355 | 3.0899 | 112.3053 | 67.2406 | 1008.6094
2020-09-02 04:00 | 4.3401 | 4.5683 | 105.848 | 502.8336 | 7542.5047
2020-09-02 05:00 | 4.7584 | 5.0087 | 108.9659 | 689.3508 | 10340.2613
2020-09-02 06:00 | 3.9134 | 4.1192 | 112.2401 | 339.9614 | 5099.4211
2020-09-02 07:00 | 3.204 | 3.3725 | 117.4106 | 127.7248 | 1915.8714
2020-09-02 08:00 | 3.3285 | 3.5036 | 121.2807 | 156.0245 | 2340.367
2020-09-02 09:00 | 3.4425 | 3.6235 | 125.0763 | 190.3284 | 2854.9255
2020-09-02 10:00 | 2.5686 | 2.7037 | 123.1703 | 0 | 0
2020-09-02 11:00 | 2.2244 | 2.3414 | 127.0507 | 0 | 0
2020-09-02 12:00 | 2.3239 | 2.4462 | 138.3851 | 0 | 0
2020-09-02 13:00 | 1.7982 | 1.8928 | 155.6531 | 0 | 0
2020-09-02 14:00 | 1.0445 | 1.0995 | 208.5441 | 0 | 0
2020-09-02 15:00 | 2.5516 | 2.6858 | 287.4029 | 0 | 0
2020-09-02 16:00 | 5.7558 | 6.0585 | 300.5732 | 1272.9774 | 19094.6607
2020-09-02 17:00 | 8.0299 | 8.4523 | 302.9941 | 3492.2582 | 52383.8731
2020-09-02 18:00 | 9.2408 | 9.7268 | 303.4377 | 4831.4614 | 72471.9205
2020-09-02 19:00 | 9.5676 | 10.0708 | 306.6044 | 5097.3318 | 76459.9769
2020-09-02 20:00 | 8.856 | 9.3218 | 311.8819 | 4454.3051 | 66814.5769
2020-09-02 21:00 | 8.4023 | 8.8443 | 312.3935 | 3934.3335 | 59015.003
2020-09-02 22:00 | 8.0761 | 8.5008 | 312.9944 | 3546.947 | 53204.2046
2020-09-02 23:00 | 8.0701 | 8.4945 | 315.946 | 3539.8404 | 53097.6058
2020-09-03 00:00 | 7.8392 | 8.2515 | 317.2992 | 3266.1622 | 48992.433
2020-09-03 01:00 | 7.3974 | 7.7865 | 320.6259 | 2757.1187 | 41356.78
2020-09-03 02:00 | 6.8983 | 7.2611 | 325.7148 | 2231.3417 | 33470.1253
2020-09-03 03:00 | 6.2189 | 6.546 | 328.3873 | 1619.3676 | 24290.5139
2020-09-03 04:00 | 5.7014 | 6.0013 | 328.4311 | 1232.9055 | 18493.5832
2020-09-03 05:00 | 4.8018 | 5.0543 | 331.1941 | 712.2729 | 10684.0928
2020-09-03 06:00 | 4.2985 | 4.5246 | 333.6488 | 484.3765 | 7265.6471
2020-09-03 07:00 | 4.2089 | 4.4302 | 332.7997 | 449.4466 | 6741.6986
2020-09-03 08:00 | 4.411 | 4.643 | 330.1793 | 534.3659 | 8015.488
2020-09-03 09:00 | 4.6844 | 4.9307 | 332.8408 | 655.7718 | 9836.577
2020-09-03 10:00 | 4.8328 | 5.0869 | 345.4992 | 728.6481 | 10929.7219
2020-09-03 11:00 | 5.2501 | 5.5262 | 347.3729 | 951.5098 | 14272.647
2020-09-03 12:00 | 5.3853 | 5.6686 | 355.4791 | 1035.7847 | 15536.77
2020-09-03 13:00 | 5.5096 | 5.7994 | 358.6725 | 1113.2468 | 16698.7021
2020-09-03 14:00 | 5.2813 | 5.5591 | 1.6334 | 970.9907 | 14564.8602
2020-09-03 15:00 | 4.4826 | 4.7184 | 349.5753 | 566.1512 | 8492.2677
2020-09-03 16:00 | 5.0966 | 5.3646 | 335.3695 | 868.034 | 13020.5102
2020-09-03 17:00 | 5.8954 | 6.2054 | 334.2706 | 1375.8143 | 20637.2139
2020-09-03 18:00 | 6.4256 | 6.7635 | 337.1232 | 1795.9625 | 26939.4376
2020-09-03 19:00 | 6.8432 | 7.2031 | 339.5543 | 2177.2928 | 32659.3918
2020-09-03 20:00 | 6.7295 | 7.0834 | 347.2043 | 2065.7603 | 30986.405
2020-09-03 21:00 | 6.143 | 6.4661 | 1.194 | 1558.2932 | 23374.3981
2020-09-03 22:00 | 5.6356 | 5.932 | 358.9399 | 1191.722 | 17875.8298
2020-09-03 23:00 | 5.4752 | 5.7632 | 350.2404 | 1091.807 | 16377.105
2020-09-04 00:00 | 5.7153 | 6.0159 | 341.4368 | 1243.1397 | 18647.0949
2020-09-04 01:00 | 6.0448 | 6.3627 | 339.3362 | 1485.9143 | 22288.7144
2020-09-04 02:00 | 6.0697 | 6.3889 | 331.6304 | 1504.2504 | 22563.7561
2020-09-04 03:00 | 6.7508 | 7.1059 | 328.9942 | 2086.669 | 31300.0348
2020-09-04 04:00 | 7.4133 | 7.8032 | 328.7179 | 2774.7751 | 41621.627
2020-09-04 05:00 | 7.6738 | 8.0774 | 333.0485 | 3070.1879 | 46052.8185
2020-09-04 06:00 | 7.2632 | 7.6452 | 340.4842 | 2607.6018 | 39114.0264
2020-09-04 07:00 | 6.8841 | 7.2461 | 347.9746 | 2217.3984 | 33260.9766
2020-09-04 08:00 | 6.225 | 6.5524 | 350.1831 | 1624.5757 | 24368.6354
2020-09-04 09:00 | 5.7491 | 6.0515 | 348.4605 | 1268.0378 | 19020.5665
2020-09-04 10:00 | 5.5499 | 5.8418 | 342.4908 | 1138.3547 | 17075.3211
2020-09-04 11:00 | 5.5656 | 5.8584 | 338.6217 | 1148.1523 | 17222.284
2020-09-04 12:00 | 5.9264 | 6.238 | 337.4692 | 1398.6314 | 20979.4705
2020-09-04 13:00 | 6.5782 | 6.9242 | 338.1123 | 1926.4472 | 28896.7074
2020-09-04 14:00 | 7.0077 | 7.3763 | 340.4717 | 2338.7021 | 35080.5314
2020-09-04 15:00 | 7.0724 | 7.4444 | 344.5154 | 2402.1538 | 36032.3074
2020-09-04 16:00 | 6.3683 | 6.7033 | 348.6433 | 1747.0401 | 26205.6012
2020-09-04 17:00 | 5.7866 | 6.0909 | 353.8537 | 1295.6303 | 19434.4543
2020-09-04 18:00 | 5.6702 | 5.9684 | 352.7689 | 1213.2895 | 18199.3432
2020-09-04 19:00 | 6.0765 | 6.3961 | 348.7963 | 1509.2715 | 22639.0723
2020-09-04 20:00 | 6.5229 | 6.866 | 346.7821 | 1879.1732 | 28187.5973
2020-09-04 21:00 | 6.6951 | 7.0473 | 346.7779 | 2032.0374 | 30480.5607
2020-09-04 22:00 | 6.5359 | 6.8797 | 347.1721 | 1890.304 | 28354.5602
2020-09-04 23:00 | 6.3268 | 6.6596 | 342.2514 | 1711.5999 | 25673.9982
2020-09-05 00:00 | 5.994 | 6.3093 | 343.285 | 1448.5011 | 21727.5165
2020-09-05 01:00 | 5.9918 | 6.3069 | 342.2796 | 1446.8405 | 21702.6077
2020-09-05 02:00 | 6.2894 | 6.6202 | 338.58 | 1679.5773 | 25193.6602
2020-09-05 03:00 | 6.4301 | 6.7683 | 335.879 | 1799.8521 | 26997.7814
2020-09-05 04:00 | 6.5322 | 6.8758 | 334.482 | 1887.1216 | 28306.8233
2020-09-05 05:00 | 6.2778 | 6.608 | 335.8988 | 1669.6735 | 25045.1026
2020-09-05 06:00 | 5.2654 | 5.5423 | 341.1823 | 961.0299 | 14415.4478
2020-09-05 07:00 | 5.3866 | 5.6699 | 350.1637 | 1036.5952 | 15548.9279
2020-09-05 08:00 | 5.2761 | 5.5536 | 1.2986 | 967.7117 | 14515.6758
2020-09-05 09:00 | 4.7957 | 5.0479 | 3.0735 | 709.0363 | 10635.5439
2020-09-05 10:00 | 4.0316 | 4.2436 | 2.1715 | 383.7433 | 5756.1493
2020-09-05 11:00 | 3.8935 | 4.0982 | 3.4786 | 332.5806 | 4988.7085
2020-09-05 12:00 | 3.9552 | 4.1632 | 6.9052 | 355.4555 | 5331.8321
2020-09-05 13:00 | 4.1301 | 4.3473 | 9.5893 | 420.2387 | 6303.5806
2020-09-05 14:00 | 4.0688 | 4.2828 | 9.9946 | 397.5491 | 5963.2367
2020-09-05 15:00 | 3.9396 | 4.1468 | 9.742 | 349.6713 | 5245.0696
2020-09-05 16:00 | 4.3464 | 4.575 | 1.2534 | 505.6657 | 7584.9859
2020-09-05 17:00 | 4.9919 | 5.2545 | 358.8085 | 812.7452 | 12191.1775
2020-09-05 18:00 | 5.0655 | 5.3319 | 4.2022 | 851.6378 | 12774.5672
2020-09-05 19:00 | 4.8637 | 5.1195 | 13.4225 | 744.9678 | 11174.5169
2020-09-05 20:00 | 4.5473 | 4.7864 | 23.5519 | 594.88 | 8923.2
2020-09-05 21:00 | 4.09 | 4.3051 | 25.9666 | 405.4045 | 6081.0678
2020-09-05 22:00 | 3.7753 | 3.9738 | 15.0642 | 290.5167 | 4357.7508
2020-09-05 23:00 | 3.446 | 3.6273 | 5.9068 | 191.3955 | 2870.932
2020-09-06 00:00 | 3.3304 | 3.5055 | 358.3654 | 156.58 | 2348.7003
2020-09-06 01:00 | 3.3173 | 3.4917 | 354.9118 | 153.2294 | 2298.4403
2020-09-06 02:00 | 3.3883 | 3.5665 | 348.2596 | 174.0154 | 2610.2303
2020-09-06 03:00 | 3.5322 | 3.718 | 346.3691 | 217.3537 | 3260.3051
2020-09-06 04:00 | 3.5734 | 3.7613 | 345.2073 | 229.7416 | 3446.124
2020-09-06 05:00 | 2.9966 | 3.1542 | 357.9489 | 81.0056 | 1215.0833
2020-09-06 06:00 | 1.5261 | 1.6063 | 24.6181 | 0 | 0
2020-09-06 07:00 | 1.0898 | 1.1471 | 52.3275 | 0 | 0
2020-09-06 08:00 | 0.94476 | 0.99445 | 39.7698 | 0 | 0
2020-09-06 09:00 | 0.74135 | 0.78034 | 352.8551 | 0 | 0
2020-09-06 10:00 | 0.83299 | 0.8768 | 343.8375 | 0 | 0
2020-09-06 11:00 | 1.1717 | 1.2333 | 308.2866 | 0 | 0
2020-09-06 12:00 | 1.0934 | 1.1509 | 305.6762 | 0 | 0
2020-09-06 13:00 | 1.3765 | 1.4489 | 310.6805 | 0 | 0
2020-09-06 14:00 | 1.6324 | 1.7183 | 324.8764 | 0 | 0
2020-09-06 15:00 | 1.9176 | 2.0184 | 339.2799 | 0 | 0
2020-09-06 16:00 | 3.3743 | 3.5518 | 337.4936 | 169.8087 | 2547.1306
2020-09-06 17:00 | 4.5222 | 4.7601 | 344.0825 | 583.7557 | 8756.335
2020-09-06 18:00 | 4.7559 | 5.006 | 1.4553 | 688.0365 | 10320.5479
2020-09-06 19:00 | 4.6229 | 4.866 | 13.2429 | 628.4496 | 9426.7441
2020-09-06 20:00 | 4.308 | 4.5346 | 17.0126 | 488.6091 | 7329.1372
2020-09-06 21:00 | 4.1503 | 4.3685 | 27.4139 | 427.7275 | 6415.9127
2020-09-06 22:00 | 4.1942 | 4.4148 | 38.7683 | 444.009 | 6660.1356
2020-09-06 23:00 | 3.9124 | 4.1181 | 45.9827 | 339.5789 | 5093.684
2020-09-07 00:00 | 3.5559 | 3.7429 | 37.7636 | 224.4704 | 3367.0556
2020-09-07 01:00 | 3.7072 | 3.9022 | 33.3507 | 270.0364 | 4050.5464
2020-09-07 02:00 | 3.8087 | 4.009 | 36.8877 | 301.1811 | 4517.7161
2020-09-07 03:00 | 3.9095 | 4.1152 | 41.1702 | 338.5349 | 5078.0232
2020-09-07 04:00 | 4.034 | 4.2461 | 52.582 | 384.6387 | 5769.5799
2020-09-07 05:00 | 3.7752 | 3.9737 | 66.3336 | 290.4855 | 4357.2818
2020-09-07 06:00 | 2.5498 | 2.6839 | 79.6498 | 0 | 0
2020-09-07 07:00 | 2.5971 | 2.7337 | 100.1296 | 0 | 0
2020-09-07 08:00 | 2.8879 | 3.0398 | 117.3249 | 56.5097 | 847.6462
2020-09-07 09:00 | 3.3618 | 3.5386 | 133.7134 | 166.0515 | 2490.772
2020-09-07 10:00 | 3.7003 | 3.895 | 141.2654 | 267.9577 | 4019.3655
2020-09-07 11:00 | 4.3804 | 4.6108 | 157.5888 | 520.762 | 7811.4306
2020-09-07 12:00 | 4.8566 | 5.112 | 173.7672 | 741.217 | 11118.2556
2020-09-07 13:00 | 5.1351 | 5.4052 | 187.1352 | 888.4016 | 13326.024
2020-09-07 14:00 | 5.0931 | 5.3609 | 198.9075 | 866.1849 | 12992.7738
2020-09-07 15:00 | 4.2706 | 4.4953 | 213.0637 | 472.3293 | 7084.9389
2020-09-07 16:00 | 4.1274 | 4.3444 | 238.5795 | 419.2418 | 6288.6276
2020-09-07 17:00 | 5.8787 | 6.1879 | 294.1009 | 1363.5344 | 20453.0163
2020-09-07 18:00 | 9.8241 | 10.3408 | 325.1736 | 5255.0278 | 78825.4172
2020-09-07 19:00 | 9.7401 | 10.2523 | 335.8244 | 5203.3716 | 78050.5741
2020-09-07 20:00 | 8.315 | 8.7523 | 336.9059 | 3830.6423 | 57459.6346
2020-09-07 21:00 | 7.4813 | 7.8747 | 335.881 | 2850.476 | 42757.1395
2020-09-07 22:00 | 7.7105 | 8.1161 | 326.9562 | 3113.7035 | 46705.5525
2020-09-07 23:00 | 8.3374 | 8.7759 | 329.356 | 3857.2066 | 57858.0988
2020-09-08 00:00 | 8.2083 | 8.64 | 334.5005 | 3703.8974 | 55558.4609
2020-09-08 01:00 | 7.4232 | 7.8137 | 337.6844 | 2785.8473 | 41787.7094
2020-09-08 02:00 | 6.7777 | 7.1342 | 335.2693 | 2113.0522 | 31695.7837
2020-09-08 03:00 | 6.1539 | 6.4776 | 328.4936 | 1566.2933 | 23494.399
2020-09-08 04:00 | 5.6856 | 5.9846 | 322.095 | 1222.8805 | 18343.2068
2020-09-08 05:00 | 6.2617 | 6.5911 | 314.8917 | 1655.9527 | 24839.2898
2020-09-08 06:00 | 5.7944 | 6.0991 | 311.0975 | 1301.4018 | 19521.0271
2020-09-08 07:00 | 5.5964 | 5.8908 | 308.1755 | 1167.3255 | 17509.8829
2020-09-08 08:00 | 6.0523 | 6.3706 | 307.9073 | 1491.4472 | 22371.7087
2020-09-08 09:00 | 6.4139 | 6.7513 | 306.1492 | 1786.0236 | 26790.354
2020-09-08 10:00 | 6.5626 | 6.9078 | 302.7127 | 1913.1152 | 28696.7287
2020-09-08 11:00 | 6.7202 | 7.0736 | 300.6575 | 2056.6123 | 30849.1841
2020-09-08 12:00 | 6.6387 | 6.9879 | 298.3187 | 1978.1652 | 29672.4774
2020-09-08 13:00 | 6.2335 | 6.5614 | 295.7903 | 1631.827 | 24477.4047
2020-09-08 14:00 | 6.2044 | 6.5307 | 294.34 | 1606.9688 | 24104.5318
2020-09-08 15:00 | 5.9824 | 6.2971 | 295.0266 | 1439.9368 | 21599.0518
2020-09-08 16:00 | 5.4358 | 5.7217 | 291.9226 | 1067.218 | 16008.2697
2020-09-08 17:00 | 5.2219 | 5.4965 | 278.1463 | 934.2467 | 14013.7003
2020-09-08 18:00 | 5.8137 | 6.1195 | 272.9756 | 1315.6289 | 19734.4342
2020-09-08 19:00 | 6.344 | 6.6777 | 275.113 | 1726.2732 | 25894.0987
2020-09-08 20:00 | 6.58 | 6.926 | 275.5024 | 1927.9336 | 28919.0034
2020-09-08 21:00 | 6.8076 | 7.1657 | 270.944 | 2142.3895 | 32135.842
2020-09-08 22:00 | 7.4745 | 7.8676 | 263.5245 | 2842.9113 | 42643.669
2020-09-08 23:00 | 8.2386 | 8.6719 | 260.5245 | 3739.8693 | 56098.0389
2020-09-09 00:00 | 8.6113 | 9.0642 | 260.6165 | 4178.7262 | 62680.893
2020-09-09 01:00 | 8.7057 | 9.1636 | 260.1029 | 4285.004 | 64275.0605
2020-09-09 02:00 | 8.7465 | 9.2065 | 261.429 | 4330.9234 | 64963.8512
2020-09-09 03:00 | 8.5588 | 9.0089 | 265.3666 | 4119.5654 | 61793.4816
2020-09-09 04:00 | 8.3138 | 8.751 | 271.6811 | 3829.1842 | 57437.7633
2020-09-09 05:00 | 7.9454 | 8.3633 | 275.7454 | 3392.115 | 50881.7251
2020-09-09 06:00 | 6.8529 | 7.2133 | 276.4194 | 2186.8078 | 32802.1166
2020-09-09 07:00 | 6.9275 | 7.2918 | 280.1442 | 2259.9652 | 33899.4778
2020-09-09 08:00 | 7.6121 | 8.0124 | 285.4902 | 2997.01 | 44955.1502
2020-09-09 09:00 | 8.6038 | 9.0563 | 288.9067 | 4170.2165 | 62553.248
2020-09-09 10:00 | 7.369 | 7.7565 | 286.2109 | 2725.4051 | 40881.0771
2020-09-09 11:00 | 7.3616 | 7.7488 | 284.8802 | 2717.1942 | 40757.9133
2020-09-09 12:00 | 7.3477 | 7.7342 | 285.0285 | 2701.735 | 40526.0253
2020-09-09 13:00 | 7.1656 | 7.5425 | 287.426 | 2498.987 | 37484.8044
2020-09-09 14:00 | 6.7512 | 7.1063 | 287.4601 | 2087.028 | 31305.4206
2020-09-09 15:00 | 6.069 | 6.3882 | 288.2082 | 1503.7125 | 22555.6876
2020-09-09 16:00 | 5.5623 | 5.8548 | 288.7658 | 1146.0493 | 17190.7401
2020-09-09 17:00 | 5.3505 | 5.6319 | 288.2602 | 1014.1021 | 15211.5319
2020-09-09 18:00 | 5.0262 | 5.2906 | 286.2373 | 830.8649 | 12462.9735
2020-09-09 19:00 | 4.706 | 4.9535 | 283.5378 | 665.3783 | 9980.674
2020-09-09 20:00 | 4.3902 | 4.6211 | 278.6899 | 525.1024 | 7876.5359
2020-09-09 21:00 | 4.4985 | 4.7351 | 267.3764 | 573.1995 | 8597.9927
2020-09-09 22:00 | 5.1045 | 5.373 | 260.0079 | 872.2285 | 13083.4276
2020-09-09 23:00 | 5.1865 | 5.4593 | 251.869 | 915.5472 | 13733.2075
2020-09-10 00:00 | 5.4351 | 5.721 | 244.7904 | 1066.8162 | 16002.2428
2020-09-10 01:00 | 5.9012 | 6.2115 | 238.3479 | 1380.0696 | 20701.0442
2020-09-10 02:00 | 6.4056 | 6.7425 | 234.7156 | 1778.9169 | 26683.7536
2020-09-10 03:00 | 6.7525 | 7.1076 | 232.4717 | 2088.307 | 31324.6045
2020-09-10 04:00 | 6.9307 | 7.2952 | 230.4341 | 2263.1575 | 33947.3632
2020-09-10 05:00 | 6.9725 | 7.3392 | 229.8538 | 2304.1059 | 34561.5885
2020-09-10 06:00 | 6.1476 | 6.4709 | 230.8806 | 1561.6444 | 23424.6653
2020-09-10 07:00 | 6.3623 | 6.6969 | 233.6574 | 1741.8983 | 26128.4749
2020-09-10 08:00 | 7.6756 | 8.0793 | 240.5522 | 3072.2484 | 46083.7262
2020-09-10 09:00 | 8.7009 | 9.1585 | 246.1941 | 4279.6444 | 64194.6666
2020-09-10 10:00 | 8.1919 | 8.6227 | 244.909 | 3684.4542 | 55266.8129
2020-09-10 11:00 | 8.1066 | 8.5329 | 250.6901 | 3583.1286 | 53746.9287
2020-09-10 12:00 | 7.8912 | 8.3062 | 256.9048 | 3327.8018 | 49917.0273
2020-09-10 13:00 | 7.7117 | 8.1173 | 267.1267 | 3115.1161 | 46726.741
2020-09-10 14:00 | 7.586 | 7.985 | 278.0555 | 2967.137 | 44507.0546
2020-09-10 15:00 | 6.9714 | 7.3381 | 289.8744 | 2303.0836 | 34546.2534
2020-09-10 16:00 | 7.2418 | 7.6227 | 305.7056 | 2583.8423 | 38757.6352
2020-09-10 17:00 | 7.6433 | 8.0453 | 324.5078 | 3033.9582 | 45509.3737
2020-09-10 18:00 | 7.1145 | 7.4887 | 334.9986 | 2443.4433 | 36651.6501
2020-09-10 19:00 | 7.1588 | 7.5353 | 339.8345 | 2491.3802 | 37370.7034
2020-09-10 20:00 | 7.1816 | 7.5593 | 345.4449 | 2516.7131 | 37750.6962
2020-09-10 21:00 | 6.7614 | 7.117 | 350.8436 | 2097.0894 | 31456.341
2020-09-10 22:00 | 6.584 | 6.9303 | 342.5717 | 1931.3836 | 28970.7534
2020-09-10 23:00 | 6.1906 | 6.5162 | 338.8441 | 1595.1595 | 23927.3932
2020-09-11 00:00 | 5.9288 | 6.2407 | 337.096 | 1400.4725 | 21007.0881
2020-09-11 01:00 | 5.9556 | 6.2688 | 337.4067 | 1420.1567 | 21302.3505
2020-09-11 02:00 | 5.7847 | 6.0889 | 339.8738 | 1294.2519 | 19413.7788
2020-09-11 03:00 | 5.2154 | 5.4897 | 342.6377 | 930.846 | 13962.69
2020-09-11 04:00 | 4.7461 | 4.9957 | 343.4899 | 683.1932 | 10247.8978
2020-09-11 05:00 | 3.8555 | 4.0583 | 345.6466 | 318.5321 | 4777.9817
2020-09-11 06:00 | 3.5479 | 3.7345 | 356.0665 | 222.0558 | 3330.8376
2020-09-11 07:00 | 3.2335 | 3.4035 | 4.2377 | 134.3584 | 2015.3758
2020-09-11 08:00 | 2.9325 | 3.0867 | 7.6968 | 66.5511 | 998.2658
2020-09-11 09:00 | 2.7456 | 2.89 | 9.1045 | 0 | 0
2020-09-11 10:00 | 2.2026 | 2.3185 | 18.7908 | 0 | 0
2020-09-11 11:00 | 1.7202 | 1.8107 | 28.5858 | 0 | 0
2020-09-11 12:00 | 1.4046 | 1.4785 | 23.2861 | 0 | 0
2020-09-11 13:00 | 1.4795 | 1.5573 | 19.7179 | 0 | 0
2020-09-11 14:00 | 1.5778 | 1.6607 | 25.7958 | 0 | 0
2020-09-11 15:00 | 1.7097 | 1.7997 | 33.0259 | 0 | 0
2020-09-11 16:00 | 2.2345 | 2.3521 | 40.6989 | 0 | 0
2020-09-11 17:00 | 3.3317 | 3.5069 | 56.3339 | 156.967 | 2354.5046
2020-09-11 18:00 | 4.0637 | 4.2774 | 74.1174 | 395.6388 | 5934.5814
2020-09-11 19:00 | 4.5003 | 4.737 | 82.6357 | 574.0253 | 8610.3789
2020-09-11 20:00 | 4.7346 | 4.9836 | 92.2253 | 678.0802 | 10171.2026
2020-09-11 21:00 | 4.8437 | 5.0984 | 103.3661 | 734.4044 | 11016.0659
2020-09-11 22:00 | 4.5828 | 4.8239 | 118.1317 | 610.6777 | 9160.1655
2020-09-11 23:00 | 4.3239 | 4.5513 | 123.908 | 495.6344 | 7434.5155
2020-09-12 00:00 | 4.1347 | 4.3522 | 127.0134 | 421.9656 | 6329.4841
2020-09-12 01:00 | 4.0227 | 4.2343 | 130.905 | 380.4732 | 5707.0986
2020-09-12 02:00 | 4.0145 | 4.2257 | 134.5254 | 377.4388 | 5661.5815
2020-09-12 03:00 | 4.1223 | 4.3391 | 138.7025 | 417.3783 | 6260.6751
2020-09-12 04:00 | 4.1177 | 4.3343 | 143.6591 | 415.6576 | 6234.8642
2020-09-12 05:00 | 4.5014 | 4.7382 | 147.2247 | 574.513 | 8617.695
2020-09-12 06:00 | 3.4005 | 3.5794 | 150.3502 | 177.695 | 2665.4257
2020-09-12 07:00 | 2.5993 | 2.736 | 151.9842 | 0 | 0
2020-09-12 08:00 | 2.4474 | 2.5761 | 152.7037 | 0 | 0
2020-09-12 09:00 | 2.5377 | 2.6712 | 162.4539 | 0 | 0
2020-09-12 10:00 | 2.616 | 2.7536 | 162.3596 | 0 | 0
2020-09-12 11:00 | 2.4543 | 2.5833 | 165.6646 | 0 | 0
2020-09-12 12:00 | 2.5215 | 2.6541 | 168.8161 | 0 | 0
2020-09-12 13:00 | 2.4478 | 2.5765 | 168.6258 | 0 | 0
2020-09-12 14:00 | 2.5358 | 2.6691 | 165.8847 | 0 | 0
2020-09-12 15:00 | 2.9781 | 3.1348 | 156.2916 | 76.8369 | 1152.5532
2020-09-12 16:00 | 4.0287 | 4.2406 | 147.1103 | 382.6989 | 5740.4835
2020-09-12 17:00 | 5.2283 | 5.5033 | 147.3907 | 937.9366 | 14069.0493
2020-09-12 18:00 | 6.0673 | 6.3864 | 151.3904 | 1502.4648 | 22536.9715
2020-09-12 19:00 | 6.4461 | 6.7852 | 156.447 | 1813.5461 | 27203.1918
2020-09-12 20:00 | 6.477 | 6.8176 | 162.3603 | 1839.9204 | 27598.8067
2020-09-12 21:00 | 6.4621 | 6.802 | 170.42 | 1827.2254 | 27408.3809
2020-09-12 22:00 | 6.5879 | 6.9344 | 175.9004 | 1934.7248 | 29020.872
2020-09-12 23:00 | 6.9002 | 7.2631 | 180.8217 | 2233.2365 | 33498.548
2020-09-13 00:00 | 7.0354 | 7.4055 | 186.4437 | 2365.8826 | 35488.2383
2020-09-13 01:00 | 6.9079 | 7.2712 | 194.7817 | 2240.7376 | 33611.0633
2020-09-13 02:00 | 6.6675 | 7.0181 | 204.0895 | 2004.91 | 30073.6495
2020-09-13 03:00 | 6.3005 | 6.6318 | 212.098 | 1689.0446 | 25335.6688
2020-09-13 04:00 | 6.1083 | 6.4296 | 218.7921 | 1532.7094 | 22990.641
2020-09-13 05:00 | 5.9833 | 6.298 | 221.3167 | 1440.5836 | 21608.7536
2020-09-13 06:00 | 4.8738 | 5.1301 | 230.1414 | 750.3304 | 11254.9563
2020-09-13 07:00 | 3.8434 | 4.0455 | 239.8703 | 314.0321 | 4710.4808
2020-09-13 08:00 | 3.5402 | 3.7264 | 251.7195 | 219.7562 | 3296.3432
2020-09-13 09:00 | 3.4677 | 3.6501 | 264.2317 | 197.9352 | 2969.0285
2020-09-13 10:00 | 3.4711 | 3.6536 | 257.4256 | 198.9392 | 2984.0881
2020-09-13 11:00 | 4.0721 | 4.2863 | 265.1645 | 398.7656 | 5981.484
2020-09-13 12:00 | 4.7886 | 5.0404 | 276.2212 | 705.2954 | 10579.4315
2020-09-13 13:00 | 5.0104 | 5.2739 | 280.6444 | 822.5219 | 12337.8286
2020-09-13 14:00 | 5.4589 | 5.746 | 287.075 | 1081.6452 | 16224.6782
2020-09-13 15:00 | 5.1369 | 5.407 | 291.9623 | 889.3333 | 13340.0001
2020-09-13 16:00 | 4.9072 | 5.1653 | 289.2139 | 767.9844 | 11519.766
2020-09-13 17:00 | 5.2463 | 5.5222 | 286.2721 | 949.1419 | 14237.1278
2020-09-13 18:00 | 5.9485 | 6.2613 | 288.1101 | 1414.9323 | 21223.9851
2020-09-13 19:00 | 6.9706 | 7.3372 | 300.0339 | 2302.2872 | 34534.3082
2020-09-13 20:00 | 7.484 | 7.8776 | 312.0938 | 2853.529 | 42802.9344
2020-09-13 21:00 | 7.3641 | 7.7515 | 318.735 | 2720.0406 | 40800.6091
2020-09-13 22:00 | 7.7876 | 8.1972 | 324.0626 | 3205.0102 | 48075.1532
2020-09-13 23:00 | 7.1748 | 7.5522 | 327.6731 | 2509.2319 | 37638.4788
2020-09-14 00:00 | 6.7701 | 7.1261 | 329.3319 | 2105.5601 | 31583.4022
2020-09-14 01:00 | 6.6616 | 7.0119 | 328.8366 | 1999.135 | 29987.025
2020-09-14 02:00 | 6.5042 | 6.8463 | 329.0583 | 1863.2176 | 27948.2647
2020-09-14 03:00 | 5.9571 | 6.2704 | 327.2512 | 1421.2895 | 21319.3425
2020-09-14 04:00 | 5.7106 | 6.0109 | 326.3603 | 1239.6484 | 18594.7262
2020-09-14 05:00 | 5.2667 | 5.5437 | 327.9881 | 961.8922 | 14428.3834
2020-09-14 06:00 | 3.8765 | 4.0804 | 327.0906 | 326.3005 | 4894.5081
2020-09-14 07:00 | 3.2828 | 3.4554 | 317.2182 | 145.4578 | 2181.8672
2020-09-14 08:00 | 3.8442 | 4.0464 | 306.5981 | 314.3156 | 4714.7345
2020-09-14 09:00 | 4.532 | 4.7704 | 302.1916 | 588.113 | 8821.695
2020-09-14 10:00 | 4.5835 | 4.8245 | 294.5983 | 610.9464 | 9164.1953
2020-09-14 11:00 | 5.0174 | 5.2813 | 293.4662 | 826.2123 | 12393.1847
2020-09-14 12:00 | 5.3739 | 5.6565 | 292.393 | 1028.6436 | 15429.6546
2020-09-14 13:00 | 5.7035 | 6.0035 | 290.7731 | 1234.4578 | 18516.8676
2020-09-14 14:00 | 6.106 | 6.4271 | 295.4448 | 1530.9636 | 22964.4546
2020-09-14 15:00 | 6.0465 | 6.3645 | 301.6103 | 1487.1597 | 22307.3958
2020-09-14 16:00 | 5.8469 | 6.1544 | 303.5211 | 1340.1097 | 20101.6448
2020-09-14 17:00 | 6.0178 | 6.3343 | 306.6915 | 1465.9785 | 21989.6777
2020-09-14 18:00 | 6.1239 | 6.446 | 310.3497 | 1544.1783 | 23162.6741
2020-09-14 19:00 | 6.102 | 6.4229 | 313.8991 | 1528.0323 | 22920.4848
2020-09-14 20:00 | 5.986 | 6.3008 | 317.3873 | 1442.5711 | 21638.567
2020-09-14 21:00 | 5.7536 | 6.0562 | 319.5112 | 1271.3497 | 19070.2456
2020-09-14 22:00 | 6.1553 | 6.4791 | 317.4491 | 1567.3424 | 23510.1366
2020-09-14 23:00 | 5.6502 | 5.9473 | 319.7779 | 1200.819 | 18012.285
2020-09-15 00:00 | 5.2782 | 5.5558 | 320.4196 | 969.0108 | 14535.1614
2020-09-15 01:00 | 5.0557 | 5.3216 | 317.0788 | 846.4416 | 12696.6247
2020-09-15 02:00 | 5.0133 | 5.2769 | 313.826 | 824.0252 | 12360.3786
2020-09-15 03:00 | 4.9454 | 5.2055 | 312.262 | 788.1799 | 11822.698
2020-09-15 04:00 | 4.8078 | 5.0607 | 310.6164 | 715.4678 | 10732.0172
2020-09-15 05:00 | 4.3076 | 4.5341 | 307.7136 | 488.3919 | 7325.8789
2020-09-15 06:00 | 3.0145 | 3.1731 | 304.2033 | 85.0349 | 1275.5235
2020-09-15 07:00 | 3.0008 | 3.1586 | 304.9772 | 81.9351 | 1229.0271
2020-09-15 08:00 | 3.8938 | 4.0986 | 311.4551 | 332.7116 | 4990.6739
2020-09-15 09:00 | 4.0009 | 4.2113 | 317.2214 | 372.3733 | 5585.5991
2020-09-15 10:00 | 3.7323 | 3.9286 | 316.9872 | 277.5935 | 4163.9025
2020-09-15 11:00 | 3.7806 | 3.9795 | 315.3411 | 292.1294 | 4381.9412
2020-09-15 12:00 | 3.9284 | 4.135 | 310.5594 | 345.5299 | 5182.9492
2020-09-15 13:00 | 4.0684 | 4.2824 | 311.2463 | 397.4119 | 5961.1785
2020-09-15 14:00 | 4.2371 | 4.46 | 315.4902 | 459.9095 | 6898.6426
2020-09-15 15:00 | 3.9591 | 4.1673 | 319.7989 | 356.8847 | 5353.2707
2020-09-15 16:00 | 4.0946 | 4.31 | 322.3391 | 407.1188 | 6106.7826
2020-09-15 17:00 | 4.311 | 4.5377 | 326.7222 | 489.9065 | 7348.597
2020-09-15 18:00 | 4.4006 | 4.632 | 332.7963 | 529.7156 | 7945.7338
2020-09-15 19:00 | 4.5319 | 4.7703 | 339.7209 | 588.0615 | 8820.9226
2020-09-15 20:00 | 4.5769 | 4.8177 | 349.1006 | 608.0579 | 9120.8689
2020-09-15 21:00 | 4.4176 | 4.6499 | 359.8415 | 537.2706 | 8059.0588
2020-09-15 22:00 | 3.8272 | 4.0284 | 10.0042 | 308.0132 | 4620.1981
2020-09-15 23:00 | 2.9259 | 3.0798 | 24.4362 | 65.085 | 976.2746
2020-09-16 00:00 | 1.8564 | 1.954 | 36.2037 | 0 | 0
2020-09-16 01:00 | 1.0052 | 1.0581 | 42.0134 | 0 | 0
2020-09-16 02:00 | 0.29605 | 0.31162 | 89.2351 | 0 | 0
2020-09-16 03:00 | 0.91956 | 0.96792 | 174.5048 | 0 | 0
2020-09-16 04:00 | 1.7575 | 1.8499 | 184.7307 | 0 | 0
2020-09-16 05:00 | 2.399 | 2.5252 | 188.1759 | 0 | 0
2020-09-16 06:00 | 2.688 | 2.8294 | 195.0366 | 0 | 0
2020-09-16 07:00 | 1.9544 | 2.0572 | 197.6998 | 0 | 0
2020-09-16 08:00 | 2.0743 | 2.1833 | 211.1923 | 0 | 0
2020-09-16 09:00 | 1.8747 | 1.9733 | 210.9767 | 0 | 0
2020-09-16 10:00 | 1.516 | 1.5957 | 202.7382 | 0 | 0
2020-09-16 11:00 | 1.7024 | 1.792 | 178.2157 | 0 | 0
2020-09-16 12:00 | 2.3234 | 2.4456 | 171.4568 | 0 | 0
2020-09-16 13:00 | 3.0947 | 3.2574 | 170.741 | 103.0911 | 1546.3662
2020-09-16 14:00 | 3.8991 | 4.1041 | 169.8694 | 334.6599 | 5019.8985
2020-09-16 15:00 | 4.6332 | 4.8769 | 163.81 | 633.0322 | 9495.4836
2020-09-16 16:00 | 5.9558 | 6.2691 | 163.4199 | 1420.347 | 21305.2043
2020-09-16 17:00 | 7.014 | 7.3829 | 169.1102 | 2344.833 | 35172.4956
2020-09-16 18:00 | 7.7106 | 8.1161 | 177.0095 | 3113.7742 | 46706.613
2020-09-16 19:00 | 8.0229 | 8.4448 | 185.0571 | 3483.8939 | 52258.4092
2020-09-16 20:00 | 8.2415 | 8.675 | 193.1331 | 3743.405 | 56151.0751
2020-09-16 21:00 | 8.2413 | 8.6748 | 198.7091 | 3743.1649 | 56147.4735
2020-09-16 22:00 | 8.7745 | 9.236 | 201.0575 | 4362.5035 | 65437.5518
2020-09-16 23:00 | 8.8254 | 9.2896 | 203.4648 | 4419.8902 | 66298.3532
2020-09-17 00:00 | 8.4597 | 8.9046 | 206.9551 | 4002.4225 | 60036.3368
2020-09-17 01:00 | 8.1349 | 8.5628 | 209.3543 | 3616.7843 | 54251.7648
2020-09-17 02:00 | 7.996 | 8.4165 | 208.9723 | 3452.0284 | 51780.426
2020-09-17 03:00 | 8.0367 | 8.4594 | 207.6127 | 3500.2628 | 52503.9427
2020-09-17 04:00 | 8.501 | 8.9481 | 206.1139 | 4051.4644 | 60771.9667
2020-09-17 05:00 | 8.8861 | 9.3535 | 205.2579 | 4488.2464 | 67323.6964
2020-09-17 06:00 | 9.1568 | 9.6385 | 208.5458 | 4758.8063 | 71382.0951
2020-09-17 07:00 | 8.3394 | 8.778 | 213.5444 | 3859.6032 | 57894.0475
2020-09-17 08:00 | 8.9796 | 9.4519 | 219.7175 | 4593.5376 | 68903.0645
2020-09-17 09:00 | 9.1074 | 9.5864 | 225.0662 | 4716.025 | 70740.375
2020-09-17 10:00 | 9.0991 | 9.5777 | 231.2938 | 4708.8582 | 70632.8724
2020-09-17 11:00 | 10.1195 | 10.6517 | 245.6443 | 5405.9584 | 81089.3766
2020-09-17 12:00 | 10.261 | 10.8007 | 265.2764 | 5462.8517 | 81942.7752
2020-09-17 13:00 | 9.31 | 9.7997 | 284.6017 | 4891.3336 | 73370.0033
2020-09-17 14:00 | 10.4767 | 11.0278 | 305.7402 | 5545.2739 | 83179.1084
2020-09-17 15:00 | 11.3031 | 11.8976 | 323.2716 | 5689.375 | 85340.6244
2020-09-17 16:00 | 11.1032 | 11.6872 | 330.7128 | 5669.594 | 85043.9107
2020-09-17 17:00 | 10.4567 | 11.0067 | 332.5399 | 5540.5152 | 83107.7277
2020-09-17 18:00 | 9.5902 | 10.0946 | 331.7721 | 5111.27 | 76669.0507
2020-09-17 19:00 | 8.5141 | 8.9619 | 326.8054 | 4067.0712 | 61006.0678
2020-09-17 20:00 | 7.6127 | 8.0131 | 316.2457 | 2997.7393 | 44966.0892
2020-09-17 21:00 | 7.7942 | 8.2041 | 310.7681 | 3212.8699 | 48193.0489
2020-09-17 22:00 | 9.34 | 9.8312 | 306.2393 | 4917.2798 | 73759.1976
2020-09-17 23:00 | 9.4735 | 9.9717 | 308.496 | 5032.7449 | 75491.1733
2020-09-18 00:00 | 9.4929 | 9.9921 | 308.9999 | 5049.5304 | 75742.9564
2020-09-18 01:00 | 9.327 | 9.8175 | 307.5898 | 4905.9836 | 73589.7535
2020-09-18 02:00 | 8.8447 | 9.3099 | 304.0337 | 4441.5576 | 66623.3635
2020-09-18 03:00 | 9.4723 | 9.9705 | 304.9817 | 5031.7285 | 75475.928
2020-09-18 04:00 | 9.3489 | 9.8406 | 304.7243 | 4924.991 | 73874.8657
2020-09-18 05:00 | 9.6262 | 10.1324 | 306.4482 | 5133.3443 | 77000.1643
2020-09-18 06:00 | 10.0923 | 10.6231 | 314.7197 | 5395.0316 | 80925.4744
2020-09-18 07:00 | 9.9344 | 10.4569 | 314.9444 | 5322.8496 | 79842.7437
2020-09-18 08:00 | 9.8408 | 10.3584 | 315.1385 | 5265.3073 | 78979.6098
2020-09-18 09:00 | 9.6731 | 10.1818 | 313.3933 | 5162.1768 | 77432.6524
2020-09-18 10:00 | 9.9434 | 10.4664 | 315.4903 | 5328.35 | 79925.2498
2020-09-18 11:00 | 10.4739 | 11.0248 | 318.825 | 5544.5941 | 83168.9116
2020-09-18 12:00 | 10.1073 | 10.6388 | 318.7011 | 5401.0385 | 81015.5776
2020-09-18 13:00 | 10.2578 | 10.7973 | 318.9901 | 5461.5792 | 81923.6882
2020-09-18 14:00 | 9.6151 | 10.1208 | 319.604 | 5126.5332 | 76897.9982
2020-09-18 15:00 | 8.2723 | 8.7073 | 322.1675 | 3779.8804 | 56698.2064
2020-09-18 16:00 | 8.4167 | 8.8594 | 328.4034 | 3951.4116 | 59271.1743
2020-09-18 17:00 | 7.6786 | 8.0824 | 329.4886 | 3075.812 | 46137.1797
2020-09-18 18:00 | 7.0266 | 7.3962 | 327.2875 | 2357.2656 | 35358.9838
2020-09-18 19:00 | 6.6647 | 7.0152 | 323.0567 | 2002.1886 | 30032.8286
2020-09-18 20:00 | 6.7244 | 7.0781 | 320.7144 | 2060.7579 | 30911.3691
2020-09-18 21:00 | 6.5777 | 6.9237 | 319.0423 | 1926.0223 | 28890.3348
2020-09-18 22:00 | 7.6451 | 8.0472 | 320.7341 | 3036.1761 | 45542.6421
2020-09-18 23:00 | 7.5884 | 7.9875 | 318.2165 | 2969.744 | 44546.16
2020-09-19 00:00 | 7.4153 | 7.8053 | 317.5774 | 2777.0506 | 41655.7592
2020-09-19 01:00 | 7.305 | 7.6892 | 315.5514 | 2654.1903 | 39812.8541
2020-09-19 02:00 | 6.9479 | 7.3134 | 314.2822 | 2280.0476 | 34200.7141
2020-09-19 03:00 | 6.6068 | 6.9543 | 314.4812 | 1950.8985 | 29263.4779
2020-09-19 04:00 | 6.3523 | 6.6864 | 314.1532 | 1733.3363 | 26000.0446
2020-09-19 05:00 | 5.7846 | 6.0889 | 310.6148 | 1294.2091 | 19413.1362
2020-09-19 06:00 | 4.687 | 4.9335 | 308.844 | 656.9408 | 9854.112
2020-09-19 07:00 | 4.5197 | 4.7574 | 310.3938 | 582.6209 | 8739.314
2020-09-19 08:00 | 4.5271 | 4.7652 | 312.7855 | 585.9346 | 8789.0194
2020-09-19 09:00 | 4.6988 | 4.9459 | 314.1653 | 662.1759 | 9932.6391
2020-09-19 10:00 | 4.6656 | 4.9109 | 313.0457 | 647.4207 | 9711.3101
2020-09-19 11:00 | 4.7408 | 4.9901 | 307.1724 | 680.833 | 10212.4946
2020-09-19 12:00 | 4.6966 | 4.9436 | 302.2436 | 661.2116 | 9918.1733
2020-09-19 13:00 | 4.8515 | 5.1067 | 298.5163 | 738.5631 | 11078.446
2020-09-19 14:00 | 5.1821 | 5.4547 | 296.9102 | 913.2474 | 13698.7116
2020-09-19 15:00 | 5.1945 | 5.4678 | 296.8477 | 919.8117 | 13797.1749
2020-09-19 16:00 | 5.7768 | 6.0807 | 297.4877 | 1288.4725 | 19327.0878
2020-09-19 17:00 | 6.3158 | 6.648 | 300.6562 | 1702.1423 | 25532.135
2020-09-19 18:00 | 6.7058 | 7.0585 | 308.114 | 2042.5521 | 30638.2813
2020-09-19 19:00 | 6.7458 | 7.1006 | 318.0494 | 2081.7707 | 31226.5607
2020-09-19 20:00 | 6.4145 | 6.7519 | 326.7403 | 1786.5556 | 26798.3338
2020-09-19 21:00 | 5.9653 | 6.2791 | 332.7575 | 1427.3623 | 21410.4348
2020-09-19 22:00 | 5.8755 | 6.1845 | 333.9511 | 1361.183 | 20417.7448
2020-09-19 23:00 | 5.2788 | 5.5564 | 332.4541 | 969.3825 | 14540.7374
2020-09-20 00:00 | 4.9874 | 5.2497 | 330.9048 | 810.3408 | 12155.1114
2020-09-20 01:00 | 4.8832 | 5.14 | 333.5157 | 755.2704 | 11329.0564
2020-09-20 02:00 | 4.5773 | 4.818 | 334.7992 | 608.2106 | 9123.1597
2020-09-20 03:00 | 4.3155 | 4.5424 | 333.7862 | 491.9074 | 7378.6106
2020-09-20 04:00 | 4.214 | 4.4356 | 336.0726 | 451.3386 | 6770.0791
2020-09-20 05:00 | 3.9108 | 4.1165 | 341.0408 | 339.0211 | 5085.3168
2020-09-20 06:00 | 2.52 | 2.6526 | 343.4077 | 0 | 0
2020-09-20 07:00 | 2.2033 | 2.3192 | 347.4716 | 0 | 0
2020-09-20 08:00 | 2.1589 | 2.2724 | 354.1971 | 0 | 0
2020-09-20 09:00 | 2.9621 | 3.1179 | 1.8054 | 73.2292 | 1098.4379
2020-09-20 10:00 | 2.9636 | 3.1194 | 4.6337 | 73.5606 | 1103.4094
2020-09-20 11:00 | 2.9484 | 3.1034 | 8.3893 | 70.133 | 1051.9955
2020-09-20 12:00 | 2.8225 | 2.971 | 12.2529 | 0 | 0
2020-09-20 13:00 | 2.6832 | 2.8243 | 17.3875 | 0 | 0
2020-09-20 14:00 | 2.5179 | 2.6503 | 27.1742 | 0 | 0
2020-09-20 15:00 | 2.5792 | 2.7149 | 38.5164 | 0 | 0
2020-09-20 16:00 | 2.8947 | 3.047 | 53.3777 | 58.0502 | 870.7526
2020-09-20 17:00 | 3.2697 | 3.4417 | 71.7109 | 142.5222 | 2137.8323
2020-09-20 18:00 | 3.6739 | 3.8672 | 91.6003 | 260.0085 | 3900.1277
2020-09-20 19:00 | 4.1509 | 4.3692 | 110.2237 | 427.9603 | 6419.4041
2020-09-20 20:00 | 4.7339 | 4.9829 | 124.039 | 677.7657 | 10166.4851
2020-09-20 21:00 | 5.0153 | 5.2791 | 136.5791 | 825.0856 | 12376.2836
2020-09-20 22:00 | 4.7488 | 4.9985 | 149.9021 | 684.3787 | 10265.6799
2020-09-20 23:00 | 4.4344 | 4.6677 | 158.5898 | 544.7599 | 8171.3981
2020-09-21 00:00 | 4.4359 | 4.6693 | 164.2649 | 545.4259 | 8181.3884
2020-09-21 01:00 | 4.494 | 4.7304 | 170.2919 | 571.2317 | 8568.4753
2020-09-21 02:00 | 4.8688 | 5.1249 | 180.1431 | 747.7047 | 11215.5701
2020-09-21 03:00 | 5.1938 | 5.467 | 189.3953 | 919.4347 | 13791.5211
2020-09-21 04:00 | 5.0218 | 5.286 | 198.2995 | 828.5568 | 12428.3521
2020-09-21 05:00 | 4.6407 | 4.8848 | 205.4204 | 636.3932 | 9545.8982
2020-09-21 06:00 | 3.3506 | 3.5268 | 210.1919 | 162.6747 | 2440.1209
2020-09-21 07:00 | 2.1838 | 2.2986 | 209.8233 | 0 | 0
2020-09-21 08:00 | 1.7639 | 1.8567 | 213.3399 | 0 | 0
2020-09-21 09:00 | 1.5633 | 1.6455 | 218.8568 | 0 | 0
2020-09-21 10:00 | 1.4086 | 1.4827 | 204.467 | 0 | 0
2020-09-21 11:00 | 1.0104 | 1.0635 | 206.3944 | 0 | 0
2020-09-21 12:00 | 0.86831 | 0.91398 | 196.5618 | 0 | 0
2020-09-21 13:00 | 1.3115 | 1.3805 | 189.8924 | 0 | 0
2020-09-21 14:00 | 1.7522 | 1.8444 | 191.4149 | 0 | 0
2020-09-21 15:00 | 1.869 | 1.9673 | 186.6746 | 0 | 0
2020-09-21 16:00 | 2.0282 | 2.1348 | 175.6948 | 0 | 0
2020-09-21 17:00 | 2.538 | 2.6715 | 168.3796 | 0 | 0
2020-09-21 18:00 | 3.4159 | 3.5956 | 169.4259 | 182.3351 | 2735.0258
2020-09-21 19:00 | 4.2612 | 4.4853 | 175.4915 | 468.8263 | 7032.395
2020-09-21 20:00 | 5.0109 | 5.2744 | 183.1695 | 822.7559 | 12341.3385
2020-09-21 21:00 | 5.708 | 6.0082 | 191.3869 | 1237.7671 | 18566.5069
2020-09-21 22:00 | 6.1654 | 6.4897 | 203.2917 | 1574.7577 | 23621.3656
2020-09-21 23:00 | 6.1279 | 6.4502 | 209.9313 | 1547.1153 | 23206.73
2020-09-22 00:00 | 6.0422 | 6.36 | 212.9497 | 1484.0258 | 22260.3877
2020-09-22 01:00 | 6.0396 | 6.3573 | 213.9233 | 1482.0852 | 22231.2773
2020-09-22 02:00 | 6.0245 | 6.3414 | 212.79 | 1470.9463 | 22064.1952
2020-09-22 03:00 | 6.131 | 6.4535 | 210.5598 | 1549.4504 | 23241.7559
2020-09-22 04:00 | 6.1073 | 6.4285 | 209.1628 | 1531.9325 | 22978.9874
2020-09-22 05:00 | 5.9259 | 6.2375 | 205.4732 | 1398.2629 | 20973.9435
2020-09-22 06:00 | 5.0155 | 5.2793 | 202.2455 | 825.1939 | 12377.9079
2020-09-22 07:00 | 3.7028 | 3.8975 | 198.2853 | 268.6914 | 4030.3716
2020-09-22 08:00 | 3.5978 | 3.787 | 197.6888 | 237.0808 | 3556.2117
2020-09-22 09:00 | 4.123 | 4.3399 | 200.2595 | 417.6303 | 6264.4549
2020-09-22 10:00 | 4.9097 | 5.168 | 197.0717 | 769.3178 | 11539.7667
2020-09-22 11:00 | 5.1075 | 5.3761 | 198.1208 | 873.8187 | 13107.2799
2020-09-22 12:00 | 5.141 | 5.4114 | 198.6801 | 891.5411 | 13373.1158
2020-09-22 13:00 | 4.9186 | 5.1773 | 199.3588 | 774.0054 | 11610.0805
2020-09-22 14:00 | 4.6742 | 4.92 | 196.4068 | 651.2504 | 9768.7556
2020-09-22 15:00 | 4.7004 | 4.9476 | 187.9676 | 662.8955 | 9943.4328
2020-09-22 16:00 | 5.623 | 5.9187 | 180.8975 | 1183.8965 | 17758.4471
2020-09-22 17:00 | 6.4372 | 6.7758 | 181.7009 | 1805.9128 | 27088.6925
2020-09-22 18:00 | 6.905 | 7.2681 | 184.6569 | 2237.8832 | 33568.2474
2020-09-22 19:00 | 6.8895 | 7.2518 | 187.9197 | 2222.6819 | 33340.2288
2020-09-22 20:00 | 6.9568 | 7.3227 | 190.005 | 2288.7256 | 34330.884
2020-09-22 21:00 | 6.9736 | 7.3403 | 191.7847 | 2305.1863 | 34577.7947
2020-09-22 22:00 | 7.2496 | 7.6308 | 197.634 | 2592.4317 | 38886.4748
2020-09-22 23:00 | 6.9214 | 7.2854 | 201.0654 | 2254.0167 | 33810.2509
2020-09-23 00:00 | 6.569 | 6.9145 | 200.6499 | 1918.551 | 28778.2654
2020-09-23 01:00 | 6.194 | 6.5198 | 196.5022 | 1598.0912 | 23971.3685
2020-09-23 02:00 | 5.9944 | 6.3097 | 191.1745 | 1448.7688 | 21731.5319
2020-09-23 03:00 | 6.028 | 6.345 | 187.6565 | 1473.4947 | 22102.421
2020-09-23 04:00 | 6.1203 | 6.4422 | 185.3786 | 1541.5707 | 23123.5612
2020-09-23 05:00 | 6.1743 | 6.499 | 180.5076 | 1581.3015 | 23719.5224
2020-09-23 06:00 | 5.5919 | 5.886 | 172.2028 | 1164.5278 | 17467.9176
2020-09-23 07:00 | 4.6837 | 4.93 | 168.6851 | 655.4758 | 9832.1377
2020-09-23 08:00 | 4.9564 | 5.2171 | 171.1705 | 793.9882 | 11909.8237
2020-09-23 09:00 | 6.0673 | 6.3864 | 172.4116 | 1502.4934 | 22537.4006
2020-09-23 10:00 | 6.6131 | 6.9609 | 167.8729 | 1956.2551 | 29343.8266
2020-09-23 11:00 | 6.5602 | 6.9052 | 169.0431 | 1911.0502 | 28665.7528
2020-09-23 12:00 | 6.3207 | 6.6531 | 171.1148 | 1706.3121 | 25594.6815
2020-09-23 13:00 | 5.8648 | 6.1733 | 172.5138 | 1353.3095 | 20299.6425
2020-09-23 14:00 | 5.4172 | 5.7021 | 168.5192 | 1055.6318 | 15834.4766
2020-09-23 15:00 | 5.0847 | 5.3521 | 159.8641 | 861.747 | 12926.2043
2020-09-23 16:00 | 5.6385 | 5.935 | 156.1992 | 1193.5311 | 17902.9659
2020-09-23 17:00 | 6.1039 | 6.425 | 153.7227 | 1529.4866 | 22942.2984
2020-09-23 18:00 | 6.145 | 6.4682 | 156.929 | 1559.7079 | 23395.6184
2020-09-23 19:00 | 5.867 | 6.1756 | 162.6011 | 1354.9079 | 20323.6184
2020-09-23 20:00 | 5.7366 | 6.0383 | 163.355 | 1258.8368 | 18882.5525
2020-09-23 21:00 | 5.7021 | 6.002 | 160.9294 | 1233.4328 | 18501.4916
2020-09-23 22:00 | 5.7167 | 6.0174 | 169.753 | 1244.1923 | 18662.8838
2020-09-23 23:00 | 5.2898 | 5.568 | 169.3302 | 976.2786 | 14644.179
2020-09-24 00:00 | 4.9736 | 5.2352 | 163.2844 | 803.0579 | 12045.8679
2020-09-24 01:00 | 5.0137 | 5.2773 | 155.8196 | 824.2295 | 12363.4423
2020-09-24 02:00 | 5.308 | 5.5872 | 151.8901 | 987.6092 | 14814.1373
2020-09-24 03:00 | 5.8145 | 6.1203 | 152.6676 | 1316.2201 | 19743.3017
2020-09-24 04:00 | 6.0767 | 6.3962 | 154.4073 | 1509.3744 | 22640.6153
2020-09-24 05:00 | 6.0979 | 6.4186 | 157.8193 | 1525.0507 | 22875.7607
2020-09-24 06:00 | 5.2537 | 5.53 | 163.6651 | 953.7473 | 14306.2102
2020-09-24 07:00 | 3.793 | 3.9925 | 160.685 | 295.8538 | 4437.8076
2020-09-24 08:00 | 3.848 | 4.0504 | 154.1181 | 315.7322 | 4735.9827
2020-09-24 09:00 | 4.431 | 4.6641 | 158.7375 | 543.2366 | 8148.5493
2020-09-24 10:00 | 4.6383 | 4.8823 | 161.7358 | 635.3113 | 9529.67
2020-09-24 11:00 | 4.9172 | 5.1758 | 165.9058 | 773.2548 | 11598.8222
2020-09-24 12:00 | 4.8211 | 5.0747 | 165.0354 | 722.4962 | 10837.4431
2020-09-24 13:00 | 4.6385 | 4.8824 | 165.0033 | 635.3907 | 9530.8603
2020-09-24 14:00 | 4.3389 | 4.5671 | 160.6816 | 502.3347 | 7535.0212
2020-09-24 15:00 | 4.2006 | 4.4215 | 153.5586 | 446.381 | 6695.7152
2020-09-24 16:00 | 4.6396 | 4.8837 | 151.3028 | 635.902 | 9538.5306
2020-09-24 17:00 | 5.0809 | 5.3481 | 157.4181 | 859.7544 | 12896.3159
2020-09-24 18:00 | 5.3125 | 5.5919 | 160.9779 | 990.3897 | 14855.845
2020-09-24 19:00 | 5.4178 | 5.7027 | 164.8912 | 1056.0026 | 15840.0392
2020-09-24 20:00 | 5.1945 | 5.4677 | 167.7258 | 919.8029 | 13797.0431
2020-09-24 21:00 | 5.2224 | 5.4971 | 169.02 | 934.5228 | 14017.8423
2020-09-24 22:00 | 5.1313 | 5.4012 | 172.1575 | 886.379 | 13295.6845
2020-09-24 23:00 | 5.2106 | 5.4846 | 169.5899 | 928.2781 | 13924.1719
2020-09-25 00:00 | 5.2267 | 5.5016 | 170.7966 | 936.9699 | 14054.549
2020-09-25 01:00 | 5.2542 | 5.5306 | 168.4922 | 954.109 | 14311.6356
2020-09-25 02:00 | 5.3537 | 5.6353 | 164.8818 | 1016.085 | 15241.2744
2020-09-25 03:00 | 5.5151 | 5.8052 | 167.0631 | 1116.6641 | 16749.9622
2020-09-25 04:00 | 5.5674 | 5.8602 | 169.2826 | 1149.2513 | 17238.7691
2020-09-25 05:00 | 5.5051 | 5.7947 | 169.1158 | 1110.4543 | 16656.8147
2020-09-25 06:00 | 4.8065 | 5.0593 | 164.9802 | 714.7727 | 10721.5901
2020-09-25 07:00 | 3.5525 | 3.7393 | 152.4102 | 223.4507 | 3351.7607
2020-09-25 08:00 | 3.9978 | 4.2081 | 143.7708 | 371.2345 | 5568.5171
2020-09-25 09:00 | 5.0491 | 5.3147 | 144.1837 | 842.9759 | 12644.6382
2020-09-25 10:00 | 6.2673 | 6.5969 | 151.4852 | 1660.6871 | 24910.307
2020-09-25 11:00 | 6.8194 | 7.1781 | 151.4412 | 2153.9952 | 32309.9284
2020-09-25 12:00 | 7.0341 | 7.404 | 151.1688 | 2364.5489 | 35468.2333
2020-09-25 13:00 | 7.1567 | 7.5331 | 151.8611 | 2489.0371 | 37335.556
2020-09-25 14:00 | 6.6861 | 7.0378 | 148.2465 | 2023.2314 | 30348.4717
2020-09-25 15:00 | 6.1943 | 6.52 | 149.0802 | 1598.2787 | 23974.1811
2020-09-25 16:00 | 6.6202 | 6.9684 | 141.5975 | 1962.3167 | 29434.751
2020-09-25 17:00 | 7.4326 | 7.8235 | 138.3777 | 2796.2572 | 41943.8579
2020-09-25 18:00 | 7.842 | 8.2544 | 141.9134 | 3269.4956 | 49042.4335
2020-09-25 19:00 | 7.8889 | 8.3039 | 147.1948 | 3325.1506 | 49877.2586
2020-09-25 20:00 | 7.8942 | 8.3094 | 150.2561 | 3331.4215 | 49971.323
2020-09-25 21:00 | 7.9948 | 8.4153 | 150.9575 | 3450.6134 | 51759.201
2020-09-25 22:00 | 8.2325 | 8.6655 | 156.4619 | 3732.6536 | 55989.8035
2020-09-25 23:00 | 8.0114 | 8.4327 | 153.4588 | 3470.2346 | 52053.5184
2020-09-26 00:00 | 8.0047 | 8.4257 | 149.9037 | 3462.3814 | 51935.7217
2020-09-26 01:00 | 8.1583 | 8.5874 | 146.6041 | 3644.5771 | 54668.6558
2020-09-26 02:00 | 8.4724 | 8.918 | 142.8339 | 4017.5362 | 60263.0435
2020-09-26 03:00 | 8.8491 | 9.3145 | 140.0352 | 4446.49 | 66697.3499
2020-09-26 04:00 | 9.1992 | 9.6831 | 136.2007 | 4795.4854 | 71932.2803
2020-09-26 05:00 | 9.2462 | 9.7325 | 133.773 | 4836.1068 | 72541.6017
2020-09-26 06:00 | 8.3445 | 8.7834 | 132.3793 | 3865.683 | 57985.2454
2020-09-26 07:00 | 7.9176 | 8.3341 | 130.0871 | 3359.1597 | 50387.3951
2020-09-26 08:00 | 8.5392 | 8.9884 | 126.2198 | 4096.8642 | 61452.963
2020-09-26 09:00 | 9.3828 | 9.8763 | 125.0618 | 4954.2899 | 74314.3486
2020-09-26 10:00 | 10.2995 | 10.8412 | 130.0451 | 5478.355 | 82175.3254
2020-09-26 11:00 | 10.8215 | 11.3907 | 137.5238 | 5627.2968 | 84409.452
2020-09-26 12:00 | 11.4117 | 12.0119 | 140.4357 | 5699.0238 | 85485.3565
2020-09-26 13:00 | 11.45 | 12.0522 | 141.564 | 5699.1044 | 85486.5654
2020-09-26 14:00 | 10.8083 | 11.3768 | 144.2947 | 5624.1561 | 84362.3411
2020-09-26 15:00 | 9.2407 | 9.7267 | 133.8084 | 4831.3434 | 72470.1512
2020-09-26 16:00 | 9.4431 | 9.9398 | 121.7098 | 5006.5103 | 75097.655
2020-09-26 17:00 | 10.3872 | 10.9335 | 112.9533 | 5513.6078 | 82704.1163
2020-09-26 18:00 | 11.3795 | 11.978 | 112.117 | 5696.9335 | 85454.002
2020-09-26 19:00 | 11.6923 | 12.3072 | 115.3831 | 5699.6145 | 85494.2172
2020-09-26 20:00 | 11.6539 | 12.2668 | 120.2163 | 5699.5337 | 85493.0051
2020-09-26 21:00 | 11.6999 | 12.3153 | 125.0496 | 5699.6306 | 85494.4584
2020-09-26 22:00 | 12.846 | 13.5216 | 134.1079 | 5700 | 85500
2020-09-26 23:00 | 12.0474 | 12.6811 | 133.9852 | 5700 | 85500
2020-09-27 00:00 | 10.8874 | 11.46 | 131.8049 | 5642.9583 | 84644.3752
2020-09-27 01:00 | 10.5547 | 11.1098 | 126.1098 | 5563.8152 | 83457.2279
2020-09-27 02:00 | 10.5995 | 11.1569 | 120.8375 | 5574.4691 | 83617.0368
2020-09-27 03:00 | 11.0636 | 11.6454 | 116.8144 | 5665.6715 | 84985.0724
2020-09-27 04:00 | 11.334 | 11.9301 | 119.1436 | 5692.4253 | 85386.38
2020-09-27 05:00 | 11.6251 | 12.2365 | 118.4077 | 5699.473 | 85492.0948
2020-09-27 06:00 | 11.869 | 12.4932 | 117.9416 | 5699.9865 | 85499.7969
2020-09-27 07:00 | 11.579 | 12.188 | 115.1312 | 5699.376 | 85490.6395
2020-09-27 08:00 | 11.825 | 12.4469 | 118.7301 | 5699.8939 | 85498.4079
2020-09-27 09:00 | 11.7883 | 12.4083 | 120.1627 | 5699.8165 | 85497.2482
2020-09-27 10:00 | 10.4163 | 10.9641 | 130.0913 | 5525.2948 | 82879.4216
2020-09-27 11:00 | 9.5449 | 10.047 | 156.04 | 5083.4197 | 76251.2951
2020-09-27 12:00 | 7.4876 | 7.8814 | 177.9329 | 2857.5119 | 42862.6781
2020-09-27 13:00 | 7.0393 | 7.4095 | 193.3246 | 2369.672 | 35545.0797
2020-09-27 14:00 | 8.2857 | 8.7215 | 222.7655 | 3795.8393 | 56937.5888
2020-09-27 15:00 | 9.1948 | 9.6784 | 256.0533 | 4791.6398 | 71874.5974
2020-09-27 16:00 | 8.0875 | 8.5129 | 270.5407 | 3560.5443 | 53408.164
2020-09-27 17:00 | 6.3204 | 6.6529 | 269.3234 | 1706.1169 | 25591.7539
2020-09-27 18:00 | 5.5536 | 5.8457 | 264.4429 | 1140.6275 | 17109.4127
2020-09-27 19:00 | 5.8975 | 6.2077 | 259.911 | 1377.3621 | 20660.431
2020-09-27 20:00 | 6.7531 | 7.1083 | 256.5578 | 2088.9155 | 31333.732
2020-09-27 21:00 | 6.7281 | 7.0819 | 257.4711 | 2064.3475 | 30965.2131
2020-09-27 22:00 | 5.4255 | 5.7109 | 262.844 | 1060.8246 | 15912.369
2020-09-27 23:00 | 4.6052 | 4.8474 | 257.1388 | 620.6083 | 9309.1251
2020-09-28 00:00 | 3.9947 | 4.2048 | 247.8407 | 370.1014 | 5551.5211
2020-09-28 01:00 | 3.8644 | 4.0677 | 241.0139 | 321.8265 | 4827.3976
2020-09-28 02:00 | 3.5162 | 3.7011 | 241.1486 | 212.5217 | 3187.8261
2020-09-28 03:00 | 2.6415 | 2.7804 | 230.4018 | 0 | 0
2020-09-28 04:00 | 3.0326 | 3.1921 | 214.4431 | 89.1 | 1336.5
2020-09-28 05:00 | 2.969 | 3.1252 | 203.368 | 74.7846 | 1121.7687
2020-09-28 06:00 | 3.0497 | 3.2101 | 188.1988 | 92.9527 | 1394.2906
2020-09-28 07:00 | 3.4355 | 3.6162 | 177.8542 | 188.2343 | 2823.5152
2020-09-28 08:00 | 4.2027 | 4.4238 | 173.7733 | 447.1662 | 6707.493
2020-09-28 09:00 | 4.4163 | 4.6486 | 174.4227 | 536.715 | 8050.7255
2020-09-28 10:00 | 4.0713 | 4.2855 | 175.1431 | 398.4842 | 5977.2636
2020-09-28 11:00 | 3.7811 | 3.9799 | 172.8366 | 292.2563 | 4383.8445
2020-09-28 12:00 | 3.7284 | 3.9245 | 157.6429 | 276.4034 | 4146.0514
2020-09-28 13:00 | 4.2043 | 4.4254 | 145.5735 | 447.7486 | 6716.2283
2020-09-28 14:00 | 5.1064 | 5.375 | 152.8711 | 873.2392 | 13098.5885
2020-09-28 15:00 | 4.6019 | 4.844 | 125.1039 | 619.1564 | 9287.3467
2020-09-28 16:00 | 6.0258 | 6.3427 | 99.5217 | 1471.894 | 22078.4101
2020-09-28 17:00 | 7.7273 | 8.1337 | 94.2434 | 3133.5792 | 47003.6877
2020-09-28 18:00 | 8.5706 | 9.0214 | 99.0255 | 4132.8551 | 61992.8263
2020-09-28 19:00 | 8.6961 | 9.1534 | 104.3062 | 4274.1893 | 64112.8397
2020-09-28 20:00 | 8.5029 | 8.9501 | 109.4049 | 4053.7129 | 60805.6941
2020-09-28 21:00 | 7.9914 | 8.4117 | 115.657 | 3446.5693 | 51698.539
2020-09-28 22:00 | 7.4006 | 7.7898 | 122.3631 | 2760.6372 | 41409.5576
2020-09-28 23:00 | 7.2235 | 7.6034 | 118.632 | 2563.4361 | 38451.5411
2020-09-29 00:00 | 6.618 | 6.966 | 115.1158 | 1960.4324 | 29406.4867
2020-09-29 01:00 | 6.95 | 7.3155 | 107.8829 | 2282.0849 | 34231.2742
2020-09-29 02:00 | 7.4193 | 7.8095 | 104.3381 | 2781.4715 | 41722.0727
2020-09-29 03:00 | 7.6531 | 8.0557 | 104.0326 | 3045.6703 | 45685.0552
2020-09-29 04:00 | 7.5749 | 7.9733 | 104.8234 | 2954.6986 | 44320.4788
2020-09-29 05:00 | 7.3415 | 7.7277 | 103.0676 | 2694.8592 | 40422.8887
2020-09-29 06:00 | 7.5002 | 7.8946 | 100.0691 | 2871.5374 | 43073.061
2020-09-29 07:00 | 6.2478 | 6.5764 | 98.8403 | 1644.0549 | 24660.8239
2020-09-29 08:00 | 5.8729 | 6.1818 | 99.41 | 1359.2454 | 20388.6806
2020-09-29 09:00 | 5.6648 | 5.9627 | 97.4478 | 1209.9287 | 18148.9306
2020-09-29 10:00 | 5.5137 | 5.8037 | 91.7779 | 1115.8145 | 16737.218
2020-09-29 11:00 | 6.3816 | 6.7173 | 103.5046 | 1758.4233 | 26376.35
2020-09-29 12:00 | 6.2872 | 6.6179 | 108.7582 | 1677.698 | 25165.4693
2020-09-29 13:00 | 5.711 | 6.0114 | 102.9229 | 1239.9642 | 18599.4635
2020-09-29 14:00 | 6.768 | 7.1239 | 90.5657 | 2103.5156 | 31552.734
2020-09-29 15:00 | 7.9811 | 8.4008 | 82.5891 | 3434.3325 | 51514.9875
2020-09-29 16:00 | 9.0727 | 9.5499 | 81.8957 | 4686.0202 | 70290.3023
2020-09-29 17:00 | 9.8575 | 10.376 | 80.4822 | 5275.5721 | 79133.5813
2020-09-29 18:00 | 10.5871 | 11.144 | 82.5028 | 5571.5385 | 83573.0781
2020-09-29 19:00 | 9.9933 | 10.5189 | 89.4177 | 5355.2291 | 80328.4369
2020-09-29 20:00 | 9.5602 | 10.0631 | 89.2137 | 5092.8261 | 76392.392
2020-09-29 21:00 | 9.4122 | 9.9073 | 89.2527 | 4979.7773 | 74696.6591
2020-09-29 22:00 | 9.3682 | 9.8609 | 92.3339 | 4941.6729 | 74125.0937
2020-09-29 23:00 | 8.9236 | 9.393 | 97.967 | 4530.4649 | 67956.9734
2020-09-30 00:00 | 8.2762 | 8.7115 | 96.2196 | 3784.5438 | 56768.1572
2020-09-30 01:00 | 7.9935 | 8.4139 | 92.6049 | 3449.0559 | 51735.8389
2020-09-30 02:00 | 7.7528 | 8.1606 | 87.1208 | 3163.783 | 47456.745
2020-09-30 03:00 | 8.0913 | 8.5168 | 83.8454 | 3564.9613 | 53474.4191
2020-09-30 04:00 | 8.2482 | 8.6821 | 82.3373 | 3751.362 | 56270.4294
2020-09-30 05:00 | 8.5265 | 8.975 | 83.3781 | 4081.8 | 61226.9997
2020-09-30 06:00 | 8.739 | 9.1987 | 83.1381 | 4322.5674 | 64838.5108
2020-09-30 07:00 | 9.1443 | 9.6253 | 83.5646 | 4747.9913 | 71219.8694
2020-09-30 08:00 | 9.7698 | 10.2837 | 87.6726 | 5221.6599 | 78324.8981
2020-09-30 09:00 | 9.5133 | 10.0137 | 92.6831 | 5063.979 | 75959.6846
2020-09-30 10:00 | 8.3337 | 8.772 | 97.9563 | 3852.8071 | 57792.1069
2020-09-30 11:00 | 7.7719 | 8.1807 | 97.5246 | 3186.4739 | 47797.1088
2020-09-30 12:00 | 7.4016 | 7.7909 | 92.5653 | 2761.7874 | 41426.8108
2020-09-30 13:00 | 8.0059 | 8.427 | 91.3427 | 3463.7546 | 51956.3183
2020-09-30 14:00 | 8.3661 | 8.8061 | 86.6561 | 3891.3087 | 58369.6306
2020-09-30 15:00 | 7.5716 | 7.9698 | 85.4205 | 2951.0548 | 44265.8225
2020-09-30 16:00 | 7.9834 | 8.4032 | 85.7226 | 3437.0471 | 51555.7059
2020-09-30 17:00 | 8.0802 | 8.5052 | 83.6185 | 3551.858 | 53277.8697
2020-09-30 18:00 | 7.7895 | 8.1992 | 82.7651 | 3207.2968 | 48109.4518
2020-09-30 19:00 | 7.5235 | 7.9192 | 78.1046 | 2897.4927 | 43462.3902
2020-09-30 20:00 | 7.3274 | 7.7128 | 71.1841 | 2679.1231 | 40186.8464
2020-09-30 21:00 | 7.6264 | 8.0275 | 67.0256 | 3013.9715 | 45209.5718
2020-09-30 22:00 | 7.4927 | 7.8868 | 69.2056 | 2863.201 | 42948.0149
2020-09-30 23:00 | 7.7726 | 8.1814 | 61.6543 | 3187.2067 | 47808.1006
2020-10-01 00:00 | 8.4742 | 8.9199 | 60.1938 | 4019.6698 | 60295.0477
2020-10-01 01:00 | 9.3521 | 9.844 | 68.1792 | 4927.7799 | 73916.6987
2020-10-01 02:00 | 10.0014 | 10.5274 | 88.9235 | 5358.4616 | 80376.9234
2020-10-01 03:00 | 10.1358 | 10.6689 | 123.5397 | 5412.5247 | 81187.8704
2020-10-01 04:00 | 11.4835 | 12.0875 | 146.3986 | 5699.175 | 85487.6248
2020-10-01 05:00 | 10.7982 | 11.3662 | 145.4476 | 5621.7533 | 84326.3
2020-10-01 06:00 | 10.3946 | 10.9413 | 138.155 | 5516.5591 | 82748.386
2020-10-01 07:00 | 9.0913 | 9.5694 | 128.9351 | 4702.064 | 70530.9599
2020-10-01 08:00 | 8.8898 | 9.3573 | 121.8336 | 4492.3488 | 67385.2316
2020-10-01 09:00 | 9.7757 | 10.2899 | 124.5212 | 5225.2862 | 78379.2925
2020-10-01 10:00 | 9.201 | 9.6849 | 113.284 | 4797.0099 | 71955.1485
2020-10-01 11:00 | 8.8952 | 9.3631 | 113.3246 | 4498.4783 | 67477.1742
2020-10-01 12:00 | 8.8519 | 9.3175 | 115.9656 | 4449.7188 | 66745.7819
2020-10-01 13:00 | 8.4438 | 8.8879 | 111.2952 | 3983.5971 | 59753.9562
2020-10-01 14:00 | 8.8337 | 9.2983 | 106.5822 | 4429.1392 | 66437.0883
2020-10-01 15:00 | 9.4246 | 9.9203 | 104.7555 | 4990.4541 | 74856.8121
2020-10-01 16:00 | 9.3605 | 9.8528 | 111.485 | 4934.9805 | 74024.7074
2020-10-01 17:00 | 9.4538 | 9.9511 | 116.5515 | 5015.7748 | 75236.622
2020-10-01 18:00 | 9.0461 | 9.5218 | 115.5209 | 4662.9525 | 69944.2873
2020-10-01 19:00 | 8.5686 | 9.0192 | 114.1931 | 4130.5639 | 61958.4586
2020-10-01 20:00 | 8.4249 | 8.868 | 114.2394 | 3961.07 | 59416.0493
2020-10-01 21:00 | 8.0024 | 8.4233 | 114.5485 | 3459.584 | 51893.7601
2020-10-01 22:00 | 8.1516 | 8.5803 | 120.6701 | 3636.6305 | 54549.4571
2020-10-01 23:00 | 8.022 | 8.4439 | 120.4696 | 3482.856 | 52242.8403
2020-10-02 00:00 | 7.4936 | 7.8877 | 120.8811 | 2864.2261 | 42963.3915
2020-10-02 01:00 | 6.8805 | 7.2423 | 116.1434 | 2213.8521 | 33207.7817
2020-10-02 02:00 | 6.8621 | 7.223 | 116.2623 | 2195.8293 | 32937.4394
2020-10-02 03:00 | 6.8106 | 7.1688 | 117.5234 | 2145.2901 | 32179.3513
2020-10-02 04:00 | 6.7519 | 7.107 | 119.226 | 2087.6931 | 31315.3969
2020-10-02 05:00 | 6.6151 | 6.9631 | 118.1918 | 1957.997 | 29369.9549
2020-10-02 06:00 | 6.7229 | 7.0765 | 113.753 | 2059.3118 | 30889.6765
2020-10-02 07:00 | 6.9001 | 7.263 | 111.8848 | 2233.1274 | 33496.9108
2020-10-02 08:00 | 7.1237 | 7.4983 | 112.4417 | 2452.4468 | 36786.7026
2020-10-02 09:00 | 7.2029 | 7.5817 | 117.0853 | 2540.469 | 38107.0343
2020-10-02 10:00 | 6.4166 | 6.7541 | 116.3906 | 1788.3285 | 26824.927
2020-10-02 11:00 | 7.1772 | 7.5547 | 116.8129 | 2511.8291 | 37677.4369
2020-10-02 12:00 | 6.5511 | 6.8956 | 118.7624 | 1903.2546 | 28548.8185
2020-10-02 13:00 | 6.5265 | 6.8697 | 120.4942 | 1882.2171 | 28233.256
2020-10-02 14:00 | 6.1827 | 6.5079 | 122.521 | 1588.4352 | 23826.5287
2020-10-02 15:00 | 6.9854 | 7.3528 | 126.1407 | 2316.803 | 34752.0454
2020-10-02 16:00 | 6.5609 | 6.906 | 122.0631 | 1911.6553 | 28674.8299
2020-10-02 17:00 | 6.8025 | 7.1603 | 122.1137 | 2137.4194 | 32061.2916
2020-10-02 18:00 | 6.5272 | 6.8705 | 126.563 | 1882.8392 | 28242.5885
2020-10-02 19:00 | 6.3377 | 6.671 | 131.9081 | 1720.8842 | 25813.2635
2020-10-02 20:00 | 6.3998 | 6.7363 | 133.8709 | 1773.9117 | 26608.6756
2020-10-02 21:00 | 6.3495 | 6.6834 | 136.1955 | 1730.946 | 25964.1893
2020-10-02 22:00 | 6.4882 | 6.8294 | 143.5087 | 1849.509 | 27742.6349
2020-10-02 23:00 | 6.2339 | 6.5618 | 144.9954 | 1632.183 | 24482.7456
2020-10-03 00:00 | 5.9375 | 6.2497 | 146.0399 | 1406.8135 | 21102.203
2020-10-03 01:00 | 5.6016 | 5.8962 | 143.3269 | 1170.5331 | 17557.9961
2020-10-03 02:00 | 5.3074 | 5.5865 | 142.3528 | 987.2115 | 14808.1732
2020-10-03 03:00 | 5.2958 | 5.5743 | 142.5053 | 980.0121 | 14700.1816
2020-10-03 04:00 | 5.5426 | 5.8342 | 134.5581 | 1133.8244 | 17007.3666
2020-10-03 05:00 | 6.2722 | 6.602 | 131.2107 | 1664.8503 | 24972.7544
2020-10-03 06:00 | 5.7686 | 6.072 | 133.385 | 1282.3947 | 19235.9202
2020-10-03 07:00 | 6.2788 | 6.6091 | 132.5538 | 1670.5627 | 25058.4402
2020-10-03 08:00 | 6.1049 | 6.426 | 131.1261 | 1530.206 | 22953.0896
2020-10-03 09:00 | 6.033 | 6.3503 | 132.3585 | 1477.206 | 22158.0903
2020-10-03 10:00 | 6.5112 | 6.8537 | 139.6596 | 1869.2057 | 28038.0857
2020-10-03 11:00 | 7.2799 | 7.6628 | 139.5085 | 2626.2596 | 39393.8933
2020-10-03 12:00 | 7.7639 | 8.1722 | 138.0852 | 3176.8895 | 47653.3424
2020-10-03 13:00 | 7.791 | 8.2008 | 132.8134 | 3209.1136 | 48136.7038
2020-10-03 14:00 | 7.8 | 8.2102 | 126.694 | 3219.7026 | 48295.5391
2020-10-03 15:00 | 8.4527 | 8.8972 | 123.8224 | 3994.0815 | 59911.2232
2020-10-03 16:00 | 9.0784 | 9.5558 | 125.3782 | 4690.8924 | 70363.3853
2020-10-03 17:00 | 9.4495 | 9.9465 | 129.7561 | 5012.0533 | 75180.8002
2020-10-03 18:00 | 9.5408 | 10.0426 | 134.7922 | 5080.8975 | 76213.4621
2020-10-03 19:00 | 9.6898 | 10.1995 | 137.2665 | 5172.4977 | 77587.466
2020-10-03 20:00 | 9.622 | 10.1281 | 142.3679 | 5130.7902 | 76961.853
2020-10-03 21:00 | 9.4529 | 9.95 | 148.5731 | 5014.9312 | 75223.9681
2020-10-03 22:00 | 9.9959 | 10.5217 | 152.4072 | 5356.2791 | 80344.1872
2020-10-03 23:00 | 9.7073 | 10.2179 | 155.7018 | 5183.2497 | 77748.7449
2020-10-04 00:00 | 9.3499 | 9.8416 | 158.803 | 4925.829 | 73887.4351
2020-10-04 01:00 | 9.2168 | 9.7016 | 158.4066 | 4810.7104 | 72160.656
2020-10-04 02:00 | 9.2361 | 9.7219 | 155.6552 | 4827.41 | 72411.1497
2020-10-04 03:00 | 9.463 | 9.9607 | 151.1967 | 5023.6921 | 75355.3817
2020-10-04 04:00 | 9.8396 | 10.3571 | 147.4834 | 5264.5313 | 78967.969
2020-10-04 05:00 | 9.8881 | 10.4081 | 148.5295 | 5294.3374 | 79415.0614
2020-10-04 06:00 | 9.7418 | 10.2541 | 145.6526 | 5204.4053 | 78066.08
2020-10-04 07:00 | 12.1175 | 12.7548 | 149.5943 | 5700 | 85500
2020-10-04 08:00 | 12.4401 | 13.0944 | 151.2189 | 5700 | 85500
2020-10-04 09:00 | 12.2167 | 12.8592 | 148.9399 | 5700 | 85500
2020-10-04 10:00 | 13.1151 | 13.8049 | 162.696 | 5700 | 85500
2020-10-04 11:00 | 12.1387 | 12.7771 | 168.0932 | 5700 | 85500
2020-10-04 12:00 | 10.3771 | 10.9229 | 162.5175 | 5509.5314 | 82642.9708
2020-10-04 13:00 | 9.8323 | 10.3495 | 154.7022 | 5260.0863 | 78901.2949
2020-10-04 14:00 | 10.1901 | 10.726 | 150.6104 | 5434.3403 | 81515.1039
2020-10-04 15:00 | 10.4291 | 10.9776 | 146.683 | 5530.4617 | 82956.9254
2020-10-04 16:00 | 10.6116 | 11.1697 | 144.7522 | 5577.3575 | 83660.363
2020-10-04 17:00 | 10.2381 | 10.7765 | 146.3744 | 5453.6375 | 81804.5625
2020-10-04 18:00 | 9.6787 | 10.1877 | 150.8453 | 5165.6247 | 77484.3705
2020-10-04 19:00 | 9.2211 | 9.7061 | 153.4231 | 4814.4262 | 72216.3928
2020-10-04 20:00 | 9.4761 | 9.9745 | 151.1623 | 5035.0359 | 75525.538
2020-10-04 21:00 | 9.8328 | 10.35 | 150.8103 | 5260.3847 | 78905.7703
2020-10-04 22:00 | 9.508 | 10.0081 | 151.3283 | 5060.7351 | 75911.0264
2020-10-04 23:00 | 9.3049 | 9.7943 | 152.7847 | 4886.9358 | 73304.0369
2020-10-05 00:00 | 9.2528 | 9.7394 | 151.398 | 4841.8096 | 72627.1435
2020-10-05 01:00 | 9.4167 | 9.912 | 149.4367 | 4983.6644 | 74754.9656
2020-10-05 02:00 | 9.8071 | 10.3229 | 147.1455 | 5244.5515 | 78668.2727
2020-10-05 03:00 | 10.0339 | 10.5616 | 146.3838 | 5371.5433 | 80573.1501
2020-10-05 04:00 | 10.1146 | 10.6466 | 144.8648 | 5403.9858 | 81059.7877
2020-10-05 05:00 | 9.8765 | 10.3959 | 144.7077 | 5287.2132 | 79308.1976
2020-10-05 06:00 | 9.9432 | 10.4661 | 141.2159 | 5328.2112 | 79923.1685
2020-10-05 07:00 | 9.6359 | 10.1427 | 140.306 | 5139.3499 | 77090.249
2020-10-05 08:00 | 9.9236 | 10.4455 | 141.7191 | 5316.1879 | 79742.818
2020-10-05 09:00 | 10.0642 | 10.5935 | 142.2277 | 5383.7281 | 80755.9208
2020-10-05 10:00 | 9.7522 | 10.2651 | 136.2261 | 5210.8162 | 78162.2424
2020-10-05 11:00 | 10.2121 | 10.7492 | 137.4774 | 5443.1982 | 81647.9733
2020-10-05 12:00 | 10.6929 | 11.2553 | 142.6689 | 5596.7026 | 83950.5384
2020-10-05 13:00 | 10.8193 | 11.3883 | 149.5366 | 5626.7597 | 84401.3962
2020-10-05 14:00 | 10.0277 | 10.5552 | 152.0673 | 5369.0682 | 80536.0235
2020-10-05 15:00 | 9.5059 | 10.0059 | 154.358 | 5059.4433 | 75891.6496
2020-10-05 16:00 | 9.5793 | 10.0831 | 149.6397 | 5104.5236 | 76567.8536
2020-10-05 17:00 | 10.3795 | 10.9254 | 145.821 | 5510.4962 | 82657.4426
2020-10-05 18:00 | 10.8373 | 11.4073 | 150.8941 | 5631.0565 | 84465.8474
2020-10-05 19:00 | 11.0853 | 11.6683 | 152.886 | 5667.8186 | 85017.2797
2020-10-05 20:00 | 11.137 | 11.7227 | 155.6345 | 5672.9379 | 85094.0683
2020-10-05 21:00 | 11.1208 | 11.7057 | 157.2467 | 5671.3313 | 85069.9691
2020-10-05 22:00 | 11.3188 | 11.9141 | 161.9945 | 5690.9259 | 85363.8892
2020-10-05 23:00 | 10.8644 | 11.4358 | 164.7884 | 5637.4893 | 84562.3397
2020-10-06 00:00 | 10.2489 | 10.7879 | 167.7598 | 5457.9851 | 81869.7763
2020-10-06 01:00 | 9.623 | 10.1291 | 171.6369 | 5131.4081 | 76971.1216
2020-10-06 02:00 | 9.1731 | 9.6556 | 170.0907 | 4772.8721 | 71593.081
2020-10-06 03:00 | 8.9917 | 9.4646 | 166.4952 | 4607.0907 | 69106.3598
2020-10-06 04:00 | 8.7743 | 9.2358 | 161.3639 | 4362.322 | 65434.8296
2020-10-06 05:00 | 8.3324 | 8.7706 | 168.1928 | 3851.2395 | 57768.5921
2020-10-06 06:00 | 8.0511 | 8.4746 | 171.4316 | 3517.3777 | 52760.665
2020-10-06 07:00 | 7.9348 | 8.3522 | 160.8744 | 3379.5445 | 50693.1669
2020-10-06 08:00 | 7.8877 | 8.3026 | 156.4748 | 3323.7011 | 49855.5168
2020-10-06 09:00 | 7.6237 | 8.0246 | 159.4419 | 3010.7156 | 45160.7342
2020-10-06 10:00 | 6.913 | 7.2766 | 158.0899 | 2245.8133 | 33687.1999
2020-10-06 11:00 | 6.4218 | 6.7595 | 153.4587 | 1792.7303 | 26890.9541
2020-10-06 12:00 | 6.7644 | 7.1201 | 148.4945 | 2099.964 | 31499.4596
2020-10-06 13:00 | 7.0185 | 7.3877 | 141.4458 | 2349.2988 | 35239.4824
2020-10-06 14:00 | 7.6269 | 8.028 | 141.5489 | 3014.5265 | 45217.8975
2020-10-06 15:00 | 8.154 | 8.5829 | 137.5075 | 3639.4927 | 54592.3903
2020-10-06 16:00 | 8.0396 | 8.4625 | 134.0637 | 3503.7337 | 52556.005
2020-10-06 17:00 | 7.8544 | 8.2675 | 135.855 | 3284.1955 | 49262.9326
2020-10-06 18:00 | 8.0521 | 8.4756 | 148.8511 | 3518.5771 | 52778.6564
2020-10-06 19:00 | 8.7984 | 9.2612 | 165.7284 | 4389.4707 | 65842.0609
2020-10-06 20:00 | 8.5522 | 9.002 | 181.1034 | 4112.1732 | 61682.5986
2020-10-06 21:00 | 7.8974 | 8.3128 | 192.29 | 3335.2254 | 50028.3812
2020-10-06 22:00 | 5.6463 | 5.9433 | 205.0274 | 1198.4276 | 17976.4137
2020-10-06 23:00 | 4.9642 | 5.2253 | 209.8032 | 798.11 | 11971.6502
2020-10-07 00:00 | 4.3213 | 4.5486 | 216.3403 | 494.4967 | 7417.4501
2020-10-07 01:00 | 4.3857 | 4.6163 | 215.9829 | 523.0976 | 7846.4634
2020-10-07 02:00 | 4.382 | 4.6125 | 219.3569 | 521.4726 | 7822.0894
2020-10-07 03:00 | 3.9466 | 4.1542 | 225.6126 | 352.2659 | 5283.9889
2020-10-07 04:00 | 2.8356 | 2.9847 | 227.7627 | 0 | 0
2020-10-07 05:00 | 1.6581 | 1.7453 | 208.1588 | 0 | 0
2020-10-07 06:00 | 1.3105 | 1.3794 | 172.6227 | 0 | 0
2020-10-07 07:00 | 1.7055 | 1.7952 | 182.8246 | 0 | 0
2020-10-07 08:00 | 1.4988 | 1.5776 | 211.0055 | 0 | 0
2020-10-07 09:00 | 1.4012 | 1.4749 | 209.4474 | 0 | 0
2020-10-07 10:00 | 1.7049 | 1.7946 | 151.7136 | 0 | 0
2020-10-07 11:00 | 2.1936 | 2.3089 | 136.407 | 0 | 0
2020-10-07 12:00 | 2.5064 | 2.6382 | 138.012 | 0 | 0
2020-10-07 13:00 | 2.6028 | 2.7397 | 142.3004 | 0 | 0
2020-10-07 14:00 | 2.5192 | 2.6517 | 140.2642 | 0 | 0
2020-10-07 15:00 | 3.0354 | 3.195 | 121.8309 | 89.7365 | 1346.0474
2020-10-07 16:00 | 3.0414 | 3.2013 | 117.946 | 91.0863 | 1366.2939
2020-10-07 17:00 | 3.1016 | 3.2647 | 117.9068 | 104.6455 | 1569.6831
2020-10-07 18:00 | 3.052 | 3.2125 | 118.6351 | 93.4679 | 1402.0188
2020-10-07 19:00 | 3.4506 | 3.6321 | 122.5368 | 192.7797 | 2891.6955
2020-10-07 20:00 | 3.8532 | 4.0558 | 125.7977 | 317.659 | 4764.8857
2020-10-07 21:00 | 4.2344 | 4.4572 | 128.5316 | 458.9177 | 6883.7661
2020-10-07 22:00 | 3.9952 | 4.2053 | 118.2128 | 370.2715 | 5554.0721
2020-10-07 23:00 | 3.5451 | 3.7316 | 116.4393 | 221.2383 | 3318.5741
2020-10-08 00:00 | 3.273 | 3.4452 | 116.1436 | 143.2664 | 2148.9963
2020-10-08 01:00 | 3.0245 | 3.1836 | 108.9867 | 87.2894 | 1309.3409
2020-10-08 02:00 | 2.919 | 3.0725 | 100.3122 | 63.5252 | 952.878
2020-10-08 03:00 | 3.1981 | 3.3663 | 100.9856 | 126.3855 | 1895.7831
2020-10-08 04:00 | 3.1704 | 3.3372 | 98.2178 | 120.1533 | 1802.2988
2020-10-08 05:00 | 3.1289 | 3.2935 | 99.5042 | 110.805 | 1662.0754
2020-10-08 06:00 | 3.1927 | 3.3606 | 101.6521 | 125.1694 | 1877.5413
2020-10-08 07:00 | 3.78 | 3.9788 | 115.0275 | 291.9248 | 4378.8718
2020-10-08 08:00 | 4.8501 | 5.1052 | 131.7153 | 737.8163 | 11067.2449
2020-10-08 09:00 | 4.3534 | 4.5824 | 131.1398 | 508.7629 | 7631.4433
2020-10-08 10:00 | 5.2116 | 5.4857 | 119.4611 | 928.8049 | 13932.074
2020-10-08 11:00 | 4.8963 | 5.1538 | 115.0231 | 762.2192 | 11433.2886
2020-10-08 12:00 | 5.9772 | 6.2915 | 108.4106 | 1436.0805 | 21541.2074
2020-10-08 13:00 | 6.8679 | 7.2291 | 106.616 | 2201.5668 | 33023.5024
2020-10-08 14:00 | 6.145 | 6.4682 | 102.2286 | 1559.7453 | 23396.1792
2020-10-08 15:00 | 7.2456 | 7.6267 | 100.8268 | 2588.0424 | 38820.6357
2020-10-08 16:00 | 8.1559 | 8.5848 | 110.3164 | 3641.694 | 54625.4104
2020-10-08 17:00 | 8.4112 | 8.8535 | 121.4069 | 3944.7904 | 59171.8554
2020-10-08 18:00 | 8.3808 | 8.8216 | 129.0757 | 3908.7235 | 58630.8525
2020-10-08 19:00 | 8.1441 | 8.5724 | 134.7349 | 3627.713 | 54415.6952
2020-10-08 20:00 | 7.792 | 8.2018 | 142.14 | 3210.2449 | 48153.6731
2020-10-08 21:00 | 7.3419 | 7.728 | 150.913 | 2695.2283 | 40428.4241
2020-10-08 22:00 | 6.0003 | 6.3159 | 146.1412 | 1453.1055 | 21796.5819
2020-10-08 23:00 | 5.8145 | 6.1203 | 148.8877 | 1316.2282 | 19743.423
2020-10-09 00:00 | 5.5255 | 5.8161 | 153.0475 | 1123.1527 | 16847.2902
2020-10-09 01:00 | 5.5698 | 5.8627 | 156.3831 | 1150.7233 | 17260.8489
2020-10-09 02:00 | 5.3394 | 5.6202 | 160.411 | 1007.1514 | 15107.2716
2020-10-09 03:00 | 4.9208 | 5.1796 | 163.3119 | 775.1386 | 11627.0784
2020-10-09 04:00 | 4.192 | 4.4125 | 173.5029 | 443.1945 | 6647.918
2020-10-09 05:00 | 3.5766 | 3.7647 | 181.3612 | 230.7074 | 3460.6111
2020-10-09 06:00 | 3.5126 | 3.6973 | 172.8496 | 211.4382 | 3171.5737
2020-10-09 07:00 | 3.3296 | 3.5047 | 168.2791 | 156.3554 | 2345.3309
2020-10-09 08:00 | 3.6622 | 3.8549 | 170.7847 | 256.4887 | 3847.3298
2020-10-09 09:00 | 3.5813 | 3.7696 | 173.6646 | 232.1139 | 3481.7089
2020-10-09 10:00 | 3.5212 | 3.7064 | 179.8982 | 214.0293 | 3210.4398
2020-10-09 11:00 | 2.5953 | 2.7318 | 200.4468 | 0 | 0
2020-10-09 12:00 | 2.0218 | 2.1282 | 238.7552 | 0 | 0
2020-10-09 13:00 | 2.165 | 2.2789 | 298.8041 | 0 | 0
2020-10-09 14:00 | 2.7087 | 2.8511 | 328.2359 | 0 | 0
2020-10-09 15:00 | 3.3133 | 3.4875 | 345.6632 | 152.3277 | 2284.9155
2020-10-09 16:00 | 4.3591 | 4.5884 | 350.6963 | 511.2972 | 7669.4575
2020-10-09 17:00 | 5.0359 | 5.3008 | 356.0073 | 835.9924 | 12539.8863
2020-10-09 18:00 | 5.1664 | 5.4381 | 357.3006 | 904.9509 | 13574.2628
2020-10-09 19:00 | 5.213 | 5.4872 | 356.8426 | 929.5657 | 13943.4856
2020-10-09 20:00 | 5.6049 | 5.8997 | 357.3233 | 1172.6345 | 17589.5168
2020-10-09 21:00 | 5.9819 | 6.2965 | 359.7244 | 1439.5243 | 21592.8651
2020-10-09 22:00 | 5.9885 | 6.3034 | 3.6351 | 1444.3935 | 21665.9028
2020-10-09 23:00 | 5.9706 | 6.2846 | 13.063 | 1431.2401 | 21468.6012
2020-10-10 00:00 | 5.8186 | 6.1246 | 16.5 | 1319.208 | 19788.1203
2020-10-10 01:00 | 5.9548 | 6.268 | 17.7087 | 1419.6195 | 21294.2924
2020-10-10 02:00 | 5.7447 | 6.0468 | 20.1066 | 1264.7798 | 18971.6972
2020-10-10 03:00 | 5.4888 | 5.7775 | 24.8976 | 1100.2505 | 16503.7569
2020-10-10 04:00 | 5.7668 | 6.0701 | 29.4955 | 1281.0376 | 19215.5647
2020-10-10 05:00 | 5.9709 | 6.2849 | 36.8103 | 1431.4415 | 21471.6224
2020-10-10 06:00 | 6.1731 | 6.4978 | 47.8118 | 1580.4576 | 23706.8637
2020-10-10 07:00 | 5.1447 | 5.4153 | 55.6819 | 893.4842 | 13402.2637
2020-10-10 08:00 | 4.3399 | 4.5682 | 65.2922 | 502.7656 | 7541.4845
2020-10-10 09:00 | 3.7725 | 3.9709 | 81.6228 | 289.6688 | 4345.0318
2020-10-10 10:00 | 3.5821 | 3.7705 | 82.872 | 232.3574 | 3485.3607
2020-10-10 11:00 | 2.6244 | 2.7624 | 91.2607 | 0 | 0
2020-10-10 12:00 | 2.7946 | 2.9415 | 79.8435 | 0 | 0
2020-10-10 13:00 | 2.5264 | 2.6592 | 69.7521 | 0 | 0
2020-10-10 14:00 | 3.9693 | 4.1781 | 64.2454 | 360.6816 | 5410.2246
2020-10-10 15:00 | 5.066 | 5.3325 | 67.557 | 851.9117 | 12778.6748
2020-10-10 16:00 | 5.2263 | 5.5012 | 76.6253 | 936.6933 | 14050.3998
2020-10-10 17:00 | 5.0664 | 5.3329 | 84.3114 | 852.1193 | 12781.7894
2020-10-10 18:00 | 4.9946 | 5.2573 | 90.5831 | 814.1822 | 12212.7324
2020-10-10 19:00 | 4.561 | 4.8009 | 94.9446 | 600.9914 | 9014.8712
2020-10-10 20:00 | 3.8854 | 4.0897 | 108.3328 | 329.5821 | 4943.7309
2020-10-10 21:00 | 3.3119 | 3.4861 | 119.0354 | 152.0189 | 2280.2837
2020-10-10 22:00 | 2.5971 | 2.7337 | 126.8903 | 0 | 0
2020-10-10 23:00 | 1.9134 | 2.014 | 123.3465 | 0 | 0
2020-10-11 00:00 | 1.7034 | 1.793 | 107.9286 | 0 | 0
2020-10-11 01:00 | 1.5217 | 1.6018 | 91.1003 | 0 | 0
2020-10-11 02:00 | 1.4481 | 1.5243 | 68.1985 | 0 | 0
2020-10-11 03:00 | 1.7863 | 1.8802 | 59.6216 | 0 | 0
2020-10-11 04:00 | 2.022 | 2.1283 | 61.8896 | 0 | 0
2020-10-11 05:00 | 2.1183 | 2.2297 | 80.4419 | 0 | 0
2020-10-11 06:00 | 1.2107 | 1.2744 | 102.1846 | 0 | 0
2020-10-11 07:00 | 0.63466 | 0.66804 | 151.5994 | 0 | 0
2020-10-11 08:00 | 0.71744 | 0.75517 | 191.2167 | 0 | 0
2020-10-11 09:00 | 0.66366 | 0.69856 | 184.7677 | 0 | 0
2020-10-11 10:00 | 0.66328 | 0.69816 | 132.4678 | 0 | 0
2020-10-11 11:00 | 0.069573 | 0.073232 | 288.9277 | 0 | 0
2020-10-11 12:00 | 1.0429 | 1.0977 | 315.7416 | 0 | 0
2020-10-11 13:00 | 1.7663 | 1.8592 | 309.3364 | 0 | 0
2020-10-11 14:00 | 1.8981 | 1.9979 | 326.5087 | 0 | 0
2020-10-11 15:00 | 2.2225 | 2.3394 | 349.0074 | 0 | 0
2020-10-11 16:00 | 2.507 | 2.6389 | 0.41917 | 0 | 0
2020-10-11 17:00 | 2.4988 | 2.6302 | 4.2139 | 0 | 0
2020-10-11 18:00 | 2.0649 | 2.1735 | 4.911 | 0 | 0
2020-10-11 19:00 | 1.5802 | 1.6633 | 10.8825 | 0 | 0
2020-10-11 20:00 | 0.76708 | 0.80743 | 3.8837 | 0 | 0
2020-10-11 21:00 | 0.70945 | 0.74676 | 269.1238 | 0 | 0
2020-10-11 22:00 | 2.3658 | 2.4902 | 266.6182 | 0 | 0
2020-10-11 23:00 | 3.6656 | 3.8584 | 269.6317 | 257.4961 | 3862.4411
2020-10-12 00:00 | 3.613 | 3.803 | 281.0494 | 241.6502 | 3624.7533
2020-10-12 01:00 | 3.3105 | 3.4846 | 296.1905 | 151.7028 | 2275.5414
2020-10-12 02:00 | 3.3305 | 3.5056 | 305.2848 | 156.6099 | 2349.1487
2020-10-12 03:00 | 3.0395 | 3.1994 | 298.4154 | 90.6648 | 1359.9717
2020-10-12 04:00 | 2.7976 | 2.9448 | 290.3655 | 0 | 0
2020-10-12 05:00 | 1.9649 | 2.0682 | 283.4494 | 0 | 0
2020-10-12 06:00 | 1.6732 | 1.7613 | 279.9125 | 0 | 0
2020-10-12 07:00 | 1.1602 | 1.2212 | 283.3412 | 0 | 0
2020-10-12 08:00 | 1.1528 | 1.2134 | 207.4256 | 0 | 0
2020-10-12 09:00 | 2.0342 | 2.1412 | 188.4367 | 0 | 0
2020-10-12 10:00 | 2.0767 | 2.186 | 154.9789 | 0 | 0
2020-10-12 11:00 | 2.6319 | 2.7703 | 160.8809 | 0 | 0
2020-10-12 12:00 | 3.0981 | 3.261 | 163.693 | 103.8558 | 1557.837
2020-10-12 13:00 | 3.1556 | 3.3215 | 158.7498 | 116.808 | 1752.1205
2020-10-12 14:00 | 3.4035 | 3.5825 | 163.9329 | 178.5873 | 2678.8096
2020-10-12 15:00 | 3.0318 | 3.1913 | 163.1615 | 88.9392 | 1334.0874
2020-10-12 16:00 | 3.0736 | 3.2353 | 144.0319 | 98.3517 | 1475.2761
2020-10-12 17:00 | 4.3479 | 4.5766 | 125.3592 | 506.3373 | 7595.0596
2020-10-12 18:00 | 5.1464 | 5.417 | 125.0351 | 894.3452 | 13415.1785
2020-10-12 19:00 | 6.0053 | 6.3212 | 127.1809 | 1456.8279 | 21852.419
2020-10-12 20:00 | 6.8141 | 7.1725 | 127.911 | 2148.745 | 32231.1754
2020-10-12 21:00 | 7.3774 | 7.7654 | 130.8454 | 2734.7727 | 41021.5908
2020-10-12 22:00 | 7.6971 | 8.102 | 147.5637 | 3097.8109 | 46467.1637
2020-10-12 23:00 | 7.606 | 8.006 | 150.4748 | 2989.7672 | 44846.5076
2020-10-13 00:00 | 7.435 | 7.826 | 152.3116 | 2798.9327 | 41983.991
2020-10-13 01:00 | 7.3168 | 7.7017 | 150.1258 | 2667.3666 | 40010.4996
2020-10-13 02:00 | 7.4709 | 7.8639 | 150.2299 | 2838.9671 | 42584.5072
2020-10-13 03:00 | 7.4541 | 7.8462 | 149.8714 | 2820.2695 | 42304.043
2020-10-13 04:00 | 7.3888 | 7.7774 | 151.0455 | 2747.4695 | 41212.0423
2020-10-13 05:00 | 7.1944 | 7.5728 | 147.1382 | 2531.0144 | 37965.2157
2020-10-13 06:00 | 8.109 | 8.5355 | 140.5776 | 3586.0154 | 53790.2307
2020-10-13 07:00 | 8.6756 | 9.1319 | 141.8089 | 4251.1573 | 63767.3592
2020-10-13 08:00 | 8.0648 | 8.489 | 136.147 | 3533.6231 | 53004.3472
2020-10-13 09:00 | 8.1388 | 8.5668 | 132.3025 | 3621.3683 | 54320.525
2020-10-13 10:00 | 8.8873 | 9.3547 | 132.767 | 4489.5504 | 67343.2562
2020-10-13 11:00 | 8.7998 | 9.2626 | 134.0617 | 4390.9713 | 65864.5699
2020-10-13 12:00 | 8.8758 | 9.3426 | 134.5941 | 4476.5617 | 67148.4254
2020-10-13 13:00 | 7.8694 | 8.2833 | 126.6973 | 3302.0136 | 49530.2033
2020-10-13 14:00 | 8.0764 | 8.5012 | 119.4677 | 3547.309 | 53209.6343
2020-10-13 15:00 | 8.7233 | 9.1821 | 114.808 | 4304.8834 | 64573.2506
2020-10-13 16:00 | 9.4088 | 9.9037 | 113.2368 | 4976.8094 | 74652.1409
2020-10-13 17:00 | 9.4982 | 9.9978 | 115.0902 | 5054.1944 | 75812.9158
2020-10-13 18:00 | 9.7151 | 10.226 | 116.1189 | 5187.9941 | 77819.9109
2020-10-13 19:00 | 10.0559 | 10.5848 | 116.7292 | 5380.3987 | 80705.9807
2020-10-13 20:00 | 10.3147 | 10.8571 | 119.6306 | 5484.4313 | 82266.4688
2020-10-13 21:00 | 10.5611 | 11.1165 | 125.3425 | 5565.3312 | 83479.9684
2020-10-13 22:00 | 10.7618 | 11.3278 | 131.4757 | 5613.0813 | 84196.2192
2020-10-13 23:00 | 11.2431 | 11.8344 | 138.0878 | 5683.435 | 85251.5247
2020-10-14 00:00 | 10.2815 | 10.8223 | 146.0124 | 5471.1003 | 82066.504
2020-10-14 01:00 | 9.273 | 9.7608 | 154.5906 | 4859.3366 | 72890.0483
2020-10-14 02:00 | 8.477 | 8.9228 | 157.6991 | 4022.9536 | 60344.3044
2020-10-14 03:00 | 8.0016 | 8.4224 | 162.1032 | 3458.6249 | 51879.373
2020-10-14 04:00 | 7.6713 | 8.0748 | 166.6908 | 3067.18 | 46007.6993
2020-10-14 05:00 | 7.4796 | 7.873 | 176.5119 | 2848.603 | 42729.0448
2020-10-14 06:00 | 7.0288 | 7.3985 | 199.1772 | 2359.3778 | 35390.6672
2020-10-14 07:00 | 5.9097 | 6.2205 | 226.6042 | 1386.3584 | 20795.3756
2020-10-14 08:00 | 5.8351 | 6.142 | 245.0826 | 1331.3702 | 19970.5534
2020-10-14 09:00 | 5.572 | 5.865 | 246.0926 | 1152.1051 | 17281.5763
2020-10-14 10:00 | 4.688 | 4.9345 | 238.237 | 657.3669 | 9860.5042
2020-10-14 11:00 | 5.2775 | 5.5551 | 213.8166 | 968.594 | 14528.9102
2020-10-14 12:00 | 6.8558 | 7.2164 | 205.5488 | 2189.6637 | 32844.9548
2020-10-14 13:00 | 7.1957 | 7.5741 | 207.5504 | 2532.4469 | 37986.7042
2020-10-14 14:00 | 7.21 | 7.5892 | 216.0427 | 2548.3929 | 38225.8931
2020-10-14 15:00 | 7.0157 | 7.3847 | 222.6845 | 2346.5454 | 35198.1803
2020-10-14 16:00 | 6.4088 | 6.7458 | 224.037 | 1781.6188 | 26724.2816
2020-10-14 17:00 | 5.8129 | 6.1186 | 217.1674 | 1315.0449 | 19725.6738
2020-10-14 18:00 | 5.7562 | 6.059 | 200.6619 | 1273.2745 | 19099.1176
2020-10-14 19:00 | 6.3514 | 6.6854 | 189.5041 | 1732.5464 | 25988.1967
2020-10-14 20:00 | 6.8359 | 7.1954 | 184.7031 | 2170.1249 | 32551.8731
2020-10-14 21:00 | 7.3118 | 7.6964 | 181.977 | 2661.769 | 39926.5352
2020-10-14 22:00 | 7.659 | 8.0618 | 182.5409 | 3052.5619 | 45788.4287
2020-10-14 23:00 | 7.8373 | 8.2495 | 182.6203 | 3263.9677 | 48959.5158
2020-10-15 00:00 | 7.7906 | 8.2003 | 183.7416 | 3208.5602 | 48128.403
2020-10-15 01:00 | 7.818 | 8.2292 | 186.4918 | 3241.0941 | 48616.4113
2020-10-15 02:00 | 7.964 | 8.3829 | 190.3132 | 3414.1363 | 51212.0447
2020-10-15 03:00 | 8.0793 | 8.5043 | 192.4829 | 3550.8021 | 53262.031
2020-10-15 04:00 | 8.1345 | 8.5624 | 194.1004 | 3616.3579 | 54245.368
2020-10-15 05:00 | 7.9169 | 8.3332 | 199.0065 | 3358.2307 | 50373.4599
2020-10-15 06:00 | 7.6264 | 8.0275 | 202.7879 | 3013.9208 | 45208.8114
2020-10-15 07:00 | 6.5744 | 6.9202 | 201.555 | 1923.1727 | 28847.5898
2020-10-15 08:00 | 6.6339 | 6.9828 | 203.816 | 1974.0366 | 29610.5496
2020-10-15 09:00 | 6.661 | 7.0113 | 207.0272 | 1998.5498 | 29978.2466
2020-10-15 10:00 | 6.1356 | 6.4583 | 205.0166 | 1552.7915 | 23291.8726
2020-10-15 11:00 | 6.0943 | 6.4148 | 202.2538 | 1522.376 | 22835.6405
2020-10-15 12:00 | 6.8892 | 7.2516 | 205.0555 | 2222.475 | 33337.1248
2020-10-15 13:00 | 5.4913 | 5.7801 | 208.1262 | 1101.8326 | 16527.4889
2020-10-15 14:00 | 4.9054 | 5.1634 | 205.235 | 767.0396 | 11505.5944
2020-10-15 15:00 | 4.9853 | 5.2475 | 203.693 | 809.2344 | 12138.5153
2020-10-15 16:00 | 5.3835 | 5.6667 | 206.7994 | 1034.6681 | 15520.0222
2020-10-15 17:00 | 5.4831 | 5.7714 | 208.1444 | 1096.6898 | 16450.3473
2020-10-15 18:00 | 5.3548 | 5.6364 | 206.1584 | 1016.7754 | 15251.6317
2020-10-15 19:00 | 5.4086 | 5.693 | 202.5661 | 1050.2655 | 15753.983
2020-10-15 20:00 | 5.3203 | 5.6001 | 202.4175 | 995.2508 | 14928.7616
2020-10-15 21:00 | 4.9842 | 5.2463 | 209.4309 | 808.6569 | 12129.8538
2020-10-15 22:00 | 4.111 | 4.3273 | 219.3885 | 413.1947 | 6197.9204
2020-10-15 23:00 | 3.3311 | 3.5063 | 234.7133 | 156.802 | 2352.0297
2020-10-16 00:00 | 3.1277 | 3.2922 | 268.7988 | 110.5312 | 1657.9677
2020-10-16 01:00 | 4.0229 | 4.2345 | 306.8971 | 380.5473 | 5708.21
2020-10-16 02:00 | 4.8493 | 5.1043 | 329.7819 | 737.3611 | 11060.4168
2020-10-16 03:00 | 5.0328 | 5.2975 | 349.5876 | 834.3518 | 12515.2776
2020-10-16 04:00 | 5.0274 | 5.2918 | 4.6941 | 831.4862 | 12472.2935
2020-10-16 05:00 | 4.5795 | 4.8204 | 15.1866 | 609.1959 | 9137.9382
2020-10-16 06:00 | 3.51 | 3.6947 | 21.962 | 210.6705 | 3160.0574
2020-10-16 07:00 | 2.6516 | 2.7911 | 20.8743 | 0 | 0
2020-10-16 08:00 | 2.6866 | 2.8279 | 21.6451 | 0 | 0
2020-10-16 09:00 | 2.3311 | 2.4538 | 18.9523 | 0 | 0
2020-10-16 10:00 | 2.5984 | 2.735 | 28.7717 | 0 | 0
2020-10-16 11:00 | 2.3086 | 2.43 | 26.8973 | 0 | 0
2020-10-16 12:00 | 2.8752 | 3.0264 | 30.6922 | 53.6529 | 804.7931
2020-10-16 13:00 | 3.8272 | 4.0285 | 29.4529 | 308.0312 | 4620.4678
2020-10-16 14:00 | 4.3359 | 4.5639 | 30.9134 | 500.974 | 7514.6094
2020-10-16 15:00 | 5.1737 | 5.4458 | 36.9355 | 908.7768 | 13631.6522
2020-10-16 16:00 | 5.308 | 5.5872 | 38.512 | 987.6342 | 14814.5124
2020-10-16 17:00 | 5.7733 | 6.077 | 38.8047 | 1285.8895 | 19288.3424
2020-10-16 18:00 | 6.079 | 6.3987 | 43.9433 | 1511.0783 | 22666.1739
2020-10-16 19:00 | 6.0192 | 6.3358 | 51.2567 | 1467.0685 | 22006.0275
2020-10-16 20:00 | 6.1265 | 6.4487 | 59.4089 | 1546.0903 | 23191.3541
2020-10-16 21:00 | 6.0649 | 6.3839 | 61.3957 | 1500.7043 | 22510.5648
2020-10-16 22:00 | 6.0897 | 6.41 | 65.3842 | 1518.9736 | 22784.6046
2020-10-16 23:00 | 5.8427 | 6.15 | 64.6367 | 1336.9752 | 20054.6278
2020-10-17 00:00 | 5.8873 | 6.1969 | 59.6156 | 1369.8318 | 20547.477
2020-10-17 01:00 | 6.2411 | 6.5693 | 58.3393 | 1638.2896 | 24574.3441
2020-10-17 02:00 | 6.6579 | 7.0081 | 58.2693 | 1995.5498 | 29933.2477
2020-10-17 03:00 | 6.8206 | 7.1793 | 59.0695 | 2155.1121 | 32326.6815
2020-10-17 04:00 | 7.0359 | 7.4059 | 57.3361 | 2366.2996 | 35494.4937
2020-10-17 05:00 | 7.6964 | 8.1012 | 53.4525 | 3096.9521 | 46454.2817
2020-10-17 06:00 | 8.0898 | 8.5153 | 47.5226 | 3563.217 | 53448.2551
2020-10-17 07:00 | 7.7489 | 8.1564 | 46.8679 | 3159.161 | 47387.4147
2020-10-17 08:00 | 7.3357 | 7.7215 | 50.7368 | 2688.3242 | 40324.863
2020-10-17 09:00 | 7.136 | 7.5113 | 56.3323 | 2465.9732 | 36989.5981
2020-10-17 10:00 | 4.3233 | 4.5507 | 48.9639 | 495.4065 | 7431.0976
2020-10-17 11:00 | 2.5423 | 2.676 | 35.9872 | 0 | 0
2020-10-17 12:00 | 1.8909 | 1.9904 | 315.9089 | 0 | 0
2020-10-17 13:00 | 4.2149 | 4.4366 | 292.8989 | 451.6768 | 6775.1523
2020-10-17 14:00 | 5.9492 | 6.2621 | 288.7273 | 1415.4416 | 21231.6236
2020-10-17 15:00 | 6.7805 | 7.1371 | 289.1085 | 2115.7737 | 31736.6052
2020-10-17 16:00 | 6.8583 | 7.219 | 288.8713 | 2192.1234 | 32881.851
2020-10-17 17:00 | 6.9351 | 7.2998 | 286.6202 | 2267.42 | 34011.2994
2020-10-17 18:00 | 6.661 | 7.0113 | 279.5335 | 1998.5437 | 29978.1554
2020-10-17 19:00 | 6.8991 | 7.2619 | 271.9087 | 2232.119 | 33481.7856
2020-10-17 20:00 | 7.0323 | 7.4021 | 269.5291 | 2362.7656 | 35441.4846
2020-10-17 21:00 | 6.8594 | 7.2201 | 273.4784 | 2193.1737 | 32897.6048
2020-10-17 22:00 | 6.7628 | 7.1185 | 280.0097 | 2098.4222 | 31476.3328
2020-10-17 23:00 | 6.474 | 6.8145 | 283.0242 | 1837.3795 | 27560.6925
2020-10-18 00:00 | 5.3373 | 5.6181 | 282.6123 | 1005.893 | 15088.3951
2020-10-18 01:00 | 5.0591 | 5.3252 | 274.2888 | 848.2512 | 12723.7683
2020-10-18 02:00 | 5.329 | 5.6093 | 275.3345 | 1000.6942 | 15010.4137
2020-10-18 03:00 | 5.4877 | 5.7763 | 280.5482 | 1099.5984 | 16493.9755
2020-10-18 04:00 | 5.7761 | 6.0799 | 286.4273 | 1287.9575 | 19319.3627
2020-10-18 05:00 | 5.8253 | 6.1317 | 291.4378 | 1324.1963 | 19862.9445
2020-10-18 06:00 | 5.7048 | 6.0049 | 290.1592 | 1235.4009 | 18531.0137
2020-10-18 07:00 | 5.9789 | 6.2934 | 289.1038 | 1437.3651 | 21560.4771
2020-10-18 08:00 | 5.9899 | 6.3049 | 287.9575 | 1445.4559 | 21681.839
2020-10-18 09:00 | 5.6782 | 5.9768 | 277.9598 | 1218.2785 | 18274.177
2020-10-18 10:00 | 5.228 | 5.503 | 267.5507 | 937.7626 | 14066.4391
2020-10-18 11:00 | 6.3151 | 6.6473 | 260.3925 | 1701.5915 | 25523.8718
2020-10-18 12:00 | 7.165 | 7.5419 | 256.6473 | 2498.2913 | 37474.3697
2020-10-18 13:00 | 7.4515 | 7.8434 | 255.5114 | 2817.2902 | 42259.3527
2020-10-18 14:00 | 6.801 | 7.1587 | 254.7932 | 2135.8746 | 32038.1188
2020-10-18 15:00 | 6.9363 | 7.3011 | 257.9592 | 2268.6622 | 34029.9336
2020-10-18 16:00 | 6.7992 | 7.1568 | 260.8355 | 2134.1167 | 32011.7503
2020-10-18 17:00 | 7.0324 | 7.4023 | 264.4221 | 2362.9112 | 35443.6679
2020-10-18 18:00 | 7.1005 | 7.4739 | 259.8001 | 2429.7017 | 36445.5254
2020-10-18 19:00 | 7.5655 | 7.9634 | 253.0124 | 2944.2398 | 44163.5973
2020-10-18 20:00 | 8.0565 | 8.4803 | 252.1956 | 3523.7927 | 52856.8903
2020-10-18 21:00 | 8.0892 | 8.5147 | 251.4171 | 3562.5304 | 53437.9562
2020-10-18 22:00 | 8.134 | 8.5618 | 255.221 | 3615.7311 | 54235.9662
2020-10-18 23:00 | 8.0481 | 8.4714 | 254.5273 | 3513.7527 | 52706.2907
2020-10-19 00:00 | 7.948 | 8.366 | 254.1829 | 3395.1034 | 50926.5506
2020-10-19 01:00 | 7.8568 | 8.27 | 253.8877 | 3287.018 | 49305.2701
2020-10-19 02:00 | 7.7349 | 8.1417 | 256.2065 | 3142.5398 | 47138.0977
2020-10-19 03:00 | 7.7329 | 8.1396 | 259.1082 | 3140.1632 | 47102.4479
2020-10-19 04:00 | 7.8959 | 8.3112 | 264.569 | 3333.414 | 50001.2101
2020-10-19 05:00 | 7.9548 | 8.3731 | 269.063 | 3403.1631 | 51047.447
2020-10-19 06:00 | 7.8992 | 8.3146 | 274.5361 | 3337.276 | 50059.1401
2020-10-19 07:00 | 6.9831 | 7.3504 | 274.2546 | 2314.5737 | 34718.6058
2020-10-19 08:00 | 6.8306 | 7.1899 | 274.9383 | 2164.9499 | 32474.249
2020-10-19 09:00 | 6.6633 | 7.0138 | 277.5744 | 2000.8371 | 30012.5564
2020-10-19 10:00 | 5.9838 | 6.2986 | 280.4528 | 1440.9902 | 21614.8524
2020-10-19 11:00 | 5.8952 | 6.2053 | 280.5002 | 1375.7113 | 20635.669
2020-10-19 12:00 | 5.874 | 6.1829 | 283.5235 | 1360.0563 | 20400.8451
2020-10-19 13:00 | 6.4676 | 6.8077 | 288.1234 | 1831.8681 | 27478.0215
2020-10-19 14:00 | 6.0389 | 6.3565 | 287.1058 | 1481.5483 | 22223.2252
2020-10-19 15:00 | 5.8985 | 6.2087 | 282.318 | 1378.1244 | 20671.8657
2020-10-19 16:00 | 5.8765 | 6.1856 | 276.238 | 1361.8891 | 20428.3359
2020-10-19 17:00 | 6.0486 | 6.3668 | 270.7252 | 1488.737 | 22331.0547
2020-10-19 18:00 | 6.3968 | 6.7333 | 266.1865 | 1771.4088 | 26571.1326
2020-10-19 19:00 | 6.8106 | 7.1688 | 261.9304 | 2145.3224 | 32179.8361
2020-10-19 20:00 | 7.0638 | 7.4353 | 258.6791 | 2393.6711 | 35905.0671
2020-10-19 21:00 | 7.1484 | 7.5243 | 257.6036 | 2479.7383 | 37196.0743
2020-10-19 22:00 | 7.4649 | 7.8575 | 260.6878 | 2832.2773 | 42484.1599
2020-10-19 23:00 | 7.5287 | 7.9247 | 263.2562 | 2903.2977 | 43549.4657
2020-10-20 00:00 | 7.3182 | 7.7031 | 267.2205 | 2668.8379 | 40032.5686
2020-10-20 01:00 | 7.213 | 7.5923 | 269.4365 | 2551.6997 | 38275.4952
2020-10-20 02:00 | 6.9512 | 7.3168 | 269.5555 | 2283.2665 | 34248.9975
2020-10-20 03:00 | 6.7444 | 7.0991 | 265.8524 | 2080.3726 | 31205.5885
2020-10-20 04:00 | 6.8759 | 7.2375 | 263.8205 | 2209.3873 | 33140.8093
2020-10-20 05:00 | 6.8133 | 7.1716 | 264.7299 | 2147.9726 | 32219.5892
2020-10-20 06:00 | 6.7271 | 7.0809 | 268.4624 | 2063.445 | 30951.6747
2020-10-20 07:00 | 7.318 | 7.7029 | 276.3773 | 2668.6427 | 40029.6412
2020-10-20 08:00 | 7.8795 | 8.2939 | 282.1236 | 3313.9395 | 49709.0931
2020-10-20 09:00 | 8.1986 | 8.6298 | 285.5866 | 3692.4307 | 55386.4599
2020-10-20 10:00 | 7.697 | 8.1019 | 292.1218 | 3097.6893 | 46465.3392
2020-10-20 11:00 | 7.3193 | 7.7043 | 292.1822 | 2670.1086 | 40051.6295
2020-10-20 12:00 | 6.7892 | 7.1463 | 293.0703 | 2124.3605 | 31865.4069
2020-10-20 13:00 | 6.5395 | 6.8835 | 294.6115 | 1893.3692 | 28400.5373
2020-10-20 14:00 | 4.9928 | 5.2554 | 290.8682 | 813.2078 | 12198.117
2020-10-20 15:00 | 4.1628 | 4.3818 | 287.4071 | 432.3773 | 6485.6597
2020-10-20 16:00 | 3.4264 | 3.6066 | 280.8913 | 185.5011 | 2782.5162
2020-10-20 17:00 | 3.2343 | 3.4044 | 271.5055 | 134.5468 | 2018.2015
2020-10-20 18:00 | 3.1674 | 3.334 | 254.9613 | 119.476 | 1792.1393
2020-10-20 19:00 | 3.4453 | 3.6265 | 233.0584 | 191.1903 | 2867.8546
2020-10-20 20:00 | 4.2108 | 4.4323 | 215.0571 | 450.1604 | 6752.4062
2020-10-20 21:00 | 4.9533 | 5.2138 | 214.4424 | 792.3154 | 11884.731
2020-10-20 22:00 | 5.7312 | 6.0327 | 207.6476 | 1254.8762 | 18823.1427
2020-10-20 23:00 | 5.994 | 6.3092 | 204.0933 | 1448.4552 | 21726.8281
2020-10-21 00:00 | 6.2636 | 6.5931 | 200.9489 | 1657.5743 | 24863.6138
2020-10-21 01:00 | 6.4927 | 6.8342 | 201.4839 | 1853.3877 | 27800.8151
2020-10-21 02:00 | 6.7178 | 7.0711 | 199.369 | 2054.2971 | 30814.4559
2020-10-21 03:00 | 6.749 | 7.104 | 197.1592 | 2084.9082 | 31273.6234
2020-10-21 04:00 | 7.4314 | 7.8223 | 186.0467 | 2794.9495 | 41924.2418
2020-10-21 05:00 | 7.7382 | 8.1451 | 189.2365 | 3146.4381 | 47196.5719
2020-10-21 06:00 | 8.1249 | 8.5522 | 188.4083 | 3604.8555 | 54072.8323
2020-10-21 07:00 | 6.6108 | 6.9585 | 197.7873 | 1954.3097 | 29314.6455
2020-10-21 08:00 | 6.5485 | 6.8929 | 204.5396 | 1901.0184 | 28515.2765
2020-10-21 09:00 | 6.6808 | 7.0322 | 215.6093 | 2018.026 | 30270.39
2020-10-21 10:00 | 6.3716 | 6.7067 | 217.13 | 1749.8595 | 26247.8925
2020-10-21 11:00 | 6.4048 | 6.7417 | 223.1846 | 1778.2255 | 26673.3821
2020-10-21 12:00 | 6.1391 | 6.462 | 226.7483 | 1555.3759 | 23330.6381
2020-10-21 13:00 | 5.7788 | 6.0827 | 234.9899 | 1289.8919 | 19348.378
2020-10-21 14:00 | 5.6037 | 5.8984 | 233.5245 | 1171.8541 | 17577.8116
2020-10-21 15:00 | 5.7665 | 6.0698 | 228.4017 | 1280.8467 | 19212.7006
2020-10-21 16:00 | 6.1824 | 6.5076 | 231.5637 | 1588.1687 | 23822.5306
2020-10-21 17:00 | 6.2652 | 6.5947 | 237.3792 | 1658.8887 | 24883.3312
2020-10-21 18:00 | 6.3013 | 6.6327 | 231.4093 | 1689.762 | 25346.4304
2020-10-21 19:00 | 6.6499 | 6.9997 | 235.8355 | 1987.7342 | 29816.0137
2020-10-21 20:00 | 6.5403 | 6.8843 | 238.2917 | 1894.063 | 28410.9444
2020-10-21 21:00 | 6.4853 | 6.8264 | 237.5004 | 1847.0269 | 27705.404
2020-10-21 22:00 | 6.1523 | 6.4759 | 243.7081 | 1565.1398 | 23477.0966
2020-10-21 23:00 | 5.6004 | 5.895 | 246.2069 | 1169.8157 | 17547.2355
2020-10-22 00:00 | 5.5924 | 5.8866 | 247.0668 | 1164.856 | 17472.8405
2020-10-22 01:00 | 5.2807 | 5.5584 | 246.8523 | 970.5634 | 14558.4505
2020-10-22 02:00 | 5.0847 | 5.3521 | 248.3499 | 861.7426 | 12926.1385
2020-10-22 03:00 | 5.3363 | 5.6169 | 250.2626 | 1005.213 | 15078.1955
2020-10-22 04:00 | 5.5464 | 5.8382 | 245.8804 | 1136.1888 | 17042.8321
2020-10-22 05:00 | 5.9548 | 6.268 | 237.6363 | 1419.5746 | 21293.6184
2020-10-22 06:00 | 6.3264 | 6.6592 | 233.6538 | 1711.2585 | 25668.8782
2020-10-22 07:00 | 6.0724 | 6.3918 | 239.2758 | 1506.2486 | 22593.7295
2020-10-22 08:00 | 5.3072 | 5.5863 | 235.0092 | 987.1015 | 14806.5221
2020-10-22 09:00 | 5.9011 | 6.2115 | 238.7813 | 1380.0322 | 20700.4836
2020-10-22 10:00 | 5.5882 | 5.8821 | 241.3248 | 1162.1873 | 17432.8089
2020-10-22 11:00 | 5.7382 | 6.04 | 240.778 | 1259.9797 | 18899.696
2020-10-22 12:00 | 5.7827 | 6.0869 | 242.8011 | 1292.8119 | 19392.1792
2020-10-22 13:00 | 6.0766 | 6.3962 | 245.3686 | 1509.3181 | 22639.7708
2020-10-22 14:00 | 6.721 | 7.0745 | 245.9817 | 2057.3938 | 30860.9071
2020-10-22 15:00 | 7.1776 | 7.5551 | 245.1792 | 2512.3195 | 37684.7925
2020-10-22 16:00 | 7.3431 | 7.7293 | 247.0448 | 2696.6191 | 40449.2859
2020-10-22 17:00 | 7.5601 | 7.9578 | 248.7784 | 2938.3149 | 44074.724
2020-10-22 18:00 | 7.867 | 8.2808 | 246.6973 | 3299.1531 | 49487.2959
2020-10-22 19:00 | 8.2284 | 8.6612 | 247.6228 | 3727.8191 | 55917.286
2020-10-22 20:00 | 8.0849 | 8.5101 | 251.4012 | 3557.4445 | 53361.6669
2020-10-22 21:00 | 8.0235 | 8.4455 | 256.4016 | 3484.6448 | 52269.6726
2020-10-22 22:00 | 8.0215 | 8.4434 | 259.4632 | 3482.2248 | 52233.3717
2020-10-22 23:00 | 7.6194 | 8.0202 | 263.5143 | 3005.7096 | 45085.6441
2020-10-23 00:00 | 6.9076 | 7.2709 | 268.9256 | 2240.438 | 33606.5693
2020-10-23 01:00 | 5.9861 | 6.3009 | 269.2193 | 1442.6259 | 21639.3884
2020-10-23 02:00 | 5.3657 | 5.6479 | 272.7023 | 1023.5658 | 15353.4864
2020-10-23 03:00 | 5.1304 | 5.4002 | 280.1672 | 885.9076 | 13288.6139
2020-10-23 04:00 | 5.2437 | 5.5195 | 273.6368 | 947.5184 | 14212.7761
2020-10-23 05:00 | 5.3384 | 5.6191 | 258.0279 | 1006.5241 | 15097.8619
2020-10-23 06:00 | 5.1874 | 5.4603 | 249.7355 | 916.0519 | 13740.7779
2020-10-23 07:00 | 4.0304 | 4.2424 | 241.1675 | 383.3085 | 5749.6278
2020-10-23 08:00 | 3.9086 | 4.1142 | 235.2349 | 338.1838 | 5072.7573
2020-10-23 09:00 | 3.7236 | 3.9195 | 228.9978 | 274.9747 | 4124.6204
2020-10-23 10:00 | 3.6497 | 3.8417 | 230.8738 | 252.7127 | 3790.6908
2020-10-23 11:00 | 4.2669 | 4.4913 | 238.0896 | 470.9307 | 7063.9599
2020-10-23 12:00 | 4.8234 | 5.0771 | 246.551 | 723.7176 | 10855.7637
2020-10-23 13:00 | 5.2992 | 5.5779 | 253.2184 | 982.1311 | 14731.9669
2020-10-23 14:00 | 5.5431 | 5.8346 | 258.4614 | 1134.0766 | 17011.1497
2020-10-23 15:00 | 5.6972 | 5.9968 | 261.0928 | 1230.1214 | 18451.8212
2020-10-23 16:00 | 5.6987 | 5.9984 | 260.9002 | 1231.0685 | 18466.0275
2020-10-23 17:00 | 6.8107 | 7.1689 | 258.6847 | 2145.3731 | 32180.597
2020-10-23 18:00 | 6.7602 | 7.1158 | 260.5282 | 2095.8875 | 31438.312
2020-10-23 19:00 | 6.3801 | 6.7156 | 262.795 | 1757.1067 | 26356.6008
2020-10-23 20:00 | 6.0895 | 6.4098 | 265.0604 | 1518.8278 | 22782.4176
2020-10-23 21:00 | 5.9724 | 6.2865 | 268.4896 | 1432.5253 | 21487.8788
2020-10-23 22:00 | 6.411 | 6.7481 | 272.9343 | 1783.4939 | 26752.4085
2020-10-23 23:00 | 6.1652 | 6.4894 | 275.3781 | 1574.587 | 23618.8044
2020-10-24 00:00 | 5.7206 | 6.0215 | 274.682 | 1247.0288 | 18705.4315
2020-10-24 01:00 | 5.7328 | 6.0343 | 271.1046 | 1256.043 | 18840.6452
2020-10-24 02:00 | 5.3191 | 5.5989 | 270.0912 | 994.5504 | 14918.2559
2020-10-24 03:00 | 4.4355 | 4.6687 | 269.9482 | 545.2076 | 8178.1133
2020-10-24 04:00 | 4.4833 | 4.7191 | 267.7094 | 566.4539 | 8496.8079
2020-10-24 05:00 | 4.5671 | 4.8073 | 262.279 | 603.6831 | 9055.2472
2020-10-24 06:00 | 4.2778 | 4.5028 | 253.7888 | 475.178 | 7127.6696
2020-10-24 07:00 | 3.9853 | 4.1949 | 247.7777 | 366.5944 | 5498.9155
2020-10-24 08:00 | 3.7528 | 3.9501 | 236.5473 | 283.7414 | 4256.1203
2020-10-24 09:00 | 3.9508 | 4.1586 | 224.565 | 353.8276 | 5307.4136
2020-10-24 10:00 | 4.3723 | 4.6023 | 224.3372 | 517.1633 | 7757.4489
2020-10-24 11:00 | 4.6732 | 4.919 | 230.3522 | 650.7986 | 9761.9788
2020-10-24 12:00 | 4.7789 | 5.0303 | 235.0204 | 700.1992 | 10502.9883
2020-10-24 13:00 | 5.5664 | 5.8592 | 242.1554 | 1148.6232 | 17229.3475
2020-10-24 14:00 | 6.225 | 6.5524 | 246.2687 | 1624.542 | 24368.1301
2020-10-24 15:00 | 6.8926 | 7.2552 | 251.1827 | 2225.8107 | 33387.1607
2020-10-24 16:00 | 7.6337 | 8.0351 | 263.9126 | 3022.5666 | 45338.4994
2020-10-24 17:00 | 8.0292 | 8.4515 | 271.7026 | 3491.3922 | 52370.8831
2020-10-24 18:00 | 8.1358 | 8.5637 | 286.1323 | 3617.8452 | 54267.6778
2020-10-24 19:00 | 7.7977 | 8.2078 | 297.6999 | 3216.9548 | 48254.3214
2020-10-24 20:00 | 7.1233 | 7.4979 | 300.8535 | 2452.0475 | 36780.7125
2020-10-24 21:00 | 6.4734 | 6.8138 | 299.6388 | 1836.8278 | 27552.4176
2020-10-24 22:00 | 7.1584 | 7.5349 | 296.5917 | 2490.9403 | 37364.1041
2020-10-24 23:00 | 6.9838 | 7.3511 | 303.6987 | 2315.1979 | 34727.9678
2020-10-25 00:00 | 6.3756 | 6.7109 | 310.314 | 1753.2263 | 26298.3945
2020-10-25 01:00 | 5.9521 | 6.2651 | 314.7635 | 1417.602 | 21264.0299
2020-10-25 02:00 | 5.807 | 6.1124 | 323.3161 | 1310.7104 | 19660.6554
2020-10-25 03:00 | 4.9848 | 5.247 | 338.9061 | 809.0044 | 12135.0656
2020-10-25 04:00 | 3.7845 | 3.9835 | 341.8616 | 293.2882 | 4399.3237
2020-10-25 05:00 | 2.9955 | 3.1531 | 336.0367 | 80.763 | 1211.4455
2020-10-25 06:00 | 2.9767 | 3.1332 | 340.884 | 76.5111 | 1147.6658
2020-10-25 07:00 | 2.4868 | 2.6176 | 340.2098 | 0 | 0
2020-10-25 08:00 | 1.6772 | 1.7654 | 340.1916 | 0 | 0
2020-10-25 09:00 | 1.2863 | 1.3539 | 335.586 | 0 | 0
2020-10-25 10:00 | 0.65124 | 0.68549 | 2.0222 | 0 | 0
2020-10-25 11:00 | 0.52097 | 0.54837 | 260.2908 | 0 | 0
2020-10-25 12:00 | 0.43356 | 0.45636 | 5.149 | 0 | 0
2020-10-25 13:00 | 1.3157 | 1.3849 | 53.4249 | 0 | 0
2020-10-25 14:00 | 1.5004 | 1.5793 | 96.427 | 0 | 0
2020-10-25 15:00 | 2.3141 | 2.4358 | 109.1139 | 0 | 0
2020-10-25 16:00 | 3.2365 | 3.4067 | 99.7299 | 135.038 | 2025.5703
2020-10-25 17:00 | 4.2008 | 4.4217 | 95.7069 | 446.4347 | 6696.5207
2020-10-25 18:00 | 4.7733 | 5.0244 | 98.2952 | 697.23 | 10458.4505
2020-10-25 19:00 | 5.3143 | 5.5938 | 104.9786 | 991.5488 | 14873.2314
2020-10-25 20:00 | 5.6476 | 5.9446 | 109.453 | 1199.2261 | 17988.3911
2020-10-25 21:00 | 5.9119 | 6.2229 | 111.2923 | 1388.0128 | 20820.1919
2020-10-25 22:00 | 6.0037 | 6.3194 | 118.2576 | 1455.6082 | 21834.1231
2020-10-25 23:00 | 6.0577 | 6.3763 | 125.0081 | 1495.4403 | 22431.604
2020-10-26 00:00 | 6.1051 | 6.4262 | 130.9913 | 1530.3055 | 22954.5825
2020-10-26 01:00 | 6.1022 | 6.4231 | 133.1678 | 1528.1813 | 22922.7202
2020-10-26 02:00 | 5.9058 | 6.2164 | 137.2829 | 1383.5104 | 20752.6561
2020-10-26 03:00 | 6.0295 | 6.3466 | 135.2794 | 1474.6505 | 22119.7576
2020-10-26 04:00 | 6.3315 | 6.6645 | 131.6019 | 1715.5788 | 25733.6818
2020-10-26 05:00 | 6.4864 | 6.8275 | 129.4692 | 1847.9502 | 27719.2533
2020-10-26 06:00 | 6.5294 | 6.8728 | 128.5872 | 1884.7156 | 28270.7336
2020-10-26 07:00 | 5.7713 | 6.0749 | 127.7281 | 1284.4135 | 19266.203
2020-10-26 08:00 | 6.1991 | 6.5251 | 131.0891 | 1602.3816 | 24035.7247
2020-10-26 09:00 | 6.166 | 6.4903 | 130.7279 | 1575.2264 | 23628.3964
2020-10-26 10:00 | 6.1996 | 6.5257 | 134.2078 | 1602.8607 | 24042.9111
2020-10-26 11:00 | 6.6534 | 7.0034 | 129.6542 | 1991.1414 | 29867.121
2020-10-26 12:00 | 7.0255 | 7.395 | 131.7697 | 2356.1104 | 35341.6561
2020-10-26 13:00 | 6.6386 | 6.9878 | 127.8501 | 1978.0878 | 29671.3171
2020-10-26 14:00 | 6.7109 | 7.0638 | 123.0995 | 2047.5059 | 30712.588
2020-10-26 15:00 | 7.3524 | 7.7391 | 120.5686 | 2706.9636 | 40604.4543
2020-10-26 16:00 | 7.6731 | 8.0767 | 123.1073 | 3069.3678 | 46040.5163
2020-10-26 17:00 | 7.6837 | 8.0878 | 123.3794 | 3081.8969 | 46228.4532
2020-10-26 18:00 | 7.9931 | 8.4135 | 126.2293 | 3448.5824 | 51728.7364
2020-10-26 19:00 | 7.8415 | 8.254 | 128.8393 | 3268.9547 | 49034.3201
2020-10-26 20:00 | 7.6244 | 8.0254 | 130.5675 | 3011.5468 | 45173.2024
2020-10-26 21:00 | 7.3554 | 7.7422 | 131.9658 | 2710.272 | 40654.0795
2020-10-26 22:00 | 6.4805 | 6.8214 | 137.2161 | 1842.9383 | 27644.0741
2020-10-26 23:00 | 5.9086 | 6.2193 | 135.2979 | 1385.5215 | 20782.8221
2020-10-27 00:00 | 5.8832 | 6.1926 | 130.6984 | 1366.8442 | 20502.6631
2020-10-27 01:00 | 6.0963 | 6.4169 | 131.4328 | 1523.8612 | 22857.9173
2020-10-27 02:00 | 5.9165 | 6.2277 | 129.928 | 1391.3868 | 20870.8018
2020-10-27 03:00 | 5.9115 | 6.2224 | 130.2469 | 1387.6584 | 20814.8754
2020-10-27 04:00 | 5.7436 | 6.0457 | 131.4663 | 1263.9644 | 18959.4663
2020-10-27 05:00 | 5.4073 | 5.6917 | 133.1158 | 1049.4842 | 15742.2635
2020-10-27 06:00 | 5.6945 | 5.994 | 136.4346 | 1228.4436 | 18426.6542
2020-10-27 07:00 | 5.0309 | 5.2955 | 138.9194 | 833.3409 | 12500.1131
2020-10-27 08:00 | 4.5 | 4.7366 | 141.1622 | 573.8591 | 8607.8869
2020-10-27 09:00 | 4.2191 | 4.441 | 140.0201 | 453.2479 | 6798.7185
2020-10-27 10:00 | 3.8256 | 4.0268 | 133.6848 | 307.4178 | 4611.2677
2020-10-27 11:00 | 3.7219 | 3.9177 | 136.2674 | 274.4537 | 4116.8061
2020-10-27 12:00 | 3.3839 | 3.5619 | 134.7517 | 172.7016 | 2590.5244
2020-10-27 13:00 | 3.3644 | 3.5414 | 125.1015 | 166.8318 | 2502.4775
2020-10-27 14:00 | 4.0125 | 4.2236 | 114.7061 | 376.6944 | 5650.416
2020-10-27 15:00 | 5.1797 | 5.4521 | 115.2567 | 911.9607 | 13679.41
2020-10-27 16:00 | 6.2138 | 6.5406 | 120.2268 | 1614.9971 | 24224.9566
2020-10-27 17:00 | 6.702 | 7.0545 | 127.0443 | 2038.8191 | 30582.2858
2020-10-27 18:00 | 6.7735 | 7.1298 | 133.4137 | 2108.9558 | 31634.3376
2020-10-27 19:00 | 6.2389 | 6.5671 | 140.144 | 1636.4464 | 24546.6954
2020-10-27 20:00 | 5.8835 | 6.193 | 145.6384 | 1367.0871 | 20506.306
2020-10-27 21:00 | 5.6474 | 5.9444 | 149.7553 | 1199.0706 | 17986.0589
2020-10-27 22:00 | 4.9888 | 5.2512 | 159.0566 | 811.1039 | 12166.5578
2020-10-27 23:00 | 4.7014 | 4.9487 | 159.0207 | 663.3513 | 9950.2693
2020-10-28 00:00 | 4.6018 | 4.8438 | 153.2292 | 619.078 | 9286.1702
2020-10-28 01:00 | 4.7259 | 4.9744 | 148.1274 | 674.2053 | 10113.08
2020-10-28 02:00 | 4.7347 | 4.9837 | 145.879 | 678.1321 | 10171.9808
2020-10-28 03:00 | 4.9723 | 5.2339 | 144.373 | 802.4017 | 12036.0249
2020-10-28 04:00 | 5.0394 | 5.3045 | 144.2429 | 837.849 | 12567.7352
2020-10-28 05:00 | 5.089 | 5.3567 | 144.8566 | 864.0508 | 12960.7613
2020-10-28 06:00 | 4.9425 | 5.2024 | 146.0521 | 786.604 | 11799.0603
2020-10-28 07:00 | 4.0278 | 4.2397 | 147.1121 | 382.3577 | 5735.3656
2020-10-28 08:00 | 3.7399 | 3.9366 | 144.7045 | 279.8573 | 4197.8589
2020-10-28 09:00 | 3.7213 | 3.9171 | 143.2955 | 274.2793 | 4114.1894
2020-10-28 10:00 | 3.9146 | 4.1205 | 147.0782 | 340.4035 | 5106.0526
2020-10-28 11:00 | 3.8135 | 4.0141 | 144.3069 | 302.9614 | 4544.4212
2020-10-28 12:00 | 3.6428 | 3.8344 | 137.8311 | 250.644 | 3759.6601
2020-10-28 13:00 | 3.9114 | 4.1172 | 125.2754 | 339.2379 | 5088.568
2020-10-28 14:00 | 4.3899 | 4.6208 | 123.3588 | 524.9899 | 7874.8492
2020-10-28 15:00 | 4.7649 | 5.0155 | 123.0568 | 692.7656 | 10391.4841
2020-10-28 16:00 | 4.9334 | 5.1929 | 126.4628 | 781.8408 | 11727.6113
2020-10-28 17:00 | 5.0566 | 5.3225 | 129.5199 | 846.9012 | 12703.5176
2020-10-28 18:00 | 5.1393 | 5.4096 | 132.4281 | 890.6173 | 13359.2598
2020-10-28 19:00 | 5.056 | 5.3219 | 134.977 | 846.605 | 12699.0757
2020-10-28 20:00 | 4.808 | 5.0609 | 136.6226 | 715.5712 | 10733.5682
2020-10-28 21:00 | 4.4603 | 4.6949 | 139.5218 | 556.2361 | 8343.5418
2020-10-28 22:00 | 4.0321 | 4.2442 | 150.2825 | 383.9601 | 5759.4015
2020-10-28 23:00 | 3.6064 | 3.7961 | 154.3792 | 239.6827 | 3595.2411
2020-10-29 00:00 | 3.3703 | 3.5476 | 154.3702 | 168.6043 | 2529.0647
2020-10-29 01:00 | 3.4117 | 3.5911 | 146.9773 | 181.0518 | 2715.7766
2020-10-29 02:00 | 3.5454 | 3.7319 | 140.7747 | 221.3117 | 3319.6749
2020-10-29 03:00 | 3.8234 | 4.0244 | 139.0346 | 306.6054 | 4599.0806
2020-10-29 04:00 | 3.8404 | 4.0424 | 138.4919 | 312.9203 | 4693.8043
2020-10-29 05:00 | 3.9542 | 4.1622 | 139.5241 | 355.0962 | 5326.4429
2020-10-29 06:00 | 3.9012 | 4.1064 | 137.8627 | 335.4568 | 5031.8526
2020-10-29 07:00 | 3.5951 | 3.7842 | 139.1669 | 236.2733 | 3544.0996
2020-10-29 08:00 | 3.6822 | 3.8759 | 140.1374 | 262.4992 | 3937.4877
2020-10-29 09:00 | 3.5968 | 3.7859 | 143.6021 | 236.7739 | 3551.6084
2020-10-29 10:00 | 4.3124 | 4.5392 | 156.5024 | 490.539 | 7358.0857
2020-10-29 11:00 | 4.2948 | 4.5207 | 164.6245 | 482.7483 | 7241.2248
2020-10-29 12:00 | 4.4196 | 4.652 | 169.1631 | 538.1606 | 8072.4084
2020-10-29 13:00 | 4.3367 | 4.5647 | 165.9971 | 501.3244 | 7519.8658
2020-10-29 14:00 | 4.18 | 4.3998 | 169.7652 | 438.7312 | 6580.9684
2020-10-29 15:00 | 3.9912 | 4.2012 | 175.4381 | 368.806 | 5532.0907
2020-10-29 16:00 | 3.7428 | 3.9396 | 185.6557 | 280.7259 | 4210.8892
2020-10-29 17:00 | 3.5973 | 3.7865 | 198.7673 | 236.9418 | 3554.1267
2020-10-29 18:00 | 3.4969 | 3.6808 | 219.2862 | 206.7007 | 3100.5109
2020-10-29 19:00 | 3.3267 | 3.5016 | 232.5733 | 155.4623 | 2331.9347
2020-10-29 20:00 | 3.4301 | 3.6105 | 250.0446 | 186.5898 | 2798.8469
2020-10-29 21:00 | 3.7016 | 3.8963 | 267.3292 | 268.344 | 4025.1594
2020-10-29 22:00 | 3.577 | 3.7651 | 276.2574 | 230.8291 | 3462.4366
2020-10-29 23:00 | 3.3696 | 3.5468 | 282.9273 | 168.3765 | 2525.6477
2020-10-30 00:00 | 3.4851 | 3.6684 | 288.0465 | 203.1543 | 3047.3148
2020-10-30 01:00 | 3.3147 | 3.489 | 290.7766 | 152.6472 | 2289.7079
2020-10-30 02:00 | 3.6492 | 3.8411 | 291.9519 | 252.5583 | 3788.3748
2020-10-30 03:00 | 3.8717 | 4.0753 | 287.9117 | 324.5193 | 4867.7888
2020-10-30 04:00 | 4.0063 | 4.217 | 290.492 | 374.3898 | 5615.8464
2020-10-30 05:00 | 3.5677 | 3.7554 | 292.6798 | 228.0325 | 3420.4876
2020-10-30 06:00 | 2.7449 | 2.8892 | 285.7619 | 0 | 0
2020-10-30 07:00 | 2.1052 | 2.2159 | 276.5347 | 0 | 0
2020-10-30 08:00 | 2.1889 | 2.3041 | 279.988 | 0 | 0
2020-10-30 09:00 | 3.1995 | 3.3678 | 285.3168 | 126.7059 | 1900.5888
2020-10-30 10:00 | 2.9357 | 3.0901 | 293.2085 | 67.2785 | 1009.1777
2020-10-30 11:00 | 3.6813 | 3.875 | 296.7174 | 262.2371 | 3933.5567
2020-10-30 12:00 | 4.3574 | 4.5866 | 303.7599 | 510.531 | 7657.9643
2020-10-30 13:00 | 5.5474 | 5.8391 | 305.9051 | 1136.7594 | 17051.3903
2020-10-30 14:00 | 6.6555 | 7.0056 | 309.922 | 1993.1944 | 29897.9162
2020-10-30 15:00 | 6.9054 | 7.2686 | 310.9695 | 2238.3476 | 33575.2139
2020-10-30 16:00 | 6.787 | 7.144 | 312.2168 | 2122.1698 | 31832.5468
2020-10-30 17:00 | 6.5051 | 6.8473 | 312.8284 | 1863.9901 | 27959.8512
2020-10-30 18:00 | 6.2924 | 6.6233 | 311.8997 | 1682.1291 | 25231.9366
2020-10-30 19:00 | 6.2125 | 6.5392 | 311.4912 | 1613.8297 | 24207.4454
2020-10-30 20:00 | 6.2325 | 6.5603 | 312.7234 | 1630.9787 | 24464.6811
2020-10-30 21:00 | 6.0178 | 6.3343 | 314.1774 | 1466.0234 | 21990.3507
2020-10-30 22:00 | 5.8741 | 6.1831 | 314.7521 | 1360.1351 | 20402.0263
2020-10-30 23:00 | 5.441 | 5.7272 | 315.8758 | 1070.4743 | 16057.1144
2020-10-31 00:00 | 5.057 | 5.3229 | 314.6573 | 847.1144 | 12706.7159
2020-10-31 01:00 | 4.8091 | 5.062 | 316.7191 | 716.1466 | 10742.1987
2020-10-31 02:00 | 4.8978 | 5.1554 | 321.1967 | 762.9977 | 11444.965
2020-10-31 03:00 | 4.9196 | 5.1784 | 324.8695 | 774.5407 | 11618.1109
2020-10-31 04:00 | 5.1471 | 5.4178 | 328.4133 | 894.7219 | 13420.828
2020-10-31 05:00 | 5.6812 | 5.98 | 333.7434 | 1220.1869 | 18302.8039
2020-10-31 06:00 | 5.9563 | 6.2695 | 338.2459 | 1420.6702 | 21310.0537
2020-10-31 07:00 | 5.5661 | 5.8588 | 341.461 | 1148.4208 | 17226.3119
2020-10-31 08:00 | 6.3069 | 6.6386 | 352.329 | 1694.5236 | 25417.8539
2020-10-31 09:00 | 6.3455 | 6.6793 | 358.7267 | 1727.5814 | 25913.7207
2020-10-31 10:00 | 6.0018 | 6.3174 | 355.3272 | 1454.2059 | 21813.0885
2020-10-31 11:00 | 6.0384 | 6.356 | 348.9798 | 1481.1881 | 22217.8219
2020-10-31 12:00 | 6.3169 | 6.6492 | 347.09 | 1703.1151 | 25546.7265
2020-10-31 13:00 | 6.5456 | 6.8898 | 347.5439 | 1898.5276 | 28477.9135
2020-10-31 14:00 | 7.3158 | 7.7006 | 347.9962 | 2666.2121 | 39993.1817
2020-10-31 15:00 | 8.0365 | 8.4592 | 347.8221 | 3500.062 | 52500.9299
2020-10-31 16:00 | 8.232 | 8.665 | 348.2493 | 3732.0717 | 55981.0757
2020-10-31 17:00 | 8.213 | 8.6449 | 348.5047 | 3709.4669 | 55642.0028
2020-10-31 18:00 | 8.2158 | 8.6479 | 347.6769 | 3712.8772 | 55693.1576
2020-10-31 19:00 | 8.6632 | 9.1188 | 349.6824 | 4237.1033 | 63556.5488
2020-10-31 20:00 | 8.9047 | 9.373 | 354.2766 | 4509.1135 | 67636.7018
2020-10-31 21:00 | 9.7489 | 10.2616 | 354.6915 | 5208.8005 | 78132.007
2020-10-31 22:00 | 9.9067 | 10.4278 | 348.6692 | 5305.8271 | 79587.4063
2020-10-31 23:00 | 10.2549 | 10.7942 | 350.5834 | 5460.3931 | 81905.8967
2020-11-01 00:00 | 9.9516 | 10.475 | 356.0163 | 5333.3974 | 80000.9613
2020-11-01 01:00 | 10.1813 | 10.7167 | 353.997 | 5430.793 | 81461.8955
2020-11-01 02:00 | 9.9588 | 10.4825 | 352.0516 | 5337.8085 | 80067.128
2020-11-01 03:00 | 10.1161 | 10.6482 | 354.8585 | 5404.6053 | 81069.08
2020-11-01 04:00 | 10.0158 | 10.5426 | 359.022 | 5364.2593 | 80463.8896
2020-11-01 05:00 | 9.5381 | 10.0397 | 359.068 | 5079.1945 | 76187.9176
2020-11-01 06:00 | 8.9355 | 9.4055 | 357.5504 | 4543.862 | 68157.9303
2020-11-01 07:00 | 8.5044 | 8.9517 | 357.8227 | 4055.502 | 60832.5305
2020-11-01 08:00 | 8.0682 | 8.4926 | 354.7172 | 3537.6129 | 53064.1937
2020-11-01 09:00 | 7.8986 | 8.3141 | 350.7549 | 3336.6366 | 50049.5495
2020-11-01 10:00 | 8.0313 | 8.4538 | 350.354 | 3493.9282 | 52408.9225
2020-11-01 11:00 | 8.7715 | 9.2328 | 351.9387 | 4359.1182 | 65386.7725
2020-11-01 12:00 | 7.4589 | 7.8512 | 351.8287 | 2825.6075 | 42384.1128
2020-11-01 13:00 | 7.1236 | 7.4983 | 350.3841 | 2452.3834 | 36785.7504
2020-11-01 14:00 | 7.1485 | 7.5244 | 349.165 | 2479.8371 | 37197.5564
2020-11-01 15:00 | 7.173 | 7.5503 | 350.4763 | 2507.1662 | 37607.4934
2020-11-01 16:00 | 6.9325 | 7.2971 | 352.0396 | 2264.872 | 33973.0795
2020-11-01 17:00 | 6.6234 | 6.9718 | 350.4883 | 1965.0852 | 29476.2784
2020-11-01 18:00 | 6.2392 | 6.5673 | 347.8348 | 1636.684 | 24550.2606
2020-11-01 19:00 | 5.8326 | 6.1394 | 343.1583 | 1329.5851 | 19943.7764
2020-11-01 20:00 | 5.7603 | 6.0632 | 337.3236 | 1276.2524 | 19143.7862
2020-11-01 21:00 | 5.9667 | 6.2806 | 332.6306 | 1428.3881 | 21425.8218
2020-11-01 22:00 | 6.1567 | 6.4805 | 328.9812 | 1568.3787 | 23525.6812
2020-11-01 23:00 | 5.8924 | 6.2024 | 333.0185 | 1373.6467 | 20604.6999
2020-11-02 00:00 | 5.8493 | 6.1569 | 334.236 | 1341.8496 | 20127.7445
2020-11-02 01:00 | 6.0183 | 6.3348 | 332.1631 | 1466.3701 | 21995.5522
2020-11-02 02:00 | 6.027 | 6.344 | 332.458 | 1472.8217 | 22092.3258
2020-11-02 03:00 | 5.5833 | 5.877 | 334.5029 | 1159.1719 | 17387.5783
2020-11-02 04:00 | 5.3241 | 5.6041 | 332.9262 | 997.6276 | 14964.4137
2020-11-02 05:00 | 5.3214 | 5.6013 | 329.3094 | 995.9477 | 14939.2157
2020-11-02 06:00 | 6.2137 | 6.5405 | 325.5547 | 1614.8492 | 24222.7373
2020-11-02 07:00 | 6.1065 | 6.4277 | 325.8368 | 1531.376 | 22970.6406
2020-11-02 08:00 | 5.5432 | 5.8348 | 327.4091 | 1134.1739 | 17012.608
2020-11-02 09:00 | 5.1478 | 5.4185 | 325.4776 | 895.0951 | 13426.4261
2020-11-02 10:00 | 6.0039 | 6.3197 | 319.4321 | 1455.772 | 21836.5797
2020-11-02 11:00 | 5.7446 | 6.0468 | 320.1646 | 1264.7467 | 18971.2009
2020-11-02 12:00 | 4.913 | 5.1714 | 318.0431 | 771.0353 | 11565.5296
2020-11-02 13:00 | 4.3631 | 4.5926 | 314.7295 | 513.0722 | 7696.0833
2020-11-02 14:00 | 4.0294 | 4.2413 | 314.3039 | 382.9467 | 5744.201
2020-11-02 15:00 | 3.7393 | 3.9359 | 316.6156 | 279.6779 | 4195.1691
2020-11-02 16:00 | 3.337 | 3.5125 | 317.5294 | 158.58 | 2378.7001
2020-11-02 17:00 | 3.0874 | 3.2497 | 316.8699 | 101.4464 | 1521.6964
2020-11-02 18:00 | 2.7676 | 2.9132 | 316.7678 | 0 | 0
2020-11-02 19:00 | 2.7168 | 2.8597 | 313.7097 | 0 | 0
2020-11-02 20:00 | 2.8611 | 3.0116 | 306.965 | 50.473 | 757.0949
2020-11-02 21:00 | 2.8049 | 2.9524 | 299.1824 | 0 | 0
2020-11-02 22:00 | 2.8752 | 3.0264 | 299.886 | 53.6559 | 804.8379
2020-11-02 23:00 | 2.1983 | 2.3139 | 314.0407 | 0 | 0
2020-11-03 00:00 | 1.977 | 2.081 | 322.8126 | 0 | 0
2020-11-03 01:00 | 1.7121 | 1.8021 | 329.2152 | 0 | 0
2020-11-03 02:00 | 1.3095 | 1.3784 | 344.1558 | 0 | 0
2020-11-03 03:00 | 0.88375 | 0.93023 | 15.0419 | 0 | 0
2020-11-03 04:00 | 1.3377 | 1.408 | 67.4033 | 0 | 0
2020-11-03 05:00 | 1.9033 | 2.0034 | 92.1038 | 0 | 0
2020-11-03 06:00 | 2.0361 | 2.1432 | 106.9514 | 0 | 0
2020-11-03 07:00 | 1.791 | 1.8852 | 112.9862 | 0 | 0
2020-11-03 08:00 | 2.0189 | 2.125 | 118.9831 | 0 | 0
2020-11-03 09:00 | 2.281 | 2.4009 | 125.6417 | 0 | 0
2020-11-03 10:00 | 2.1906 | 2.3058 | 136.694 | 0 | 0
2020-11-03 11:00 | 1.7967 | 1.8912 | 136.9861 | 0 | 0
2020-11-03 12:00 | 1.9922 | 2.0969 | 131.5587 | 0 | 0
2020-11-03 13:00 | 2.4761 | 2.6063 | 124.8577 | 0 | 0
2020-11-03 14:00 | 2.6827 | 2.8238 | 121.7128 | 0 | 0
2020-11-03 15:00 | 2.814 | 2.962 | 115.1278 | 0 | 0
2020-11-03 16:00 | 3.7178 | 3.9133 | 109.7607 | 273.1998 | 4097.9967
2020-11-03 17:00 | 4.6956 | 4.9426 | 108.0047 | 660.779 | 9911.6847
2020-11-03 18:00 | 4.9105 | 5.1688 | 112.5771 | 769.7138 | 11545.7073
2020-11-03 19:00 | 4.6189 | 4.8619 | 118.9192 | 626.7011 | 9400.5167
2020-11-03 20:00 | 4.3977 | 4.629 | 128.6392 | 528.4261 | 7926.3919
2020-11-03 21:00 | 4.3074 | 4.5339 | 134.809 | 488.3118 | 7324.6776
2020-11-03 22:00 | 4.0832 | 4.2979 | 137.2674 | 402.8701 | 6043.0519
2020-11-03 23:00 | 4.1149 | 4.3313 | 136.1615 | 414.6277 | 6219.4153
2020-11-04 00:00 | 3.7973 | 3.997 | 139.6865 | 297.1428 | 4457.1415
2020-11-04 01:00 | 3.1808 | 3.3481 | 139.6574 | 122.4866 | 1837.2995
2020-11-04 02:00 | 2.4342 | 2.5622 | 134.7448 | 0 | 0
2020-11-04 03:00 | 1.7451 | 1.8369 | 132.5188 | 0 | 0
2020-11-04 04:00 | 1.5874 | 1.6709 | 120.8924 | 0 | 0
2020-11-04 05:00 | 1.9176 | 2.0185 | 113.3162 | 0 | 0
2020-11-04 06:00 | 2.2131 | 2.3295 | 108.7611 | 0 | 0
2020-11-04 07:00 | 2.3448 | 2.4681 | 110.9868 | 0 | 0
2020-11-04 08:00 | 2.1157 | 2.227 | 118.7826 | 0 | 0
2020-11-04 09:00 | 3.0313 | 3.1907 | 134.7638 | 88.8059 | 1332.0885
2020-11-04 10:00 | 4.1535 | 4.372 | 146.8819 | 428.9383 | 6434.0751
2020-11-04 11:00 | 4.3104 | 4.5371 | 155.6509 | 489.6628 | 7344.9417
2020-11-04 12:00 | 3.5353 | 3.7213 | 167.4103 | 218.2801 | 3274.2018
2020-11-04 13:00 | 3.2331 | 3.4032 | 170.8777 | 134.2778 | 2014.1669
2020-11-04 14:00 | 2.8207 | 2.969 | 162.9704 | 0 | 0
2020-11-04 15:00 | 3.4485 | 3.6298 | 150.0874 | 192.1352 | 2882.028
2020-11-04 16:00 | 3.7489 | 3.9461 | 146.1141 | 282.584 | 4238.7599
2020-11-04 17:00 | 4.0254 | 4.2371 | 147.8476 | 381.4533 | 5721.7995
2020-11-04 18:00 | 4.2926 | 4.5184 | 151.6524 | 481.7607 | 7226.4104
2020-11-04 19:00 | 4.2849 | 4.5102 | 156.5622 | 478.3102 | 7174.6523
2020-11-04 20:00 | 4.1915 | 4.4119 | 164.8951 | 442.9914 | 6644.8714
2020-11-04 21:00 | 3.9955 | 4.2056 | 177.7531 | 370.3703 | 5555.5543
2020-11-04 22:00 | 3.8733 | 4.077 | 205.5685 | 325.0966 | 4876.4497
2020-11-04 23:00 | 3.8395 | 4.0414 | 223.3254 | 312.5811 | 4688.7168
2020-11-05 00:00 | 3.572 | 3.7599 | 236.1412 | 229.337 | 3440.0551
2020-11-05 01:00 | 3.4868 | 3.6702 | 239.9654 | 203.6829 | 3055.2437
2020-11-05 02:00 | 4.1979 | 4.4187 | 248.1163 | 445.3868 | 6680.8021
2020-11-05 03:00 | 4.6965 | 4.9435 | 254.0123 | 661.1633 | 9917.4495
2020-11-05 04:00 | 4.9621 | 5.2231 | 256.83 | 796.986 | 11954.7907
2020-11-05 05:00 | 5.1022 | 5.3705 | 262.6054 | 871.0082 | 13065.1232
2020-11-05 06:00 | 5.1945 | 5.4677 | 269.3037 | 919.7818 | 13796.7269
2020-11-05 07:00 | 4.8523 | 5.1075 | 278.2222 | 738.9549 | 11084.3234
2020-11-05 08:00 | 4.5821 | 4.8231 | 288.5226 | 610.3388 | 9155.0819
2020-11-05 09:00 | 4.7474 | 4.9971 | 304.7309 | 683.7574 | 10256.3607
2020-11-05 10:00 | 6.899 | 7.2619 | 312.7639 | 2232.0705 | 33481.0575
2020-11-05 11:00 | 7.6384 | 8.0401 | 320.4015 | 3028.1853 | 45422.7797
2020-11-05 12:00 | 6.6128 | 6.9605 | 316.7393 | 1955.9637 | 29339.4552
2020-11-05 13:00 | 6.8581 | 7.2188 | 314.6341 | 2191.9445 | 32879.167
2020-11-05 14:00 | 7.0533 | 7.4242 | 314.3749 | 2383.3695 | 35750.5427
2020-11-05 15:00 | 6.75 | 7.105 | 314.0848 | 2085.8617 | 31287.9256
2020-11-05 16:00 | 6.6223 | 6.9706 | 311.793 | 1964.1051 | 29461.5768
2020-11-05 17:00 | 6.7011 | 7.0535 | 310.3405 | 2037.9001 | 30568.5013
2020-11-05 18:00 | 6.7366 | 7.0909 | 307.4395 | 2072.7479 | 31091.2189
2020-11-05 19:00 | 6.8439 | 7.2039 | 301.0202 | 2178.0111 | 32670.1672
2020-11-05 20:00 | 6.7844 | 7.1412 | 293.2214 | 2119.6092 | 31794.1385
2020-11-05 21:00 | 7.1268 | 7.5016 | 287.8121 | 2455.7025 | 36835.5379
2020-11-05 22:00 | 8.4914 | 8.938 | 288.1349 | 4040.0412 | 60600.6187
2020-11-05 23:00 | 8.7243 | 9.1831 | 288.7811 | 4305.9208 | 64588.8127
2020-11-06 00:00 | 8.7173 | 9.1758 | 287.9125 | 4298.0956 | 64471.4344
2020-11-06 01:00 | 8.6684 | 9.1243 | 288.4033 | 4242.9634 | 63644.4506
2020-11-06 02:00 | 8.6587 | 9.1141 | 286.7941 | 4232.124 | 63481.8607
2020-11-06 03:00 | 8.6751 | 9.1314 | 284.905 | 4250.57 | 63758.5495
2020-11-06 04:00 | 8.5549 | 9.0048 | 286.7556 | 4115.1546 | 61727.3189
2020-11-06 05:00 | 8.3649 | 8.8048 | 284.7778 | 3889.8172 | 58347.2584
2020-11-06 06:00 | 8.5063 | 8.9537 | 283.1397 | 4057.7849 | 60866.7731
2020-11-06 07:00 | 8.2717 | 8.7068 | 284.4608 | 3779.2499 | 56688.7491
2020-11-06 08:00 | 9.1244 | 9.6043 | 285.4359 | 4730.7322 | 70960.9824
2020-11-06 09:00 | 8.4432 | 8.8873 | 285.8428 | 3982.8205 | 59742.3071
2020-11-06 10:00 | 7.5709 | 7.9691 | 285.5095 | 2950.3094 | 44254.641
2020-11-06 11:00 | 7.3225 | 7.7076 | 282.5404 | 2673.6168 | 40104.2524
2020-11-06 12:00 | 7.563 | 7.9607 | 283.553 | 2941.4504 | 44121.7564
2020-11-06 13:00 | 8.6531 | 9.1082 | 289.916 | 4225.8052 | 63387.0777
2020-11-06 14:00 | 8.0406 | 8.4635 | 292.7218 | 3504.856 | 52572.8406
2020-11-06 15:00 | 7.8227 | 8.2342 | 296.4905 | 3246.6844 | 48700.2656
2020-11-06 16:00 | 7.6334 | 8.0348 | 301.753 | 3022.2179 | 45333.2691
2020-11-06 17:00 | 7.7051 | 8.1103 | 304.4484 | 3107.201 | 46608.0146
2020-11-06 18:00 | 7.6825 | 8.0865 | 303.4464 | 3080.4208 | 46206.3124
2020-11-06 19:00 | 7.7984 | 8.2086 | 304.3857 | 3217.8383 | 48267.5745
2020-11-06 20:00 | 7.9877 | 8.4078 | 308.4328 | 3442.1875 | 51632.813
2020-11-06 21:00 | 7.9626 | 8.3814 | 312.0969 | 3412.4094 | 51186.1413
2020-11-06 22:00 | 7.7692 | 8.1778 | 315.2337 | 3183.2075 | 47748.1123
2020-11-06 23:00 | 7.4938 | 7.888 | 310.5441 | 2864.4777 | 42967.1649
2020-11-07 00:00 | 7.5445 | 7.9413 | 311.2226 | 2920.8532 | 43812.7985
2020-11-07 01:00 | 7.1956 | 7.5741 | 313.149 | 2532.3818 | 37985.727
2020-11-07 02:00 | 6.9213 | 7.2854 | 309.9864 | 2253.9534 | 33809.3011
2020-11-07 03:00 | 6.9563 | 7.3222 | 305.5195 | 2288.2528 | 34323.7914
2020-11-07 04:00 | 7.1212 | 7.4958 | 304.2537 | 2450.0424 | 36750.6367
2020-11-07 05:00 | 7.1919 | 7.5701 | 300.3505 | 2528.1875 | 37922.8129
2020-11-07 06:00 | 7.5527 | 7.95 | 299.4524 | 2930.0591 | 43950.8872
2020-11-07 07:00 | 8.3802 | 8.8209 | 305.252 | 3907.9987 | 58619.9806
2020-11-07 08:00 | 8.2063 | 8.638 | 307.2504 | 3701.6098 | 55524.1471
2020-11-07 09:00 | 7.6271 | 8.0282 | 308.3277 | 3014.799 | 45221.985
2020-11-07 10:00 | 6.9083 | 7.2717 | 307.6741 | 2241.1925 | 33617.8877
2020-11-07 11:00 | 6.7487 | 7.1037 | 307.795 | 2084.6251 | 31269.376
2020-11-07 12:00 | 6.4573 | 6.7969 | 305.2287 | 1823.1009 | 27346.5137
2020-11-07 13:00 | 6.1154 | 6.437 | 301.7992 | 1537.9014 | 23068.5205
2020-11-07 14:00 | 6.0091 | 6.3251 | 292.118 | 1459.5812 | 21893.7175
2020-11-07 15:00 | 6.3375 | 6.6708 | 289.4189 | 1720.6714 | 25810.0703
2020-11-07 16:00 | 6.4027 | 6.7394 | 289.4255 | 1776.4164 | 26646.2455
2020-11-07 17:00 | 6.2623 | 6.5917 | 288.9936 | 1656.4663 | 24846.9952
2020-11-07 18:00 | 5.9486 | 6.2615 | 286.1653 | 1415.0151 | 21225.2262
2020-11-07 19:00 | 5.7886 | 6.0931 | 283.0272 | 1297.1678 | 19457.5171
2020-11-07 20:00 | 5.7271 | 6.0283 | 281.3345 | 1251.798 | 18776.9705
2020-11-07 21:00 | 5.6655 | 5.9635 | 279.5282 | 1210.3975 | 18155.9626
2020-11-07 22:00 | 4.7871 | 5.0389 | 277.3025 | 704.5097 | 10567.6452
2020-11-07 23:00 | 4.6518 | 4.8965 | 274.8965 | 641.3144 | 9619.7163
2020-11-08 00:00 | 4.4624 | 4.697 | 270.3227 | 557.1537 | 8357.3057
2020-11-08 01:00 | 4.5492 | 4.7885 | 257.8678 | 595.7347 | 8936.0209
2020-11-08 02:00 | 4.8241 | 5.0778 | 249.4192 | 724.0793 | 10861.1889
2020-11-08 03:00 | 4.9714 | 5.2329 | 248.2108 | 801.9028 | 12028.5419
2020-11-08 04:00 | 5.5701 | 5.8631 | 252.9001 | 1150.9418 | 17264.1263
2020-11-08 05:00 | 6.0927 | 6.4132 | 255.4087 | 1521.2342 | 22818.5129
2020-11-08 06:00 | 6.4319 | 6.7702 | 256.4506 | 1801.4114 | 27021.171
2020-11-08 07:00 | 6.3949 | 6.7313 | 259.507 | 1769.7817 | 26546.7256
2020-11-08 08:00 | 6.2052 | 6.5316 | 262.0318 | 1607.6301 | 24114.451
2020-11-08 09:00 | 6.1623 | 6.4864 | 262.9905 | 1572.4934 | 23587.4013
2020-11-08 10:00 | 5.5546 | 5.8468 | 263.0843 | 1141.2831 | 17119.2471
2020-11-08 11:00 | 5.7348 | 6.0364 | 270.2956 | 1257.4954 | 18862.4315
2020-11-08 12:00 | 5.6227 | 5.9184 | 278.2517 | 1183.6938 | 17755.4067
2020-11-08 13:00 | 5.2204 | 5.4949 | 284.2596 | 933.4623 | 14001.9342
2020-11-08 14:00 | 4.6046 | 4.8468 | 288.1904 | 620.3538 | 9305.3064
2020-11-08 15:00 | 4.2213 | 4.4433 | 291.1791 | 454.0463 | 6810.6946
2020-11-08 16:00 | 4.2883 | 4.5138 | 290.4357 | 479.8422 | 7197.6326
2020-11-08 17:00 | 4.4542 | 4.6885 | 294.2723 | 553.5389 | 8303.0836
2020-11-08 18:00 | 4.6015 | 4.8435 | 306.4503 | 618.975 | 9284.6253
2020-11-08 19:00 | 4.4541 | 4.6884 | 323.2348 | 553.4981 | 8302.471
2020-11-08 20:00 | 3.8686 | 4.0721 | 336.7578 | 323.373 | 4850.595
2020-11-08 21:00 | 3.1905 | 3.3583 | 347.3932 | 124.6855 | 1870.2829
2020-11-08 22:00 | 3.2105 | 3.3794 | 343.0457 | 129.1868 | 1937.8017
2020-11-08 23:00 | 2.9807 | 3.1374 | 354.8331 | 77.4101 | 1161.1513
2020-11-09 00:00 | 3.1897 | 3.3574 | 4.923 | 124.4863 | 1867.2944
2020-11-09 01:00 | 3.5699 | 3.7576 | 5.9968 | 228.6822 | 3430.2335
2020-11-09 02:00 | 3.7895 | 3.9888 | 10.4909 | 294.7932 | 4421.8977
2020-11-09 03:00 | 3.603 | 3.7925 | 16.5445 | 238.6528 | 3579.7922
2020-11-09 04:00 | 3.65 | 3.8419 | 19.5348 | 252.7923 | 3791.8848
2020-11-09 05:00 | 3.3603 | 3.537 | 24.3193 | 165.5853 | 2483.78
2020-11-09 06:00 | 2.8173 | 2.9655 | 28.2474 | 0 | 0
2020-11-09 07:00 | 2.2882 | 2.4085 | 37.0489 | 0 | 0
2020-11-09 08:00 | 1.9266 | 2.0279 | 48.2635 | 0 | 0
2020-11-09 09:00 | 1.7627 | 1.8554 | 53.2013 | 0 | 0
2020-11-09 10:00 | 1.5212 | 1.6012 | 43.5637 | 0 | 0
2020-11-09 11:00 | 1.612 | 1.6968 | 19.4963 | 0 | 0
2020-11-09 12:00 | 1.9627 | 2.066 | 5.5158 | 0 | 0
2020-11-09 13:00 | 2.235 | 2.3526 | 357.8293 | 0 | 0
2020-11-09 14:00 | 2.0749 | 2.1841 | 336.8126 | 0 | 0
2020-11-09 15:00 | 2.3097 | 2.4311 | 327.2397 | 0 | 0
2020-11-09 16:00 | 2.955 | 3.1104 | 327.0728 | 71.6301 | 1074.4513
2020-11-09 17:00 | 3.3565 | 3.533 | 329.9159 | 164.4457 | 2466.6852
2020-11-09 18:00 | 3.379 | 3.5567 | 329.4921 | 171.2156 | 2568.2345
2020-11-09 19:00 | 3.6687 | 3.8617 | 331.2266 | 258.4395 | 3876.5931
2020-11-09 20:00 | 3.9011 | 4.1063 | 335.4998 | 335.4183 | 5031.2742
2020-11-09 21:00 | 4.2581 | 4.4821 | 344.4919 | 467.682 | 7015.23
2020-11-09 22:00 | 4.1702 | 4.3896 | 344.5159 | 435.1219 | 6526.8285
2020-11-09 23:00 | 4.2804 | 4.5056 | 352.0469 | 476.3515 | 7145.2729
2020-11-10 00:00 | 4.3946 | 4.6257 | 0.15398 | 527.0492 | 7905.738
2020-11-10 01:00 | 4.2537 | 4.4774 | 3.1526 | 466.0378 | 6990.5671
2020-11-10 02:00 | 4.2773 | 4.5023 | 5.7318 | 474.9711 | 7124.5665
2020-11-10 03:00 | 4.255 | 4.4788 | 9.0357 | 466.5268 | 6997.9023
2020-11-10 04:00 | 4.279 | 4.5041 | 10.9021 | 475.7216 | 7135.8233
2020-11-10 05:00 | 3.9774 | 4.1866 | 13.6239 | 363.6703 | 5455.0551
2020-11-10 06:00 | 3.7014 | 3.896 | 18.0447 | 268.2632 | 4023.9482
2020-11-10 07:00 | 2.6402 | 2.7791 | 17.0263 | 0 | 0
2020-11-10 08:00 | 2.2721 | 2.3916 | 11.2613 | 0 | 0
2020-11-10 09:00 | 2.0762 | 2.1854 | 9.2737 | 0 | 0
2020-11-10 10:00 | 1.9888 | 2.0934 | 15.427 | 0 | 0
2020-11-10 11:00 | 1.8212 | 1.917 | 15.8891 | 0 | 0
2020-11-10 12:00 | 1.7274 | 1.8182 | 7.6525 | 0 | 0
2020-11-10 13:00 | 2.1573 | 2.2708 | 4.886 | 0 | 0
2020-11-10 14:00 | 2.4579 | 2.5872 | 3.2446 | 0 | 0
2020-11-10 15:00 | 2.8433 | 2.9928 | 5.5873 | 0 | 0
2020-11-10 16:00 | 3.2037 | 3.3722 | 10.4352 | 127.6431 | 1914.6465
2020-11-10 17:00 | 3.3721 | 3.5495 | 15.0348 | 169.1584 | 2537.3765
2020-11-10 18:00 | 3.1838 | 3.3513 | 19.6269 | 123.1725 | 1847.587
2020-11-10 19:00 | 3.0172 | 3.1759 | 22.7025 | 85.6477 | 1284.7162
2020-11-10 20:00 | 2.8742 | 3.0253 | 24.4834 | 53.4243 | 801.3652
2020-11-10 21:00 | 2.5241 | 2.6568 | 24.1907 | 0 | 0
2020-11-10 22:00 | 2.7634 | 2.9087 | 32.6236 | 0 | 0
2020-11-10 23:00 | 2.5653 | 2.7002 | 39.7145 | 0 | 0
2020-11-11 00:00 | 2.2719 | 2.3914 | 46.395 | 0 | 0
2020-11-11 01:00 | 2.0487 | 2.1564 | 49.869 | 0 | 0
2020-11-11 02:00 | 1.7098 | 1.7998 | 47.7148 | 0 | 0
2020-11-11 03:00 | 1.693 | 1.782 | 46.7263 | 0 | 0
2020-11-11 04:00 | 1.842 | 1.9388 | 54.3774 | 0 | 0
2020-11-11 05:00 | 1.879 | 1.9778 | 62.3402 | 0 | 0
2020-11-11 06:00 | 1.9869 | 2.0914 | 73.6605 | 0 | 0
2020-11-11 07:00 | 1.5686 | 1.6511 | 86.7773 | 0 | 0
2020-11-11 08:00 | 1.1031 | 1.1611 | 101.3376 | 0 | 0
2020-11-11 09:00 | 1.2005 | 1.2637 | 105.0941 | 0 | 0
2020-11-11 10:00 | 1.6421 | 1.7285 | 105.7107 | 0 | 0
2020-11-11 11:00 | 1.511 | 1.5905 | 102.2375 | 0 | 0
2020-11-11 12:00 | 1.3288 | 1.3987 | 96.1769 | 0 | 0
2020-11-11 13:00 | 1.3929 | 1.4661 | 90.4582 | 0 | 0
2020-11-11 14:00 | 2.0876 | 2.1974 | 92.7646 | 0 | 0
2020-11-11 15:00 | 2.7837 | 2.9302 | 97.8519 | 0 | 0
2020-11-11 16:00 | 3.3193 | 3.4939 | 104.7725 | 153.6888 | 2305.3319
2020-11-11 17:00 | 3.5741 | 3.7621 | 109.0614 | 229.9689 | 3449.5335
2020-11-11 18:00 | 4.0158 | 4.227 | 110.976 | 377.8908 | 5668.3622
2020-11-11 19:00 | 4.2036 | 4.4247 | 115.5282 | 447.5072 | 6712.6084
2020-11-11 20:00 | 4.2359 | 4.4587 | 121.1135 | 459.4615 | 6891.9221
2020-11-11 21:00 | 4.2978 | 4.5239 | 128.4573 | 484.0655 | 7260.9826
2020-11-11 22:00 | 4.4172 | 4.6495 | 137.103 | 537.1086 | 8056.629
2020-11-11 23:00 | 4.5528 | 4.7922 | 140.2901 | 597.3264 | 8959.8967
2020-11-12 00:00 | 4.5973 | 4.8391 | 139.6978 | 617.0824 | 9256.2364
2020-11-12 01:00 | 4.6305 | 4.874 | 141.0213 | 631.8357 | 9477.5353
2020-11-12 02:00 | 4.7868 | 5.0386 | 145.9069 | 704.3653 | 10565.4795
2020-11-12 03:00 | 4.8317 | 5.0858 | 148.8296 | 728.0732 | 10921.098
2020-11-12 04:00 | 4.692 | 4.9388 | 152.8394 | 659.1736 | 9887.6045
2020-11-12 05:00 | 4.6278 | 4.8712 | 155.723 | 630.658 | 9459.8697
2020-11-12 06:00 | 4.6077 | 4.85 | 156.9196 | 621.7003 | 9325.504
2020-11-12 07:00 | 4.118 | 4.3346 | 155.9886 | 415.79 | 6236.8507
2020-11-12 08:00 | 3.6216 | 3.8121 | 155.9286 | 244.2634 | 3663.9511
2020-11-12 09:00 | 3.47 | 3.6525 | 154.9443 | 198.6065 | 2979.0971
2020-11-12 10:00 | 4.1179 | 4.3345 | 163.3807 | 415.7535 | 6236.303
2020-11-12 11:00 | 4.0726 | 4.2868 | 159.3903 | 398.9452 | 5984.1785
2020-11-12 12:00 | 4.3893 | 4.6202 | 151.7111 | 524.7204 | 7870.8059
2020-11-12 13:00 | 4.5751 | 4.8158 | 143.0637 | 607.2582 | 9108.8731
2020-11-12 14:00 | 4.6665 | 4.9119 | 136.64 | 647.8408 | 9717.6117
2020-11-12 15:00 | 5.0121 | 5.2757 | 134.0399 | 823.4191 | 12351.2863
2020-11-12 16:00 | 5.2024 | 5.476 | 136.9249 | 923.9598 | 13859.3977
2020-11-12 17:00 | 5.183 | 5.4556 | 141.7436 | 913.6938 | 13705.4067
2020-11-12 18:00 | 4.9237 | 5.1826 | 144.8196 | 776.6701 | 11650.052
2020-11-12 19:00 | 4.8387 | 5.0931 | 146.2632 | 731.7599 | 10976.3979
2020-11-12 20:00 | 4.9152 | 5.1737 | 149.5117 | 772.1895 | 11582.8421
2020-11-12 21:00 | 4.8189 | 5.0723 | 152.2527 | 721.299 | 10819.4844
2020-11-12 22:00 | 4.345 | 4.5735 | 156.272 | 505.037 | 7575.5557
2020-11-12 23:00 | 4.4811 | 4.7168 | 149.4295 | 565.4738 | 8482.1073
2020-11-13 00:00 | 4.4539 | 4.6881 | 145.1227 | 553.3842 | 8300.7637
2020-11-13 01:00 | 4.6135 | 4.8562 | 141.619 | 624.2988 | 9364.4815
2020-11-13 02:00 | 4.6172 | 4.8601 | 143.3207 | 625.9548 | 9389.3225
2020-11-13 03:00 | 4.7836 | 5.0352 | 143.1536 | 702.6808 | 10540.2125
2020-11-13 04:00 | 5.1557 | 5.4269 | 142.0505 | 899.2915 | 13489.3719
2020-11-13 05:00 | 5.3108 | 5.5901 | 141.4128 | 989.3291 | 14839.9366
2020-11-13 06:00 | 5.3024 | 5.5813 | 143.2244 | 984.1352 | 14762.0281
2020-11-13 07:00 | 5.3518 | 5.6332 | 146.7497 | 1014.8735 | 15223.102
2020-11-13 08:00 | 5.5399 | 5.8313 | 151.217 | 1132.1406 | 16982.1086
2020-11-13 09:00 | 5.3138 | 5.5933 | 151.4034 | 991.2053 | 14868.0791
2020-11-13 10:00 | 4.9909 | 5.2534 | 147.1653 | 812.2121 | 12183.1822
2020-11-13 11:00 | 5.0429 | 5.3082 | 146.3124 | 839.6965 | 12595.4482
2020-11-13 12:00 | 5.1701 | 5.4421 | 147.8549 | 906.9173 | 13603.7602
2020-11-13 13:00 | 5.5524 | 5.8445 | 148.5769 | 1139.9302 | 17098.9524
2020-11-13 14:00 | 6.1346 | 6.4573 | 152.331 | 1552.0953 | 23281.4302
2020-11-13 15:00 | 6.1045 | 6.4256 | 155.089 | 1529.9112 | 22948.6673
2020-11-13 16:00 | 6.2799 | 6.6102 | 160.5217 | 1671.4458 | 25071.6874
2020-11-13 17:00 | 6.0293 | 6.3464 | 165.927 | 1474.4752 | 22117.1287
2020-11-13 18:00 | 5.8603 | 6.1685 | 171.7593 | 1349.941 | 20249.1143
2020-11-13 19:00 | 6.137 | 6.4597 | 174.086 | 1553.8204 | 23307.3059
2020-11-13 20:00 | 5.8751 | 6.1841 | 180.9182 | 1360.8678 | 20413.0177
2020-11-13 21:00 | 5.563 | 5.8556 | 187.8946 | 1146.5201 | 17197.8013
2020-11-13 22:00 | 5.2256 | 5.5004 | 184.1677 | 936.2375 | 14043.563
2020-11-13 23:00 | 5.18 | 5.4525 | 183.3242 | 912.1469 | 13682.2039
2020-11-14 00:00 | 4.9927 | 5.2552 | 186.0425 | 813.1334 | 12197.001
2020-11-14 01:00 | 4.9484 | 5.2086 | 187.793 | 789.7287 | 11845.9305
2020-11-14 02:00 | 4.8277 | 5.0816 | 193.966 | 725.9731 | 10889.5969
2020-11-14 03:00 | 4.5949 | 4.8365 | 199.285 | 616.0158 | 9240.2368
2020-11-14 04:00 | 4.6188 | 4.8617 | 202.6465 | 626.6468 | 9399.702
2020-11-14 05:00 | 4.7859 | 5.0377 | 204.5963 | 703.907 | 10558.6057
2020-11-14 06:00 | 4.9358 | 5.1954 | 205.9785 | 783.1042 | 11746.563
2020-11-14 07:00 | 4.9465 | 5.2066 | 208.8344 | 788.717 | 11830.755
2020-11-14 08:00 | 5.0207 | 5.2847 | 213.6229 | 827.9247 | 12418.8705
2020-11-14 09:00 | 5.1124 | 5.3813 | 219.9095 | 876.393 | 13145.895
2020-11-14 10:00 | 4.6416 | 4.8857 | 222.4628 | 636.7628 | 9551.4424
2020-11-14 11:00 | 4.5122 | 4.7495 | 224.4833 | 579.2807 | 8689.2102
2020-11-14 12:00 | 4.4556 | 4.6899 | 224.6638 | 554.1484 | 8312.2254
2020-11-14 13:00 | 4.0066 | 4.2173 | 226.2686 | 374.4855 | 5617.2818
2020-11-14 14:00 | 3.956 | 4.164 | 228.8658 | 355.7331 | 5335.9967
2020-11-14 15:00 | 4.1918 | 4.4123 | 231.8817 | 443.1256 | 6646.8838
2020-11-14 16:00 | 4.458 | 4.6924 | 230.0851 | 555.2128 | 8328.1924
2020-11-14 17:00 | 4.7126 | 4.9605 | 226.8872 | 668.3331 | 10024.9961
2020-11-14 18:00 | 4.9582 | 5.219 | 225.5053 | 794.9223 | 11923.8343
2020-11-14 19:00 | 5.2215 | 5.4961 | 225.5959 | 934.0458 | 14010.6877
2020-11-14 20:00 | 5.4288 | 5.7144 | 226.2943 | 1062.9068 | 15943.6022
2020-11-14 21:00 | 5.4533 | 5.7401 | 225.9024 | 1078.1508 | 16172.2624
2020-11-14 22:00 | 5.5827 | 5.8763 | 222.8538 | 1158.7862 | 17381.7928
2020-11-14 23:00 | 5.6814 | 5.9802 | 219.6228 | 1220.2799 | 18304.1988
2020-11-15 00:00 | 5.7252 | 6.0264 | 218.3415 | 1250.45 | 18756.75
2020-11-15 01:00 | 5.6812 | 5.98 | 220.1898 | 1220.1747 | 18302.621
2020-11-15 02:00 | 5.3752 | 5.6579 | 222.435 | 1029.4698 | 15442.0471
2020-11-15 03:00 | 5.1764 | 5.4487 | 222.9879 | 910.224 | 13653.3595
2020-11-15 04:00 | 5.1455 | 5.4161 | 229.4749 | 893.8894 | 13408.3409
2020-11-15 05:00 | 5.1187 | 5.3879 | 238.7012 | 879.7275 | 13195.9128
2020-11-15 06:00 | 4.8588 | 5.1143 | 246.004 | 742.3939 | 11135.9081
2020-11-15 07:00 | 4.4666 | 4.7016 | 253.2715 | 559.0556 | 8385.8345
2020-11-15 08:00 | 4.329 | 4.5567 | 267.9103 | 497.9289 | 7468.9329
2020-11-15 09:00 | 4.4759 | 4.7113 | 286.1936 | 563.1754 | 8447.6317
2020-11-15 10:00 | 4.2248 | 4.447 | 288.3028 | 455.3482 | 6830.2229
2020-11-15 11:00 | 4.664 | 4.9093 | 298.4343 | 646.7081 | 9700.622
2020-11-15 12:00 | 4.186 | 4.4062 | 308.0757 | 440.9656 | 6614.4844
2020-11-15 13:00 | 2.6981 | 2.84 | 324.5905 | 0 | 0
2020-11-15 14:00 | 2.3304 | 2.453 | 349.1017 | 0 | 0
2020-11-15 15:00 | 2.571 | 2.7062 | 17.4583 | 0 | 0
2020-11-15 16:00 | 2.8862 | 3.038 | 36.1312 | 56.1335 | 842.0021
2020-11-15 17:00 | 3.1551 | 3.3211 | 48.6264 | 116.7098 | 1750.647
2020-11-15 18:00 | 3.3062 | 3.4801 | 52.1653 | 150.7368 | 2261.0523
2020-11-15 19:00 | 3.5159 | 3.7008 | 50.1429 | 212.4193 | 3186.2899
2020-11-15 20:00 | 3.8447 | 4.0469 | 52.0011 | 314.5117 | 4717.6755
2020-11-15 21:00 | 3.7992 | 3.999 | 55.7651 | 297.7148 | 4465.7215
2020-11-15 22:00 | 3.9105 | 4.1162 | 72.9219 | 338.9037 | 5083.5552
2020-11-15 23:00 | 3.791 | 3.9904 | 80.7577 | 295.2521 | 4428.7817
2020-11-16 00:00 | 4.0791 | 4.2936 | 85.1093 | 401.3631 | 6020.446
2020-11-16 01:00 | 4.3145 | 4.5415 | 90.511 | 491.5006 | 7372.5092
2020-11-16 02:00 | 4.3871 | 4.6179 | 97.2584 | 523.7346 | 7856.0191
2020-11-16 03:00 | 4.7054 | 4.9529 | 102.5623 | 665.131 | 9976.9652
2020-11-16 04:00 | 5.03 | 5.2946 | 107.4085 | 832.8896 | 12493.3447
2020-11-16 05:00 | 5.2288 | 5.5038 | 111.9113 | 938.2253 | 14073.3801
2020-11-16 06:00 | 5.6342 | 5.9305 | 115.4635 | 1190.8785 | 17863.1781
2020-11-16 07:00 | 6.448 | 6.7871 | 120.3219 | 1815.1529 | 27227.2931
2020-11-16 08:00 | 6.7255 | 7.0793 | 124.5456 | 2061.8745 | 30928.1177
2020-11-16 09:00 | 6.4382 | 6.7768 | 122.7621 | 1806.7818 | 27101.7263
2020-11-16 10:00 | 6.2598 | 6.589 | 115.8112 | 1654.281 | 24814.2154
2020-11-16 11:00 | 6.7014 | 7.0539 | 114.3552 | 2038.2383 | 30573.5739
2020-11-16 12:00 | 7.1228 | 7.4974 | 110.9645 | 2451.5857 | 36773.7853
2020-11-16 13:00 | 7.4103 | 7.8001 | 111.1309 | 2771.4695 | 41572.0428
2020-11-16 14:00 | 7.4683 | 7.8611 | 111.3101 | 2835.9989 | 42539.9838
2020-11-16 15:00 | 7.7382 | 8.1452 | 112.1622 | 3146.4877 | 47197.3155
2020-11-16 16:00 | 7.8633 | 8.2769 | 113.6727 | 3294.7666 | 49421.4991
2020-11-16 17:00 | 7.6867 | 8.0909 | 115.7497 | 3085.4047 | 46281.0711
2020-11-16 18:00 | 7.5257 | 7.9215 | 117.3819 | 2899.9193 | 43498.789
2020-11-16 19:00 | 7.4001 | 7.7893 | 119.2677 | 2760.0675 | 41401.0127
2020-11-16 20:00 | 7.5162 | 7.9115 | 120.8615 | 2889.4042 | 43341.0624
2020-11-16 21:00 | 7.5409 | 7.9375 | 123.192 | 2916.9069 | 43753.6041
2020-11-16 22:00 | 7.2579 | 7.6397 | 123.4714 | 2601.7509 | 39026.263
2020-11-16 23:00 | 7.0399 | 7.4101 | 122.376 | 2370.2596 | 35553.8945
2020-11-17 00:00 | 7.0111 | 7.3798 | 123.2543 | 2342.0091 | 35130.1364
2020-11-17 01:00 | 7.1371 | 7.5125 | 124.2605 | 2467.2101 | 37008.1515
2020-11-17 02:00 | 7.0587 | 7.43 | 124.4937 | 2388.7162 | 35830.7433
2020-11-17 03:00 | 6.8402 | 7.2 | 125.3888 | 2174.382 | 32615.7293
2020-11-17 04:00 | 6.7752 | 7.1315 | 125.8167 | 2110.584 | 31658.7607
2020-11-17 05:00 | 6.6798 | 7.0311 | 126.6882 | 2016.9667 | 30254.5002
2020-11-17 06:00 | 6.5511 | 6.8957 | 126.3081 | 1903.2772 | 28549.1581
2020-11-17 07:00 | 6.5305 | 6.874 | 128.9585 | 1885.6954 | 28285.4305
2020-11-17 08:00 | 6.7104 | 7.0633 | 136.4172 | 2047.0416 | 30705.6246
2020-11-17 09:00 | 6.3914 | 6.7276 | 140.7741 | 1766.777 | 26501.6549
2020-11-17 10:00 | 6.0034 | 6.3191 | 142.4813 | 1455.3779 | 21830.6681
2020-11-17 11:00 | 5.7517 | 6.0542 | 141.8681 | 1269.9528 | 19049.2918
2020-11-17 12:00 | 5.772 | 6.0755 | 141.6611 | 1284.8733 | 19273.0993
2020-11-17 13:00 | 5.7347 | 6.0363 | 138.5485 | 1257.4292 | 18861.4377
2020-11-17 14:00 | 5.6269 | 5.9229 | 139.3562 | 1186.3293 | 17794.939
2020-11-17 15:00 | 5.7257 | 6.0269 | 140.6774 | 1250.8234 | 18762.3511
2020-11-17 16:00 | 5.7736 | 6.0772 | 141.5352 | 1286.0567 | 19290.8507
2020-11-17 17:00 | 6.0019 | 6.3175 | 142.0576 | 1454.2837 | 21814.2549
2020-11-17 18:00 | 5.8818 | 6.1911 | 144.0032 | 1365.789 | 20486.8344
2020-11-17 19:00 | 6.0492 | 6.3673 | 145.8897 | 1489.128 | 22336.9207
2020-11-17 20:00 | 6.3642 | 6.6989 | 148.0136 | 1743.5081 | 26152.6219
2020-11-17 21:00 | 6.3363 | 6.6696 | 149.3829 | 1719.6787 | 25795.1804
2020-11-17 22:00 | 5.3933 | 5.6769 | 149.405 | 1040.7427 | 15611.1409
2020-11-17 23:00 | 5.5451 | 5.8367 | 151.9086 | 1135.3431 | 17030.1459
2020-11-18 00:00 | 5.0353 | 5.3002 | 152.1887 | 835.6789 | 12535.184
2020-11-18 01:00 | 4.954 | 5.2145 | 155.8833 | 792.6804 | 11890.2064
2020-11-18 02:00 | 5.1916 | 5.4646 | 157.676 | 918.2357 | 13773.536
2020-11-18 03:00 | 5.1261 | 5.3957 | 160.0306 | 883.6223 | 13254.335
2020-11-18 04:00 | 4.8435 | 5.0982 | 159.3244 | 734.3196 | 11014.7943
2020-11-18 05:00 | 5.0618 | 5.328 | 158.4822 | 849.6789 | 12745.1834
2020-11-18 06:00 | 5.3563 | 5.638 | 157.6294 | 1017.6882 | 15265.3228
2020-11-18 07:00 | 5.1082 | 5.3768 | 158.8123 | 874.1594 | 13112.3912
2020-11-18 08:00 | 5.1613 | 5.4327 | 165.0127 | 902.2295 | 13533.4431
2020-11-18 09:00 | 5.1964 | 5.4697 | 171.875 | 920.7917 | 13811.8759
2020-11-18 10:00 | 4.4256 | 4.6584 | 173.4529 | 540.8248 | 8112.3725
2020-11-18 11:00 | 4.5339 | 4.7723 | 173.3712 | 588.9199 | 8833.7986
2020-11-18 12:00 | 4.6617 | 4.9069 | 171.5917 | 645.7221 | 9685.8314
2020-11-18 13:00 | 4.7409 | 4.9903 | 171.1617 | 680.8882 | 10213.3234
2020-11-18 14:00 | 4.6915 | 4.9383 | 168.9977 | 658.9486 | 9884.2294
2020-11-18 15:00 | 5.0455 | 5.3109 | 172.242 | 841.0682 | 12616.0227
2020-11-18 16:00 | 5.628 | 5.924 | 177.4603 | 1187.0256 | 17805.3834
2020-11-18 17:00 | 5.6197 | 5.9152 | 183.5415 | 1181.8248 | 17727.3719
2020-11-18 18:00 | 5.9044 | 6.2149 | 182.7586 | 1382.4423 | 20736.6349
2020-11-18 19:00 | 6.3136 | 6.6456 | 185.8775 | 1700.2378 | 25503.5677
2020-11-18 20:00 | 6.3167 | 6.6489 | 188.1096 | 1702.9458 | 25544.187
2020-11-18 21:00 | 6.3987 | 6.7353 | 186.8959 | 1773.0432 | 26595.6479
2020-11-18 22:00 | 6.0676 | 6.3867 | 196.1096 | 1502.6978 | 22540.4671
2020-11-18 23:00 | 6.0575 | 6.3761 | 196.8082 | 1495.2724 | 22429.0863
2020-11-19 00:00 | 6.1886 | 6.5141 | 193.6967 | 1593.4712 | 23902.0683
2020-11-19 01:00 | 6.5391 | 6.8831 | 189.808 | 1893.0415 | 28395.6223
2020-11-19 02:00 | 6.8073 | 7.1653 | 190.3217 | 2142.0892 | 32131.3381
2020-11-19 03:00 | 6.8883 | 7.2506 | 189.3598 | 2221.5549 | 33323.3233
2020-11-19 04:00 | 7.1622 | 7.5389 | 186.6126 | 2495.1261 | 37426.8918
2020-11-19 05:00 | 7.3176 | 7.7025 | 186.4912 | 2668.1947 | 40022.9204
2020-11-19 06:00 | 7.5959 | 7.9954 | 188.6076 | 2978.1032 | 44671.5486
2020-11-19 07:00 | 7.4278 | 7.8184 | 183.921 | 2790.9184 | 41863.7753
2020-11-19 08:00 | 7.9041 | 8.3199 | 186.7485 | 3343.1626 | 50147.4397
2020-11-19 09:00 | 8.6629 | 9.1185 | 189.7923 | 4236.8455 | 63552.6829
2020-11-19 10:00 | 8.9247 | 9.3941 | 195.5314 | 4531.7079 | 67975.6192
2020-11-19 11:00 | 8.8781 | 9.345 | 194.5461 | 4479.1391 | 67187.0868
2020-11-19 12:00 | 8.6611 | 9.1166 | 192.58 | 4234.8078 | 63522.1173
2020-11-19 13:00 | 8.4882 | 8.9346 | 189.8733 | 4036.2325 | 60543.4873
2020-11-19 14:00 | 8.2443 | 8.6779 | 183.6947 | 3746.6508 | 56199.7618
2020-11-19 15:00 | 8.8185 | 9.2823 | 181.5876 | 4412.1123 | 66181.6848
2020-11-19 16:00 | 9.5234 | 10.0243 | 181.8242 | 5070.1956 | 76052.9336
2020-11-19 17:00 | 9.7006 | 10.2108 | 186.9245 | 5179.1131 | 77686.6963
2020-11-19 18:00 | 9.6761 | 10.185 | 190.2552 | 5164.0238 | 77460.3563
2020-11-19 19:00 | 9.7398 | 10.2521 | 191.3327 | 5203.2104 | 78048.1566
2020-11-19 20:00 | 9.7897 | 10.3046 | 193.1348 | 5233.9083 | 78508.6238
2020-11-19 21:00 | 9.5877 | 10.092 | 194.945 | 5109.7025 | 76645.537
2020-11-19 22:00 | 9.1927 | 9.6762 | 197.1387 | 4789.8194 | 71847.2914
2020-11-19 23:00 | 8.3532 | 8.7926 | 195.964 | 3876.0072 | 58140.1076
2020-11-20 00:00 | 8.3989 | 8.8407 | 195.9924 | 3930.2837 | 58954.2554
2020-11-20 01:00 | 8.3317 | 8.7699 | 197.4977 | 3850.4863 | 57757.2942
2020-11-20 02:00 | 7.6779 | 8.0817 | 199.8663 | 3074.9796 | 46124.6938
2020-11-20 03:00 | 7.5053 | 7.9001 | 202.3703 | 2877.2749 | 43159.1237
2020-11-20 04:00 | 7.2328 | 7.6133 | 206.622 | 2573.823 | 38607.3453
2020-11-20 05:00 | 6.8419 | 7.2018 | 207.9336 | 2176.0402 | 32640.6029
2020-11-20 06:00 | 6.5418 | 6.8859 | 207.6416 | 1895.3359 | 28430.0389
2020-11-20 07:00 | 6.5322 | 6.8758 | 209.9861 | 1887.1569 | 28307.3538
2020-11-20 08:00 | 6.3081 | 6.6398 | 212.2419 | 1695.5352 | 25433.0279
2020-11-20 09:00 | 5.7687 | 6.0721 | 213.5957 | 1282.4626 | 19236.9391
2020-11-20 10:00 | 5.191 | 5.464 | 221.2921 | 917.9279 | 13768.9188
2020-11-20 11:00 | 4.7648 | 5.0154 | 241.5934 | 692.7134 | 10390.7016
2020-11-20 12:00 | 4.1901 | 4.4104 | 278.6417 | 442.4712 | 6637.0684
2020-11-20 13:00 | 5.4285 | 5.714 | 312.3912 | 1062.692 | 15940.3798
2020-11-20 14:00 | 6.981 | 7.3481 | 327.8043 | 2312.4659 | 34686.9887
2020-11-20 15:00 | 7.8804 | 8.2949 | 331.1088 | 3315.0401 | 49725.6008
2020-11-20 16:00 | 8.1581 | 8.5872 | 332.5787 | 3644.3824 | 54665.7355
2020-11-20 17:00 | 8.1895 | 8.6202 | 334.6543 | 3681.5822 | 55223.7336
2020-11-20 18:00 | 7.9126 | 8.3287 | 338.0617 | 3353.1574 | 50297.3604
2020-11-20 19:00 | 7.623 | 8.0239 | 339.0528 | 3009.9079 | 45148.6189
2020-11-20 20:00 | 7.6544 | 8.057 | 338.3348 | 3047.1337 | 45707.0058
2020-11-20 21:00 | 7.7886 | 8.1982 | 337.865 | 3206.1798 | 48092.6966
2020-11-20 22:00 | 8.4095 | 8.8518 | 337.8623 | 3942.8517 | 59142.7752
2020-11-20 23:00 | 7.9974 | 8.418 | 337.3577 | 3453.7151 | 51805.726
2020-11-21 00:00 | 7.7608 | 8.1689 | 336.297 | 3173.2272 | 47598.4073
2020-11-21 01:00 | 7.6245 | 8.0255 | 334.5057 | 3011.7326 | 45175.9891
2020-11-21 02:00 | 7.6219 | 8.0227 | 332.9502 | 3008.6097 | 45129.1454
2020-11-21 03:00 | 7.3764 | 7.7643 | 333.824 | 2733.6802 | 41005.2037
2020-11-21 04:00 | 7.3376 | 7.7235 | 330.4593 | 2690.469 | 40357.0347
2020-11-21 05:00 | 7.2862 | 7.6694 | 326.6945 | 2633.2398 | 39498.597
2020-11-21 06:00 | 6.7584 | 7.1139 | 324.8799 | 2094.1257 | 31411.8862
2020-11-21 07:00 | 5.9332 | 6.2453 | 324.5491 | 1403.6966 | 21055.4495
2020-11-21 08:00 | 5.6734 | 5.9717 | 326.2952 | 1215.2735 | 18229.1032
2020-11-21 09:00 | 6.1699 | 6.4944 | 328.998 | 1578.084 | 23671.2605
2020-11-21 10:00 | 7.6524 | 8.0549 | 333.2586 | 3044.7734 | 45671.6003
2020-11-21 11:00 | 7.3044 | 7.6886 | 331.4575 | 2653.5255 | 39802.8818
2020-11-21 12:00 | 6.4645 | 6.8045 | 327.2095 | 1829.2143 | 27438.2139
2020-11-21 13:00 | 5.4728 | 5.7607 | 326.183 | 1090.3215 | 16354.8223
2020-11-21 14:00 | 5.0426 | 5.3078 | 325.8055 | 839.5158 | 12592.737
2020-11-21 15:00 | 4.7759 | 5.0271 | 321.9232 | 698.5802 | 10478.7028
2020-11-21 16:00 | 4.7637 | 5.0143 | 319.7637 | 692.1644 | 10382.4667
2020-11-21 17:00 | 4.5512 | 4.7906 | 318.2602 | 596.6191 | 8949.2866
2020-11-21 18:00 | 4.4535 | 4.6877 | 311.6116 | 553.2257 | 8298.3857
2020-11-21 19:00 | 4.7478 | 4.9976 | 308.0372 | 683.9687 | 10259.5299
2020-11-21 20:00 | 4.4226 | 4.6552 | 304.3834 | 539.4895 | 8092.3429
2020-11-21 21:00 | 4.4789 | 4.7144 | 294.0931 | 564.4972 | 8467.4586
2020-11-21 22:00 | 4.8185 | 5.072 | 295.8162 | 721.1294 | 10816.9403
2020-11-21 23:00 | 4.5253 | 4.7633 | 289.8316 | 585.1041 | 8776.5609
2020-11-22 00:00 | 4.5929 | 4.8345 | 279.5379 | 615.161 | 9227.4156
2020-11-22 01:00 | 4.6333 | 4.877 | 265.524 | 633.096 | 9496.4402
2020-11-22 02:00 | 4.6081 | 4.8504 | 252.9848 | 621.8788 | 9328.1824
2020-11-22 03:00 | 5.2401 | 5.5157 | 245.6103 | 945.3149 | 14179.724
2020-11-22 04:00 | 5.8007 | 6.1058 | 239.805 | 1306.0535 | 19590.8032
2020-11-22 05:00 | 6.354 | 6.6881 | 238.0315 | 1734.7763 | 26021.6441
2020-11-22 06:00 | 6.9639 | 7.3302 | 232.8784 | 2295.7192 | 34435.7875
2020-11-22 07:00 | 7.3126 | 7.6972 | 225.2009 | 2662.6715 | 39940.072
2020-11-22 08:00 | 7.8439 | 8.2564 | 227.8655 | 3271.7135 | 49075.7031
2020-11-22 09:00 | 8.0247 | 8.4467 | 229.3743 | 3485.9961 | 52289.9412
2020-11-22 10:00 | 7.5712 | 7.9694 | 226.6069 | 2950.6027 | 44259.0407
2020-11-22 11:00 | 7.859 | 8.2723 | 229.2745 | 3289.6434 | 49344.6508
2020-11-22 12:00 | 8.0579 | 8.4817 | 229.596 | 3525.4093 | 52881.1398
2020-11-22 13:00 | 8.9896 | 9.4624 | 237.8351 | 4604.7455 | 69071.1831
2020-11-22 14:00 | 9.0523 | 9.5284 | 239.4873 | 4668.374 | 70025.6096
2020-11-22 15:00 | 9.3107 | 9.8004 | 239.7839 | 4891.9508 | 73379.2624
2020-11-22 16:00 | 9.674 | 10.1828 | 239.6285 | 5162.7548 | 77441.3227
2020-11-22 17:00 | 9.9829 | 10.508 | 240.3619 | 5351.0389 | 80265.583
2020-11-22 18:00 | 10.2307 | 10.7687 | 244.5785 | 5450.6565 | 81759.8482
2020-11-22 19:00 | 10.2463 | 10.7852 | 249.7463 | 5456.9282 | 81853.9233
2020-11-22 20:00 | 10.2806 | 10.8213 | 252.522 | 5470.7195 | 82060.7928
2020-11-22 21:00 | 10.5118 | 11.0647 | 257.0498 | 5553.624 | 83304.36
2020-11-22 22:00 | 10.6074 | 11.1652 | 261.1317 | 5576.3447 | 83645.1711
2020-11-22 23:00 | 10.6328 | 11.1921 | 268.5188 | 5582.4081 | 83736.1216
2020-11-23 00:00 | 10.4269 | 10.9753 | 274.9726 | 5529.5797 | 82943.6953
2020-11-23 01:00 | 9.6834 | 10.1927 | 279.843 | 5168.5545 | 77528.3179
2020-11-23 02:00 | 8.9826 | 9.455 | 280.8038 | 4596.8671 | 68953.0061
2020-11-23 03:00 | 8.6048 | 9.0573 | 278.9739 | 4171.3384 | 62570.0759
2020-11-23 04:00 | 8.2043 | 8.6358 | 276.7188 | 3699.1586 | 55487.3784
2020-11-23 05:00 | 7.9315 | 8.3487 | 273.1971 | 3375.6254 | 50634.3809
2020-11-23 06:00 | 7.6738 | 8.0774 | 270.3752 | 3070.1463 | 46052.1943
2020-11-23 07:00 | 7.4232 | 7.8136 | 266.8443 | 2785.8253 | 41787.3795
2020-11-23 08:00 | 6.8062 | 7.1642 | 259.2835 | 2141.0254 | 32115.3815
2020-11-23 09:00 | 7.0208 | 7.3901 | 257.0899 | 2351.5582 | 35273.3731
2020-11-23 10:00 | 6.9572 | 7.3231 | 252.9945 | 2289.1138 | 34336.7063
2020-11-23 11:00 | 6.962 | 7.3282 | 250.9782 | 2293.8426 | 34407.6385
2020-11-23 12:00 | 6.7213 | 7.0748 | 247.0928 | 2057.6731 | 30865.097
2020-11-23 13:00 | 7.4671 | 7.8598 | 253.4868 | 2834.6883 | 42520.3239
2020-11-23 14:00 | 7.567 | 7.965 | 252.4805 | 2946.007 | 44190.1047
2020-11-23 15:00 | 7.5747 | 7.9731 | 251.751 | 2954.5249 | 44317.8732
2020-11-23 16:00 | 8.1228 | 8.55 | 255.8471 | 3602.368 | 54035.5194
2020-11-23 17:00 | 8.5574 | 9.0075 | 260.6039 | 4117.9876 | 61769.8136
2020-11-23 18:00 | 8.4864 | 8.9328 | 262.0097 | 4034.1606 | 60512.4084
2020-11-23 19:00 | 8.7712 | 9.2325 | 265.8757 | 4358.7977 | 65381.9655
2020-11-23 20:00 | 8.8922 | 9.3599 | 270.0404 | 4495.1065 | 67426.5971
2020-11-23 21:00 | 9.1425 | 9.6234 | 271.6143 | 4746.4161 | 71196.242
2020-11-23 22:00 | 9.6676 | 10.1761 | 273.2682 | 5158.8268 | 77382.4025
2020-11-23 23:00 | 9.7316 | 10.2434 | 276.0797 | 5198.1437 | 77972.1558
2020-11-24 00:00 | 9.7814 | 10.2958 | 279.8903 | 5228.7466 | 78431.1996
2020-11-24 01:00 | 9.8096 | 10.3256 | 284.9071 | 5246.1267 | 78691.9003
2020-11-24 02:00 | 9.3526 | 9.8445 | 287.062 | 4928.2107 | 73923.1599
2020-11-24 03:00 | 9.0423 | 9.5178 | 284.0143 | 4659.6576 | 69894.8646
2020-11-24 04:00 | 9.3158 | 9.8058 | 283.3271 | 4896.3779 | 73445.6692
2020-11-24 05:00 | 9.8234 | 10.34 | 287.019 | 5254.58 | 78818.7007
2020-11-24 06:00 | 10.0187 | 10.5457 | 291.1887 | 5365.4439 | 80481.659
2020-11-24 07:00 | 9.9693 | 10.4936 | 293.2957 | 5344.2851 | 80164.2764
2020-11-24 08:00 | 10.4068 | 10.9541 | 297.3779 | 5521.4775 | 82822.1622
2020-11-24 09:00 | 11.8171 | 12.4387 | 304.797 | 5699.8773 | 85498.16
2020-11-24 10:00 | 8.6684 | 9.1243 | 301.5836 | 4243.0432 | 63645.6481
2020-11-24 11:00 | 9.0959 | 9.5743 | 301.3371 | 4706.0558 | 70590.8371
2020-11-24 12:00 | 9.2936 | 9.7824 | 299.3878 | 4877.133 | 73156.9953
2020-11-24 13:00 | 8.8315 | 9.296 | 296.0466 | 4426.7004 | 66400.5062
2020-11-24 14:00 | 8.6137 | 9.0667 | 290.9673 | 4181.3946 | 62720.9197
2020-11-24 15:00 | 8.6573 | 9.1126 | 286.3761 | 4230.5343 | 63458.0138
2020-11-24 16:00 | 8.4804 | 8.9264 | 283.4826 | 4027.0249 | 60405.3734
2020-11-24 17:00 | 8.8541 | 9.3197 | 282.4176 | 4452.1325 | 66781.9875
2020-11-24 18:00 | 9.062 | 9.5386 | 283.3659 | 4676.7004 | 70150.5064
2020-11-24 19:00 | 8.8075 | 9.2707 | 282.3881 | 4399.6598 | 65994.8976
2020-11-24 20:00 | 8.4504 | 8.8949 | 281.1948 | 3991.4037 | 59871.0561
2020-11-24 21:00 | 8.2824 | 8.718 | 280.6842 | 3791.9433 | 56879.1491
2020-11-24 22:00 | 8.5672 | 9.0178 | 283.0558 | 4129.0041 | 61935.0621
2020-11-24 23:00 | 8.2411 | 8.6745 | 282.822 | 3742.8749 | 56143.1235
2020-11-25 00:00 | 8.0099 | 8.4312 | 283.6061 | 3468.524 | 52027.8593
2020-11-25 01:00 | 7.6577 | 8.0604 | 284.2894 | 3051.0663 | 45765.994
2020-11-25 02:00 | 7.4043 | 7.7938 | 283.0268 | 2764.7949 | 41471.923
2020-11-25 03:00 | 7.4329 | 7.8238 | 281.8862 | 2796.5974 | 41948.9605
2020-11-25 04:00 | 7.6789 | 8.0828 | 278.734 | 3076.2013 | 46143.0191
2020-11-25 05:00 | 8.1059 | 8.5322 | 277.3864 | 3582.3706 | 53735.5584
2020-11-25 06:00 | 8.5199 | 8.968 | 279.2463 | 4073.9367 | 61109.0509
2020-11-25 07:00 | 8.5494 | 8.9991 | 278.7351 | 4108.9743 | 61634.6148
2020-11-25 08:00 | 8.2295 | 8.6623 | 277.6698 | 3729.1147 | 55936.7209
2020-11-25 09:00 | 8.4393 | 8.8831 | 281.7335 | 3978.1697 | 59672.545
2020-11-25 10:00 | 7.2526 | 7.6341 | 281.5626 | 2595.8624 | 38937.9364
2020-11-25 11:00 | 7.2523 | 7.6337 | 285.0582 | 2595.4772 | 38932.1582
2020-11-25 12:00 | 7.579 | 7.9776 | 289.8809 | 2959.3174 | 44389.7614
2020-11-25 13:00 | 8.0338 | 8.4564 | 296.1902 | 3496.8685 | 52453.0278
2020-11-25 14:00 | 7.6436 | 8.0456 | 299.2956 | 3034.3113 | 45514.6696
2020-11-25 15:00 | 7.0613 | 7.4327 | 301.9766 | 2391.2989 | 35869.4828
2020-11-25 16:00 | 6.6565 | 7.0066 | 301.1278 | 1994.1494 | 29912.2409
2020-11-25 17:00 | 6.4513 | 6.7906 | 301.3265 | 1817.9708 | 27269.5624
2020-11-25 18:00 | 6.2325 | 6.5603 | 301.8807 | 1630.9769 | 24464.6538
2020-11-25 19:00 | 6.0535 | 6.3719 | 303.3844 | 1492.3021 | 22384.5316
2020-11-25 20:00 | 5.6856 | 5.9846 | 305.0541 | 1222.8834 | 18343.2507
2020-11-25 21:00 | 5.2018 | 5.4754 | 302.3156 | 923.6589 | 13854.883
2020-11-25 22:00 | 4.8073 | 5.0601 | 297.8048 | 715.1713 | 10727.5698
2020-11-25 23:00 | 4.3081 | 4.5347 | 298.3536 | 488.6449 | 7329.6732
2020-11-26 00:00 | 3.8377 | 4.0395 | 299.1113 | 311.9046 | 4678.5697
2020-11-26 01:00 | 3.5575 | 3.7446 | 295.0244 | 224.9549 | 3374.3231
2020-11-26 02:00 | 3.5128 | 3.6976 | 283.3663 | 211.5013 | 3172.5199
2020-11-26 03:00 | 3.2718 | 3.4438 | 267.8802 | 142.9834 | 2144.7507
2020-11-26 04:00 | 3.3391 | 3.5147 | 252.2218 | 159.2041 | 2388.0618
2020-11-26 05:00 | 3.8662 | 4.0696 | 246.4974 | 322.4856 | 4837.284
2020-11-26 06:00 | 3.94 | 4.1472 | 243.3347 | 349.8266 | 5247.3993
2020-11-26 07:00 | 3.6536 | 3.8457 | 242.3223 | 253.8824 | 3808.236
2020-11-26 08:00 | 3.5204 | 3.7056 | 242.352 | 213.7933 | 3206.8991
2020-11-26 09:00 | 3.5542 | 3.7411 | 238.5185 | 223.9686 | 3359.529
2020-11-26 10:00 | 3.4765 | 3.6594 | 228.4244 | 200.5749 | 3008.6242
2020-11-26 11:00 | 4.3697 | 4.5995 | 222.0514 | 515.9846 | 7739.7694
2020-11-26 12:00 | 4.8043 | 5.057 | 216.812 | 713.6183 | 10704.2746
2020-11-26 13:00 | 5.0826 | 5.3499 | 214.0924 | 860.6378 | 12909.5668
2020-11-26 14:00 | 5.8741 | 6.183 | 213.7263 | 1360.1171 | 20401.7565
2020-11-26 15:00 | 6.5238 | 6.867 | 215.2983 | 1879.9738 | 28199.6065
2020-11-26 16:00 | 7.054 | 7.425 | 219.003 | 2384.1204 | 35761.8055
2020-11-26 17:00 | 7.5116 | 7.9067 | 222.2674 | 2884.2962 | 43264.4424
2020-11-26 18:00 | 7.7148 | 8.1205 | 228.5261 | 3118.738 | 46781.0705
2020-11-26 19:00 | 7.6573 | 8.06 | 237.9015 | 3050.5944 | 45758.9155
2020-11-26 20:00 | 7.2984 | 7.6822 | 243.215 | 2646.8032 | 39702.0478
2020-11-26 21:00 | 7.3165 | 7.7014 | 243.8936 | 2667.0366 | 40005.5484
2020-11-26 22:00 | 7.1819 | 7.5596 | 243.1843 | 2517.0897 | 37756.3453
2020-11-26 23:00 | 7.1616 | 7.5383 | 247.2052 | 2494.4761 | 37417.1411
2020-11-27 00:00 | 7.1507 | 7.5268 | 252.5939 | 2482.3754 | 37235.6312
2020-11-27 01:00 | 7.3484 | 7.7349 | 254.2194 | 2702.5649 | 40538.473
2020-11-27 02:00 | 7.4107 | 7.8004 | 254.4966 | 2771.8629 | 41577.9433
2020-11-27 03:00 | 7.3655 | 7.7529 | 255.9295 | 2721.6067 | 40824.1008
2020-11-27 04:00 | 7.3733 | 7.7611 | 256.6825 | 2730.2877 | 40954.3155
2020-11-27 05:00 | 7.6392 | 8.041 | 256.1229 | 3029.125 | 45436.8757
2020-11-27 06:00 | 7.6597 | 8.0625 | 252.859 | 3053.4206 | 45801.3095
2020-11-27 07:00 | 7.8619 | 8.2754 | 251.0028 | 3293.0788 | 49396.1826
2020-11-27 08:00 | 8.2884 | 8.7243 | 252.4834 | 3798.9843 | 56984.7649
2020-11-27 09:00 | 7.1985 | 7.5771 | 253.6661 | 2535.6064 | 38034.0965
2020-11-27 10:00 | 7.7115 | 8.117 | 256.5489 | 3114.7875 | 46721.8125
2020-11-27 11:00 | 8.173 | 8.6028 | 260.9295 | 3662.0067 | 54930.0998
2020-11-27 12:00 | 7.4829 | 7.8764 | 263.5398 | 2852.2535 | 42783.8018
2020-11-27 13:00 | 7.9405 | 8.3581 | 266.0578 | 3386.2099 | 50793.1492
2020-11-27 14:00 | 7.3046 | 7.6888 | 266.6939 | 2653.7404 | 39806.1058
2020-11-27 15:00 | 7.0503 | 7.4211 | 269.5609 | 2380.4741 | 35707.1115
2020-11-27 16:00 | 6.8122 | 7.1705 | 271.8384 | 2146.9286 | 32203.9286
2020-11-27 17:00 | 6.2546 | 6.5836 | 269.5944 | 1649.8599 | 24747.8982
2020-11-27 18:00 | 6.0712 | 6.3905 | 263.4533 | 1505.385 | 22580.7746
2020-11-27 19:00 | 6.134 | 6.4566 | 259.7418 | 1551.643 | 23274.6455
2020-11-27 20:00 | 6.0576 | 6.3762 | 256.6207 | 1495.3334 | 22430.0006
2020-11-27 21:00 | 5.8531 | 6.161 | 256.7959 | 1344.6749 | 20170.1239
2020-11-27 22:00 | 5.5616 | 5.8541 | 260.6259 | 1145.6267 | 17184.4012
2020-11-27 23:00 | 5.3092 | 5.5884 | 262.2165 | 988.3433 | 14825.1489
2020-11-28 00:00 | 5.054 | 5.3198 | 262.3624 | 845.5336 | 12683.0036
2020-11-28 01:00 | 4.5847 | 4.8258 | 258.9971 | 611.5029 | 9172.5431
2020-11-28 02:00 | 4.3407 | 4.569 | 254.6515 | 503.117 | 7546.7554
2020-11-28 03:00 | 4.4769 | 4.7124 | 254.7813 | 563.6314 | 8454.4707
2020-11-28 04:00 | 3.9145 | 4.1204 | 250.5875 | 340.3783 | 5105.675
2020-11-28 05:00 | 3.7571 | 3.9547 | 241.8545 | 285.0306 | 4275.4591
2020-11-28 06:00 | 3.813 | 4.0136 | 239.1224 | 302.7743 | 4541.614
2020-11-28 07:00 | 4.0274 | 4.2392 | 242.737 | 382.202 | 5733.0299
2020-11-28 08:00 | 3.9544 | 4.1624 | 253.0522 | 355.16 | 5327.3993
2020-11-28 09:00 | 3.8667 | 4.0701 | 260.3972 | 322.6737 | 4840.1053
2020-11-28 10:00 | 2.7123 | 2.8549 | 262.8309 | 0 | 0
2020-11-28 11:00 | 2.4522 | 2.5811 | 258.98 | 0 | 0
2020-11-28 12:00 | 2.3311 | 2.4538 | 257.303 | 0 | 0
2020-11-28 13:00 | 2.7576 | 2.9026 | 249.3391 | 0 | 0
2020-11-28 14:00 | 3.0659 | 3.2271 | 236.7104 | 96.6098 | 1449.1471
2020-11-28 15:00 | 3.6566 | 3.8489 | 232.4083 | 254.7981 | 3821.9716
2020-11-28 16:00 | 3.8706 | 4.0742 | 234.1557 | 324.1121 | 4861.6822
2020-11-28 17:00 | 4.1444 | 4.3624 | 231.8078 | 425.5527 | 6383.2906
2020-11-28 18:00 | 4.4586 | 4.6931 | 229.1872 | 555.4754 | 8332.1304
2020-11-28 19:00 | 4.5028 | 4.7397 | 228.7136 | 575.1411 | 8627.1165
2020-11-28 20:00 | 4.8104 | 5.0634 | 227.2776 | 716.8455 | 10752.6827
2020-11-28 21:00 | 5.2627 | 5.5395 | 226.068 | 959.396 | 14390.9402
2020-11-28 22:00 | 5.7818 | 6.0859 | 224.8814 | 1292.1395 | 19382.0921
2020-11-28 23:00 | 5.6846 | 5.9835 | 228.0117 | 1222.2598 | 18333.8973
2020-11-29 00:00 | 5.2932 | 5.5715 | 231.7534 | 978.3568 | 14675.3515
2020-11-29 01:00 | 5.101 | 5.3693 | 233.5519 | 870.4046 | 13056.069
2020-11-29 02:00 | 4.618 | 4.8608 | 237.8615 | 626.2736 | 9394.1035
2020-11-29 03:00 | 4.0983 | 4.3138 | 241.2339 | 408.4598 | 6126.8977
2020-11-29 04:00 | 3.7447 | 3.9417 | 240.5322 | 281.3219 | 4219.8284
2020-11-29 05:00 | 3.6782 | 3.8716 | 241.3444 | 261.2898 | 3919.347
2020-11-29 06:00 | 3.7098 | 3.9049 | 242.7974 | 270.7968 | 4061.9523
2020-11-29 07:00 | 4.247 | 4.4703 | 249.8964 | 463.5559 | 6953.3387
2020-11-29 08:00 | 4.1744 | 4.394 | 253.7113 | 436.6861 | 6550.2913
2020-11-29 09:00 | 4.1652 | 4.3842 | 251.1822 | 433.256 | 6498.8395
2020-11-29 10:00 | 4.776 | 5.0272 | 255.5628 | 698.6597 | 10479.896
2020-11-29 11:00 | 4.3006 | 4.5268 | 250.0367 | 485.2933 | 7279.3995
2020-11-29 12:00 | 4.1746 | 4.3941 | 243.157 | 436.7271 | 6550.9069
2020-11-29 13:00 | 4.2197 | 4.4417 | 235.1355 | 453.4647 | 6801.9702
2020-11-29 14:00 | 4.1126 | 4.3289 | 231.9948 | 413.7705 | 6206.5572
2020-11-29 15:00 | 4.0045 | 4.2151 | 230.6057 | 373.7215 | 5605.8227
2020-11-29 16:00 | 3.9209 | 4.1271 | 229.0711 | 342.7436 | 5141.1533
2020-11-29 17:00 | 3.8813 | 4.0855 | 224.9438 | 328.0849 | 4921.274
2020-11-29 18:00 | 4.0615 | 4.2751 | 220.6725 | 394.8224 | 5922.336
2020-11-29 19:00 | 4.2569 | 4.4808 | 223.0047 | 467.2406 | 7008.6094
2020-11-29 20:00 | 4.2733 | 4.498 | 225.7161 | 473.3119 | 7099.6791
2020-11-29 21:00 | 4.3159 | 4.5429 | 224.2924 | 492.1042 | 7381.5636
2020-11-29 22:00 | 4.0623 | 4.2759 | 218.2919 | 395.1232 | 5926.848
2020-11-29 23:00 | 4.3018 | 4.528 | 218.0557 | 485.827 | 7287.4045
2020-11-30 00:00 | 4.4943 | 4.7307 | 219.4637 | 571.3636 | 8570.454
2020-11-30 01:00 | 4.5451 | 4.7841 | 220.7919 | 593.911 | 8908.6656
2020-11-30 02:00 | 4.4473 | 4.6813 | 229.8393 | 550.4881 | 8257.3209
2020-11-30 03:00 | 4.3682 | 4.5979 | 237.8758 | 515.3164 | 7729.7466
2020-11-30 04:00 | 3.9632 | 4.1716 | 249.3946 | 358.4106 | 5376.1586
2020-11-30 05:00 | 3.6495 | 3.8415 | 261.4054 | 252.6586 | 3789.8791
2020-11-30 06:00 | 3.4917 | 3.6753 | 265.7501 | 205.1493 | 3077.2396
2020-11-30 07:00 | 3.0139 | 3.1724 | 261.3107 | 84.8903 | 1273.3544
2020-11-30 08:00 | 2.9648 | 3.1208 | 253.5201 | 73.8471 | 1107.7065
2020-11-30 09:00 | 3.2321 | 3.4021 | 250.251 | 134.0507 | 2010.7605
2020-11-30 10:00 | 3.2388 | 3.4092 | 273.0352 | 135.5627 | 2033.4411
2020-11-30 11:00 | 3.3656 | 3.5427 | 289.7777 | 167.2008 | 2508.0123
2020-11-30 12:00 | 3.2814 | 3.454 | 303.7346 | 145.1631 | 2177.4466
2020-11-30 13:00 | 2.508 | 2.6399 | 307.2072 | 0 | 0
2020-11-30 14:00 | 2.0954 | 2.2056 | 310.8945 | 0 | 0
2020-11-30 15:00 | 1.966 | 2.0694 | 316.117 | 0 | 0
2020-11-30 16:00 | 2.2865 | 2.4068 | 314.7172 | 0 | 0
2020-11-30 17:00 | 2.8294 | 2.9782 | 312.4135 | 0 | 0
2020-11-30 18:00 | 3.7852 | 3.9843 | 314.2579 | 293.5171 | 4402.7563
2020-11-30 19:00 | 4.482 | 4.7177 | 316.7049 | 565.8846 | 8488.2693
2020-11-30 20:00 | 4.5381 | 4.7768 | 321.856 | 590.8051 | 8862.0769
2020-11-30 21:00 | 4.3296 | 4.5573 | 328.9267 | 498.1823 | 7472.7347
2020-11-30 22:00 | 4.5023 | 4.7391 | 330.6727 | 574.8815 | 8623.2225
2020-11-30 23:00 | 4.2869 | 4.5124 | 336.5724 | 479.2121 | 7188.1819
2020-12-01 00:00 | 4.1752 | 4.3948 | 344.097 | 436.9647 | 6554.4702
2020-12-01 01:00 | 3.9883 | 4.198 | 350.9603 | 367.7132 | 5515.6984
2020-12-01 02:00 | 3.742 | 3.9388 | 357.2858 | 280.5058 | 4207.5877
2020-12-01 03:00 | 3.6367 | 3.828 | 8.3967 | 248.7951 | 3731.9258
2020-12-01 04:00 | 3.5382 | 3.7243 | 22.3265 | 219.1549 | 3287.3235
2020-12-01 05:00 | 3.5649 | 3.7524 | 31.4013 | 227.1806 | 3407.7086
2020-12-01 06:00 | 3.5874 | 3.7761 | 36.6904 | 233.9698 | 3509.5471
2020-12-01 07:00 | 3.4719 | 3.6545 | 39.567 | 199.1824 | 2987.7364
2020-12-01 08:00 | 3.2842 | 3.4569 | 43.7937 | 145.7822 | 2186.7334
2020-12-01 09:00 | 3.1298 | 3.2944 | 40.6398 | 110.9959 | 1664.9378
2020-12-01 10:00 | 4.0148 | 4.226 | 50.1426 | 377.5349 | 5663.0229
2020-12-01 11:00 | 4.1856 | 4.4058 | 49.4864 | 440.8297 | 6612.4453
2020-12-01 12:00 | 4.3218 | 4.5491 | 43.1483 | 494.7194 | 7420.791
2020-12-01 13:00 | 4.4734 | 4.7087 | 32.0621 | 562.0724 | 8431.0853
2020-12-01 14:00 | 4.984 | 5.2461 | 21.7049 | 808.5436 | 12128.1545
2020-12-01 15:00 | 5.4912 | 5.7801 | 18.641 | 1101.79 | 16526.8495
2020-12-01 16:00 | 5.8551 | 6.1631 | 18.8915 | 1346.1536 | 20192.3045
2020-12-01 17:00 | 6.1626 | 6.4867 | 21.8786 | 1572.6867 | 23590.3011
2020-12-01 18:00 | 6.2898 | 6.6206 | 24.7807 | 1679.9123 | 25198.6842
2020-12-01 19:00 | 6.3211 | 6.6535 | 26.2072 | 1706.6607 | 25599.9106
2020-12-01 20:00 | 6.0938 | 6.4143 | 27.2442 | 1521.9822 | 22829.7324
2020-12-01 21:00 | 5.8927 | 6.2026 | 27.6296 | 1373.834 | 20607.5095
2020-12-01 22:00 | 5.3736 | 5.6562 | 30.1097 | 1028.4679 | 15427.0181
2020-12-01 23:00 | 5.0473 | 5.3127 | 33.7461 | 841.9966 | 12629.9494
2020-12-02 00:00 | 4.8312 | 5.0853 | 35.8202 | 727.8117 | 10917.1762
2020-12-02 01:00 | 4.725 | 4.9735 | 36.9151 | 673.8 | 10107
2020-12-02 02:00 | 4.4638 | 4.6986 | 36.98 | 557.8064 | 8367.0961
2020-12-02 03:00 | 4.2584 | 4.4824 | 35.6473 | 467.7895 | 7016.842
2020-12-02 04:00 | 3.9649 | 4.1734 | 36.6821 | 359.0488 | 5385.7326
2020-12-02 05:00 | 3.625 | 3.8157 | 38.1873 | 245.2885 | 3679.3268
2020-12-02 06:00 | 3.235 | 3.4052 | 41.9959 | 134.7033 | 2020.5499
2020-12-02 07:00 | 2.762 | 2.9073 | 47.1151 | 0 | 0
2020-12-02 08:00 | 2.0763 | 2.1855 | 55.5151 | 0 | 0
2020-12-02 09:00 | 1.6726 | 1.7605 | 69.9793 | 0 | 0
2020-12-02 10:00 | 1.5514 | 1.633 | 80.7789 | 0 | 0
2020-12-02 11:00 | 1.4321 | 1.5074 | 87.2114 | 0 | 0
2020-12-02 12:00 | 1.5722 | 1.6549 | 91.1128 | 0 | 0
2020-12-02 13:00 | 2.0707 | 2.1796 | 97.131 | 0 | 0
2020-12-02 14:00 | 2.7717 | 2.9175 | 110.2965 | 0 | 0
2020-12-02 15:00 | 3.4904 | 3.674 | 124.124 | 204.7599 | 3071.3986
2020-12-02 16:00 | 3.909 | 4.1146 | 137.2246 | 338.3225 | 5074.8374
2020-12-02 17:00 | 4.2467 | 4.47 | 147.9005 | 463.4564 | 6951.846
2020-12-02 18:00 | 4.4919 | 4.7282 | 156.6289 | 570.289 | 8554.3356
2020-12-02 19:00 | 4.4301 | 4.6631 | 163.0387 | 542.8479 | 8142.7184
2020-12-02 20:00 | 4.2457 | 4.469 | 164.6605 | 463.0778 | 6946.1667
2020-12-02 21:00 | 4.2145 | 4.4362 | 164.1441 | 451.5426 | 6773.1393
2020-12-02 22:00 | 3.9068 | 4.1123 | 164.2145 | 337.5149 | 5062.7242
2020-12-02 23:00 | 4.1391 | 4.3568 | 163.4282 | 423.5932 | 6353.8973
2020-12-03 00:00 | 4.1594 | 4.3781 | 162.1881 | 431.1065 | 6466.5968
2020-12-03 01:00 | 4.2379 | 4.4608 | 153.9476 | 460.1844 | 6902.766
2020-12-03 02:00 | 4.5222 | 4.76 | 148.0093 | 583.7307 | 8755.9598
2020-12-03 03:00 | 4.7126 | 4.9605 | 146.8135 | 668.32 | 10024.7993
2020-12-03 04:00 | 4.8773 | 5.1338 | 144.4861 | 752.1887 | 11282.8298
2020-12-03 05:00 | 4.9765 | 5.2383 | 140.4863 | 804.6146 | 12069.2197
2020-12-03 06:00 | 5.0847 | 5.3521 | 137.8913 | 861.7753 | 12926.629
2020-12-03 07:00 | 5.3371 | 5.6178 | 132.376 | 1005.7398 | 15086.0973
2020-12-03 08:00 | 6.2881 | 6.6188 | 130.8676 | 1678.4738 | 25177.1064
2020-12-03 09:00 | 5.795 | 6.0998 | 132.4665 | 1301.853 | 19527.7952
2020-12-03 10:00 | 5.0806 | 5.3478 | 134.146 | 859.5826 | 12893.7386
2020-12-03 11:00 | 4.7876 | 5.0394 | 129.6994 | 704.7603 | 10571.4039
2020-12-03 12:00 | 4.9107 | 5.169 | 126.8532 | 769.8324 | 11547.4857
2020-12-03 13:00 | 6.0531 | 6.3715 | 131.9246 | 1492.0313 | 22380.4695
2020-12-03 14:00 | 6.2072 | 6.5337 | 128.5679 | 1609.3567 | 24140.3504
2020-12-03 15:00 | 6.7598 | 7.1154 | 126.3652 | 2095.5096 | 31432.6444
2020-12-03 16:00 | 6.5109 | 6.8534 | 125.8717 | 1868.9265 | 28033.8974
2020-12-03 17:00 | 6.4883 | 6.8296 | 126.9523 | 1849.6049 | 27744.0733
2020-12-03 18:00 | 7.1339 | 7.5091 | 127.834 | 2463.587 | 36953.8049
2020-12-03 19:00 | 7.7417 | 8.1489 | 128.9535 | 3150.6331 | 47259.4958
2020-12-03 20:00 | 7.9385 | 8.356 | 130.044 | 3383.8995 | 50758.493
2020-12-03 21:00 | 7.7691 | 8.1777 | 132.7211 | 3183.0603 | 47745.9042
2020-12-03 22:00 | 7.0967 | 7.47 | 136.3997 | 2426.0192 | 36390.2876
2020-12-03 23:00 | 7.1664 | 7.5434 | 137.6571 | 2499.8685 | 37498.0269
2020-12-04 00:00 | 7.6547 | 8.0573 | 134.3425 | 3047.5609 | 45713.4133
2020-12-04 01:00 | 8.4068 | 8.8489 | 130.4235 | 3939.6056 | 59094.0837
2020-12-04 02:00 | 8.8308 | 9.2952 | 129.9216 | 4425.9135 | 66388.7019
2020-12-04 03:00 | 8.9107 | 9.3793 | 133.4083 | 4515.8736 | 67738.1034
2020-12-04 04:00 | 8.9566 | 9.4276 | 136.4147 | 4567.5611 | 68513.416
2020-12-04 05:00 | 9.0984 | 9.5769 | 138.8003 | 4708.245 | 70623.6743
2020-12-04 06:00 | 9.1049 | 9.5838 | 142.8674 | 4713.8809 | 70708.213
2020-12-04 07:00 | 9.1148 | 9.5942 | 147.4595 | 4722.4468 | 70836.7017
2020-12-04 08:00 | 9.316 | 9.806 | 149.8651 | 4896.5191 | 73447.7866
2020-12-04 09:00 | 9.1491 | 9.6303 | 145.3541 | 4752.1333 | 71281.9993
2020-12-04 10:00 | 9.0356 | 9.5108 | 155.5114 | 4653.8558 | 69807.8368
2020-12-04 11:00 | 8.1156 | 8.5424 | 142.5193 | 3593.8665 | 53907.9969
2020-12-04 12:00 | 8.7774 | 9.239 | 140.2378 | 4365.7507 | 65486.2604
2020-12-04 13:00 | 9.4727 | 9.9709 | 136.5674 | 5032.0875 | 75481.312
2020-12-04 14:00 | 9.7399 | 10.2522 | 137.2261 | 5203.2837 | 78049.2556
2020-12-04 15:00 | 9.7169 | 10.2279 | 139.3632 | 5189.1083 | 77836.6252
2020-12-04 16:00 | 9.9818 | 10.5068 | 138.8161 | 5350.5892 | 80258.8383
2020-12-04 17:00 | 10.3877 | 10.934 | 138.1848 | 5513.8028 | 82707.0422
2020-12-04 18:00 | 10.1816 | 10.7171 | 140.244 | 5430.9424 | 81464.1361
2020-12-04 19:00 | 9.8567 | 10.3751 | 140.9254 | 5275.0647 | 79125.9711
2020-12-04 20:00 | 9.8225 | 10.3391 | 140.1482 | 5254.0108 | 78810.1627
2020-12-04 21:00 | 9.6424 | 10.1496 | 142.5303 | 5143.3463 | 77150.1941
2020-12-04 22:00 | 8.7589 | 9.2195 | 148.6789 | 4344.8909 | 65173.3634
2020-12-04 23:00 | 9.1509 | 9.6321 | 147.814 | 4753.624 | 71304.3605
2020-12-05 00:00 | 9.0481 | 9.524 | 146.1365 | 4664.7215 | 69970.8227
2020-12-05 01:00 | 8.5337 | 8.9825 | 142.6635 | 4090.2464 | 61353.6959
2020-12-05 02:00 | 8.8873 | 9.3547 | 139.9012 | 4489.5057 | 67342.5849
2020-12-05 03:00 | 9.3291 | 9.8197 | 138.066 | 4907.8145 | 73617.2168
2020-12-05 04:00 | 9.8596 | 10.3782 | 138.8399 | 5276.8729 | 79153.0936
2020-12-05 05:00 | 9.6509 | 10.1584 | 139.4091 | 5148.5249 | 77227.8728
2020-12-05 06:00 | 10.5711 | 11.1271 | 139.3784 | 5567.7173 | 83515.7588
2020-12-05 07:00 | 9.6389 | 10.1459 | 138.3746 | 5141.2089 | 77118.134
2020-12-05 08:00 | 8.7829 | 9.2448 | 138.6425 | 4371.9418 | 65579.1271
2020-12-05 09:00 | 8.7651 | 9.2261 | 141.0973 | 4351.8809 | 65278.2139
2020-12-05 10:00 | 8.0499 | 8.4733 | 145.777 | 3515.9297 | 52738.9458
2020-12-05 11:00 | 7.4762 | 7.8694 | 144.7464 | 2844.8523 | 42672.785
2020-12-05 12:00 | 7.3745 | 7.7623 | 140.8973 | 2731.5336 | 40973.0041
2020-12-05 13:00 | 7.6073 | 8.0074 | 136.8955 | 2991.3073 | 44869.6091
2020-12-05 14:00 | 7.4668 | 7.8595 | 132.5592 | 2834.3969 | 42515.9536
2020-12-05 15:00 | 8.3336 | 8.7719 | 131.6815 | 3852.6965 | 57790.4468
2020-12-05 16:00 | 9.0396 | 9.5151 | 131.7796 | 4657.3837 | 69860.7549
2020-12-05 17:00 | 9.2064 | 9.6906 | 132.8077 | 4801.6965 | 72025.4478
2020-12-05 18:00 | 9.0737 | 9.5509 | 136.0211 | 4686.8604 | 70302.9062
2020-12-05 19:00 | 9.0226 | 9.4972 | 135.7399 | 4641.9645 | 69629.4682
2020-12-05 20:00 | 9.3024 | 9.7917 | 136.9775 | 4884.7447 | 73271.1703
2020-12-05 21:00 | 9.1514 | 9.6327 | 138.4846 | 4754.0631 | 71310.9465
2020-12-05 22:00 | 9.1579 | 9.6396 | 146.5811 | 4759.7366 | 71396.0483
2020-12-05 23:00 | 8.4156 | 8.8583 | 143.8838 | 3950.1202 | 59251.8024
2020-12-06 00:00 | 8.3707 | 8.8109 | 143.321 | 3896.7132 | 58450.698
2020-12-06 01:00 | 8.3741 | 8.8145 | 139.5469 | 3900.7684 | 58511.5262
2020-12-06 02:00 | 8.2931 | 8.7293 | 137.584 | 3804.6486 | 57069.7285
2020-12-06 03:00 | 8.4576 | 8.9024 | 135.8924 | 3999.8788 | 59998.1826
2020-12-06 04:00 | 8.5825 | 9.0339 | 132.6429 | 4146.2486 | 62193.7295
2020-12-06 05:00 | 8.7788 | 9.2406 | 130.6361 | 4367.4025 | 65511.038
2020-12-06 06:00 | 8.8213 | 9.2852 | 129.1129 | 4415.2104 | 66228.1556
2020-12-06 07:00 | 8.7045 | 9.1623 | 126.5358 | 4283.6645 | 64254.9672
2020-12-06 08:00 | 8.2134 | 8.6454 | 126.4928 | 3709.9655 | 55649.4822
2020-12-06 09:00 | 8.0407 | 8.4636 | 128.2455 | 3504.9737 | 52574.6048
2020-12-06 10:00 | 7.7293 | 8.1358 | 133.9186 | 3135.8736 | 47038.1041
2020-12-06 11:00 | 7.5284 | 7.9244 | 130.4417 | 2902.9853 | 43544.7794
2020-12-06 12:00 | 7.2305 | 7.6108 | 124.8184 | 2571.1814 | 38567.7204
2020-12-06 13:00 | 7.9144 | 8.3307 | 121.4758 | 3355.3164 | 50329.7462
2020-12-06 14:00 | 8.7407 | 9.2004 | 118.5215 | 4324.3945 | 64865.9176
2020-12-06 15:00 | 8.9278 | 9.3974 | 118.9521 | 4535.1852 | 68027.7776
2020-12-06 16:00 | 8.7267 | 9.1857 | 121.3618 | 4308.6637 | 64629.9556
2020-12-06 17:00 | 8.7634 | 9.2243 | 122.0688 | 4349.9772 | 65249.6578
2020-12-06 18:00 | 8.9427 | 9.413 | 122.2192 | 4551.9371 | 68279.0561
2020-12-06 19:00 | 8.7864 | 9.2486 | 124.5588 | 4375.9626 | 65639.4393
2020-12-06 20:00 | 8.3645 | 8.8044 | 127.8978 | 3889.4007 | 58341.0102
2020-12-06 21:00 | 8.6468 | 9.1016 | 125.591 | 4218.6833 | 63280.2491
2020-12-06 22:00 | 8.7893 | 9.2516 | 126.7059 | 4379.159 | 65687.3856
2020-12-06 23:00 | 8.554 | 9.0039 | 127.533 | 4114.1428 | 61712.1413
2020-12-07 00:00 | 8.4035 | 8.8454 | 126.66 | 3935.6516 | 59034.7746
2020-12-07 01:00 | 8.5874 | 9.039 | 125.6275 | 4151.7751 | 62276.6269
2020-12-07 02:00 | 8.9765 | 9.4486 | 124.4011 | 4589.9831 | 68849.7467
2020-12-07 03:00 | 8.9974 | 9.4706 | 124.9399 | 4613.5458 | 69203.1875
2020-12-07 04:00 | 8.6351 | 9.0893 | 124.2105 | 4205.5077 | 63082.6162
2020-12-07 05:00 | 8.7162 | 9.1747 | 124.5111 | 4296.8959 | 64453.4388
2020-12-07 06:00 | 8.8442 | 9.3094 | 125.0022 | 4441.0541 | 66615.811
2020-12-07 07:00 | 8.6453 | 9.1 | 122.3892 | 4216.9486 | 63254.2297
2020-12-07 08:00 | 9.2563 | 9.7431 | 123.3198 | 4844.8541 | 72672.8118
2020-12-07 09:00 | 9.0286 | 9.5035 | 121.489 | 4647.8529 | 69717.7929
2020-12-07 10:00 | 9.4759 | 9.9743 | 130.1978 | 5034.8919 | 75523.3781
2020-12-07 11:00 | 8.7557 | 9.2162 | 128.0117 | 4341.3331 | 65119.9962
2020-12-07 12:00 | 8.0338 | 8.4563 | 120.1692 | 3496.8139 | 52452.2092
2020-12-07 13:00 | 8.4088 | 8.851 | 115.8682 | 3941.9343 | 59129.0147
2020-12-07 14:00 | 8.2979 | 8.7344 | 113.001 | 3810.3521 | 57155.2814
2020-12-07 15:00 | 8.3354 | 8.7738 | 111.9183 | 3854.8255 | 57822.3823
2020-12-07 16:00 | 8.3145 | 8.7518 | 112.9445 | 3830.0069 | 57450.1031
2020-12-07 17:00 | 8.3357 | 8.7741 | 114.3062 | 3855.2081 | 57828.1208
2020-12-07 18:00 | 8.2081 | 8.6398 | 114.0345 | 3703.7185 | 55555.7781
2020-12-07 19:00 | 8.2227 | 8.6551 | 113.9033 | 3720.9857 | 55814.7859
2020-12-07 20:00 | 8.1421 | 8.5703 | 112.8808 | 3625.2806 | 54379.2087
2020-12-07 21:00 | 8.0255 | 8.4476 | 111.5944 | 3486.9675 | 52304.5126
2020-12-07 22:00 | 7.7006 | 8.1056 | 110.5502 | 3101.9561 | 46529.3413
2020-12-07 23:00 | 8.2994 | 8.7359 | 114.5522 | 3812.0415 | 57180.6221
2020-12-08 00:00 | 8.1981 | 8.6293 | 112.3546 | 3691.8525 | 55377.7878
2020-12-08 01:00 | 8.2486 | 8.6824 | 112.8623 | 3751.7271 | 56275.9059
2020-12-08 02:00 | 8.3833 | 8.8242 | 114.2301 | 3911.7442 | 58676.1627
2020-12-08 03:00 | 8.5454 | 8.9949 | 113.858 | 4104.2411 | 61563.6159
2020-12-08 04:00 | 7.9745 | 8.394 | 110.9037 | 3426.5916 | 51398.8746
2020-12-08 05:00 | 8.237 | 8.6702 | 111.4454 | 3737.981 | 56069.7154
2020-12-08 06:00 | 7.921 | 8.3376 | 111.0915 | 3363.1637 | 50447.456
2020-12-08 07:00 | 8.5258 | 8.9742 | 114.9067 | 4080.9216 | 61213.824
2020-12-08 08:00 | 8.4136 | 8.8561 | 117.1794 | 3947.7255 | 59215.8822
2020-12-08 09:00 | 8.0705 | 8.4949 | 116.2326 | 3540.2823 | 53104.2339
2020-12-08 10:00 | 7.3794 | 7.7675 | 127.9454 | 2737.0436 | 41055.6535
2020-12-08 11:00 | 6.8521 | 7.2125 | 122.5048 | 2186.0072 | 32790.1082
2020-12-08 12:00 | 6.7678 | 7.1237 | 115.4678 | 2103.318 | 31549.7702
2020-12-08 13:00 | 7.1555 | 7.5319 | 109.5733 | 2487.7154 | 37315.7308
2020-12-08 14:00 | 7.0569 | 7.428 | 106.1204 | 2386.9416 | 35804.1233
2020-12-08 15:00 | 7.6047 | 8.0047 | 106.6987 | 2988.3031 | 44824.5458
2020-12-08 16:00 | 7.2366 | 7.6172 | 106.5507 | 2578.0312 | 38670.4675
2020-12-08 17:00 | 7.5028 | 7.8974 | 109.5864 | 2874.4566 | 43116.8483
2020-12-08 18:00 | 7.5036 | 7.8983 | 112.3964 | 2875.3728 | 43130.5927
2020-12-08 19:00 | 6.9399 | 7.3049 | 114.0415 | 2272.1602 | 34082.4028
2020-12-08 20:00 | 6.6082 | 6.9558 | 112.0011 | 1952.1002 | 29281.5034
2020-12-08 21:00 | 6.9649 | 7.3312 | 109.6617 | 2296.6692 | 34450.0375
2020-12-08 22:00 | 6.9529 | 7.3185 | 107.2337 | 2284.877 | 34273.1543
2020-12-08 23:00 | 6.9085 | 7.2719 | 108.1836 | 2241.4034 | 33621.0517
2020-12-09 00:00 | 6.746 | 7.1008 | 109.0023 | 2081.9727 | 31229.5901
2020-12-09 01:00 | 6.4503 | 6.7895 | 107.4663 | 1817.0963 | 27256.4442
2020-12-09 02:00 | 6.4742 | 6.8147 | 106.2358 | 1837.5694 | 27563.5416
2020-12-09 03:00 | 6.5906 | 6.9372 | 107.0531 | 1937.0117 | 29055.1751
2020-12-09 04:00 | 6.971 | 7.3377 | 107.8979 | 2302.7171 | 34540.7572
2020-12-09 05:00 | 7.1337 | 7.5089 | 110.0215 | 2463.4162 | 36951.2437
2020-12-09 06:00 | 7.166 | 7.5429 | 112.7836 | 2499.3537 | 37490.3049
2020-12-09 07:00 | 7.2686 | 7.6509 | 115.0958 | 2613.6035 | 39204.0529
2020-12-09 08:00 | 6.5099 | 6.8523 | 116.9432 | 1868.0667 | 28021.0002
2020-12-09 09:00 | 7.0737 | 7.4457 | 124.3925 | 2403.4238 | 36051.3572
2020-12-09 10:00 | 6.078 | 6.3977 | 129.7493 | 1510.3789 | 22655.6841
2020-12-09 11:00 | 5.8768 | 6.1859 | 124.8722 | 1362.1386 | 20432.0797
2020-12-09 12:00 | 5.8672 | 6.1758 | 118.2347 | 1355.0292 | 20325.4374
2020-12-09 13:00 | 6.1202 | 6.4421 | 112.0808 | 1541.4991 | 23122.4858
2020-12-09 14:00 | 6.5063 | 6.8485 | 112.9475 | 1865.0105 | 27975.1581
2020-12-09 15:00 | 6.4175 | 6.755 | 115.301 | 1789.0896 | 26836.3445
2020-12-09 16:00 | 7.1012 | 7.4747 | 118.6932 | 2430.3792 | 36455.6874
2020-12-09 17:00 | 8.2352 | 8.6683 | 118.3396 | 3735.8183 | 56037.2745
2020-12-09 18:00 | 8.0963 | 8.5221 | 117.745 | 3570.9526 | 53564.2888
2020-12-09 19:00 | 8.1853 | 8.6158 | 119.7501 | 3676.649 | 55149.7351
2020-12-09 20:00 | 7.6801 | 8.084 | 125.3031 | 3077.5755 | 46163.6321
2020-12-09 21:00 | 7.1148 | 7.489 | 130.2048 | 2443.7463 | 36656.1943
2020-12-09 22:00 | 6.8562 | 7.2168 | 126.5914 | 2190.0807 | 32851.2099
2020-12-09 23:00 | 7.0224 | 7.3917 | 116.1815 | 2353.0875 | 35296.3126
2020-12-10 00:00 | 7.3995 | 7.7886 | 114.7434 | 2759.3672 | 41390.5082
2020-12-10 01:00 | 7.1128 | 7.4869 | 121.2872 | 2441.7946 | 36626.9197
2020-12-10 02:00 | 7.2859 | 7.6691 | 121.8479 | 2632.9288 | 39493.9316
2020-12-10 03:00 | 7.8328 | 8.2448 | 118.3609 | 3258.6289 | 48879.4337
2020-12-10 04:00 | 8.9736 | 9.4456 | 113.4102 | 4586.7692 | 68801.5384
2020-12-10 05:00 | 8.3298 | 8.768 | 115.0158 | 3848.2487 | 57723.7298
2020-12-10 06:00 | 8.3499 | 8.789 | 115.2902 | 3872.0182 | 58080.2732
2020-12-10 07:00 | 8.3169 | 8.7544 | 118.4825 | 3832.9128 | 57493.6913
2020-12-10 08:00 | 8.2526 | 8.6866 | 116.5755 | 3756.5298 | 56347.9476
2020-12-10 09:00 | 8.1606 | 8.5898 | 116.2049 | 3647.3085 | 54709.6282
2020-12-10 10:00 | 7.2459 | 7.627 | 126.7796 | 2588.3152 | 38824.7274
2020-12-10 11:00 | 7.7858 | 8.1953 | 123.9673 | 3202.9095 | 48043.6424
2020-12-10 12:00 | 9.6607 | 10.1688 | 119.0111 | 5154.5689 | 77318.5335
2020-12-10 13:00 | 10.4986 | 11.0508 | 115.4727 | 5550.4754 | 83257.1303
2020-12-10 14:00 | 10.316 | 10.8586 | 115.7242 | 5484.9823 | 82274.7349
2020-12-10 15:00 | 10.0936 | 10.6245 | 118.5251 | 5395.5594 | 80933.3904
2020-12-10 16:00 | 10.2339 | 10.7722 | 121.5675 | 5451.9728 | 81779.5921
2020-12-10 17:00 | 10.6906 | 11.2529 | 124.3604 | 5596.1487 | 83942.2299
2020-12-10 18:00 | 11.0041 | 11.5828 | 127.5939 | 5659.7847 | 84896.7702
2020-12-10 19:00 | 10.6044 | 11.1621 | 133.1107 | 5575.6356 | 83634.5336
2020-12-10 20:00 | 10.0877 | 10.6182 | 134.8587 | 5393.169 | 80897.535
2020-12-10 21:00 | 9.5774 | 10.0811 | 134.684 | 5103.3531 | 76550.2965
2020-12-10 22:00 | 8.837 | 9.3018 | 135.6838 | 4432.8833 | 66493.2502
2020-12-10 23:00 | 8.6178 | 9.071 | 136.9688 | 4185.9675 | 62789.512
2020-12-11 00:00 | 8.3114 | 8.7485 | 136.8346 | 3826.2897 | 57394.3462
2020-12-11 01:00 | 8.3322 | 8.7704 | 134.4078 | 3851.0326 | 57765.489
2020-12-11 02:00 | 8.4293 | 8.8726 | 133.5418 | 3966.3132 | 59494.6978
2020-12-11 03:00 | 8.3653 | 8.8053 | 132.9448 | 3890.3547 | 58355.32
2020-12-11 04:00 | 8.2646 | 8.6993 | 132.1842 | 3770.7677 | 56561.5151
2020-12-11 05:00 | 8.4809 | 8.9269 | 132.0497 | 4027.5466 | 60413.1988
2020-12-11 06:00 | 8.8205 | 9.2845 | 131.4 | 4414.3741 | 66215.6122
2020-12-11 07:00 | 9.0539 | 9.5301 | 130.5429 | 4669.7686 | 70046.5286
2020-12-11 08:00 | 9.1153 | 9.5947 | 129.7242 | 4722.8536 | 70842.8039
2020-12-11 09:00 | 8.501 | 8.9481 | 125.7607 | 4051.4511 | 60771.766
2020-12-11 10:00 | 8.0455 | 8.4687 | 125.158 | 3510.737 | 52661.0547
2020-12-11 11:00 | 7.6062 | 8.0062 | 116.7881 | 2989.9792 | 44849.688
2020-12-11 12:00 | 7.7623 | 8.1705 | 113.531 | 3174.9895 | 47624.8421
2020-12-11 13:00 | 7.7315 | 8.1381 | 108.8649 | 3138.5038 | 47077.5577
2020-12-11 14:00 | 8.3878 | 8.8289 | 111.2942 | 3917.0304 | 58755.4564
2020-12-11 15:00 | 8.5188 | 8.9668 | 113.2902 | 4072.5537 | 61088.3057
2020-12-11 16:00 | 8.675 | 9.1312 | 115.2411 | 4250.4102 | 63756.153
2020-12-11 17:00 | 8.8301 | 9.2945 | 117.5314 | 4425.1483 | 66377.2239
2020-12-11 18:00 | 8.8301 | 9.2945 | 120.5345 | 4425.1569 | 66377.3529
2020-12-11 19:00 | 8.6434 | 9.098 | 124.4057 | 4214.8555 | 63222.832
2020-12-11 20:00 | 8.3677 | 8.8078 | 127.1001 | 3893.2417 | 58398.6256
2020-12-11 21:00 | 8.0058 | 8.4268 | 124.8969 | 3463.6056 | 51954.0841
2020-12-11 22:00 | 7.4757 | 7.8689 | 124.3767 | 2844.2682 | 42664.0231
2020-12-11 23:00 | 7.5534 | 7.9506 | 121.5543 | 2930.7654 | 43961.4812
2020-12-12 00:00 | 7.6541 | 8.0567 | 114.7149 | 3046.8551 | 45702.8263
2020-12-12 01:00 | 8.0774 | 8.5023 | 110.1938 | 3548.552 | 53228.2806
2020-12-12 02:00 | 8.2648 | 8.6994 | 108.648 | 3770.9759 | 56564.6386
2020-12-12 03:00 | 8.2606 | 8.695 | 109.8829 | 3766.002 | 56490.0299
2020-12-12 04:00 | 8.1328 | 8.5605 | 111.1777 | 3614.2662 | 54213.9935
2020-12-12 05:00 | 7.4767 | 7.87 | 107.941 | 2845.4313 | 42681.4691
2020-12-12 06:00 | 7.3892 | 7.7778 | 104.4619 | 2747.9413 | 41219.1188
2020-12-12 07:00 | 7.5587 | 7.9562 | 104.3393 | 2936.7021 | 44050.5312
2020-12-12 08:00 | 7.365 | 7.7524 | 105.4964 | 2720.9916 | 40814.8745
2020-12-12 09:00 | 7.0516 | 7.4225 | 103.8451 | 2381.794 | 35726.9097
2020-12-12 10:00 | 6.4401 | 6.7788 | 106.9768 | 1808.366 | 27125.49
2020-12-12 11:00 | 6.3333 | 6.6664 | 104.5914 | 1717.0853 | 25756.2792
2020-12-12 12:00 | 6.1892 | 6.5147 | 103.6779 | 1593.9342 | 23909.0123
2020-12-12 13:00 | 6.3362 | 6.6694 | 102.0781 | 1719.5665 | 25793.4977
2020-12-12 14:00 | 6.2363 | 6.5643 | 100.9328 | 1634.19 | 24512.8502
2020-12-12 15:00 | 6.4505 | 6.7898 | 97.1293 | 1817.2921 | 27259.382
2020-12-12 16:00 | 7.1452 | 7.521 | 97.5271 | 2476.2382 | 37143.5729
2020-12-12 17:00 | 6.7461 | 7.1009 | 104.9613 | 2082.0775 | 31231.1619
2020-12-12 18:00 | 6.4365 | 6.775 | 112.0297 | 1805.2903 | 27079.3548
2020-12-12 19:00 | 6.0938 | 6.4143 | 109.3293 | 1521.9762 | 22829.6427
2020-12-12 20:00 | 5.558 | 5.8503 | 103.8938 | 1143.3996 | 17150.9938
2020-12-12 21:00 | 5.8414 | 6.1487 | 107.328 | 1336.065 | 20040.9751
2020-12-12 22:00 | 5.3091 | 5.5884 | 109.6296 | 988.3159 | 14824.7392
2020-12-12 23:00 | 4.8217 | 5.0753 | 105.5321 | 722.8149 | 10842.2236
2020-12-13 00:00 | 5.051 | 5.3166 | 103.5669 | 843.939 | 12659.0851
2020-12-13 01:00 | 5.0308 | 5.2953 | 101.3155 | 833.2649 | 12498.9732
2020-12-13 02:00 | 5.1438 | 5.4143 | 96.922 | 892.9889 | 13394.8328
2020-12-13 03:00 | 5.3768 | 5.6596 | 97.7172 | 1030.473 | 15457.0953
2020-12-13 04:00 | 5.7984 | 6.1034 | 97.6371 | 1304.3645 | 19565.4678
2020-12-13 05:00 | 6.0829 | 6.4028 | 95.1285 | 1513.99 | 22709.8498
2020-12-13 06:00 | 6.4533 | 6.7927 | 94.7663 | 1819.6537 | 27294.8049
2020-12-13 07:00 | 6.5743 | 6.92 | 96.8381 | 1923.0667 | 28846.0005
2020-12-13 08:00 | 6.6512 | 7.001 | 96.0521 | 1988.9391 | 29834.0865
2020-12-13 09:00 | 5.94 | 6.2524 | 102.2957 | 1408.6617 | 21129.9252
2020-12-13 10:00 | 5.7524 | 6.055 | 102.4115 | 1270.4651 | 19056.9765
2020-12-13 11:00 | 5.5491 | 5.841 | 98.6811 | 1137.8484 | 17067.7267
2020-12-13 12:00 | 5.7956 | 6.1004 | 94.8685 | 1302.2911 | 19534.3664
2020-12-13 13:00 | 6.0274 | 6.3444 | 98.4164 | 1473.0566 | 22095.8485
2020-12-13 14:00 | 5.7622 | 6.0652 | 102.7802 | 1277.659 | 19164.8853
2020-12-13 15:00 | 5.7036 | 6.0035 | 99.8726 | 1234.473 | 18517.0955
2020-12-13 16:00 | 5.6088 | 5.9038 | 96.1617 | 1175.0378 | 17625.5675
2020-12-13 17:00 | 5.2697 | 5.5468 | 98.7684 | 963.723 | 14455.8445
2020-12-13 18:00 | 5.2472 | 5.5231 | 103.9056 | 949.6965 | 14245.4473
2020-12-13 19:00 | 5.3721 | 5.6547 | 108.2424 | 1027.576 | 15413.6407
2020-12-13 20:00 | 5.3712 | 5.6537 | 108.8985 | 1027.0022 | 15405.0331
2020-12-13 21:00 | 5.0615 | 5.3277 | 109.9234 | 849.5152 | 12742.7278
2020-12-13 22:00 | 4.2934 | 4.5192 | 104.747 | 482.116 | 7231.7395
2020-12-13 23:00 | 3.8608 | 4.0639 | 101.4869 | 320.4923 | 4807.3852
2020-12-14 00:00 | 3.9518 | 4.1596 | 97.8882 | 354.1854 | 5312.7815
2020-12-14 01:00 | 3.8279 | 4.0292 | 92.5195 | 308.295 | 4624.425
2020-12-14 02:00 | 3.6733 | 3.8665 | 88.9534 | 259.8213 | 3897.3202
2020-12-14 03:00 | 3.454 | 3.6357 | 84.3075 | 193.8129 | 2907.1931
2020-12-14 04:00 | 3.5327 | 3.7185 | 79.9452 | 217.4905 | 3262.3582
2020-12-14 05:00 | 3.3602 | 3.537 | 81.3595 | 165.572 | 2483.5807
2020-12-14 06:00 | 3.4127 | 3.5922 | 82.7687 | 181.3766 | 2720.6492
2020-12-14 07:00 | 3.2198 | 3.3892 | 83.8372 | 131.2791 | 1969.1862
2020-12-14 08:00 | 1.8559 | 1.9535 | 83.7217 | 0 | 0
2020-12-14 09:00 | 0.80781 | 0.85029 | 81.7233 | 0 | 0
2020-12-14 10:00 | 0.71834 | 0.75612 | 12.5693 | 0 | 0
2020-12-14 11:00 | 1.5966 | 1.6806 | 348.1647 | 0 | 0
2020-12-14 12:00 | 2.1108 | 2.2218 | 343.0846 | 0 | 0
2020-12-14 13:00 | 2.3972 | 2.5233 | 348.3054 | 0 | 0
2020-12-14 14:00 | 2.6278 | 2.766 | 351.5175 | 0 | 0
2020-12-14 15:00 | 2.6036 | 2.7405 | 354.8956 | 0 | 0
2020-12-14 16:00 | 2.5455 | 2.6794 | 354.2543 | 0 | 0
2020-12-14 17:00 | 2.3379 | 2.4609 | 355.1215 | 0 | 0
2020-12-14 18:00 | 1.8917 | 1.9912 | 347.5626 | 0 | 0
2020-12-14 19:00 | 1.6972 | 1.7864 | 330.3799 | 0 | 0
2020-12-14 20:00 | 2.7503 | 2.8949 | 311.8718 | 0 | 0
2020-12-14 21:00 | 3.4479 | 3.6292 | 308.2516 | 191.9598 | 2879.3973
2020-12-14 22:00 | 3.5621 | 3.7494 | 298.9489 | 226.336 | 3395.0393
2020-12-14 23:00 | 3.7029 | 3.8977 | 294.8793 | 268.7429 | 4031.1438
2020-12-15 00:00 | 4.0359 | 4.2481 | 295.6872 | 385.3388 | 5780.0816
2020-12-15 01:00 | 4.2395 | 4.4625 | 303.6681 | 460.7993 | 6911.9889
2020-12-15 02:00 | 4.1585 | 4.3773 | 312.0379 | 430.7967 | 6461.95
2020-12-15 03:00 | 4.0199 | 4.2313 | 316.3057 | 379.4215 | 5691.3231
2020-12-15 04:00 | 3.7397 | 3.9364 | 316.5448 | 279.8118 | 4197.1766
2020-12-15 05:00 | 3.6244 | 3.815 | 310.0991 | 245.0834 | 3676.2503
2020-12-15 06:00 | 3.888 | 4.0925 | 309.117 | 330.5703 | 4958.5541
2020-12-15 07:00 | 3.8293 | 4.0307 | 314.6631 | 308.816 | 4632.2394
2020-12-15 08:00 | 2.9881 | 3.1452 | 321.0963 | 79.0812 | 1186.2182
2020-12-15 09:00 | 2.6636 | 2.8037 | 325.0931 | 0 | 0
2020-12-15 10:00 | 2.2278 | 2.3449 | 336.258 | 0 | 0
2020-12-15 11:00 | 2.1494 | 2.2624 | 331.8385 | 0 | 0
2020-12-15 12:00 | 1.9103 | 2.0108 | 323.6189 | 0 | 0
2020-12-15 13:00 | 1.8992 | 1.9991 | 322.2681 | 0 | 0
2020-12-15 14:00 | 2.0351 | 2.1421 | 324.2302 | 0 | 0
2020-12-15 15:00 | 1.7074 | 1.7972 | 335.6876 | 0 | 0
2020-12-15 16:00 | 1.2001 | 1.2633 | 359.9577 | 0 | 0
2020-12-15 17:00 | 1.082 | 1.1389 | 48.2768 | 0 | 0
2020-12-15 18:00 | 1.1725 | 1.2342 | 86.0391 | 0 | 0
2020-12-15 19:00 | 1.6019 | 1.6862 | 111.7174 | 0 | 0
2020-12-15 20:00 | 1.8358 | 1.9323 | 134.0503 | 0 | 0
2020-12-15 21:00 | 1.8841 | 1.9832 | 150.5528 | 0 | 0
2020-12-15 22:00 | 2.7184 | 2.8614 | 165.962 | 0 | 0
2020-12-15 23:00 | 3.0946 | 3.2574 | 183.2398 | 103.0833 | 1546.2496
2020-12-16 00:00 | 3.1904 | 3.3581 | 189.8531 | 124.644 | 1869.6606
2020-12-16 01:00 | 3.5177 | 3.7028 | 183.6529 | 212.9866 | 3194.7993
2020-12-16 02:00 | 4.1128 | 4.3291 | 177.0171 | 413.8343 | 6207.5142
2020-12-16 03:00 | 4.351 | 4.5798 | 180.1883 | 507.6812 | 7615.2187
2020-12-16 04:00 | 4.1065 | 4.3225 | 185.4221 | 411.5048 | 6172.5727
2020-12-16 05:00 | 4.2746 | 4.4994 | 184.868 | 473.7982 | 7106.9723
2020-12-16 06:00 | 4.6146 | 4.8573 | 184.0519 | 624.7716 | 9371.5745
2020-12-16 07:00 | 4.6761 | 4.922 | 188.8425 | 652.082 | 9781.23
2020-12-16 08:00 | 4.4412 | 4.6747 | 193.8698 | 547.744 | 8216.1604
2020-12-16 09:00 | 4.6427 | 4.8869 | 194.3988 | 637.2598 | 9558.8966
2020-12-16 10:00 | 4.9527 | 5.2132 | 197.9346 | 792.0154 | 11880.2309
2020-12-16 11:00 | 5.5834 | 5.8771 | 203.6183 | 1159.2389 | 17388.5836
2020-12-16 12:00 | 5.4409 | 5.727 | 206.1125 | 1070.4009 | 16056.0137
2020-12-16 13:00 | 4.6273 | 4.8707 | 204.4371 | 630.4306 | 9456.4597
2020-12-16 14:00 | 4.5731 | 4.8136 | 204.7159 | 606.3369 | 9095.0535
2020-12-16 15:00 | 4.9607 | 5.2216 | 208.3325 | 796.2218 | 11943.3276
2020-12-16 16:00 | 5.1567 | 5.4279 | 208.9729 | 899.8065 | 13497.0981
2020-12-16 17:00 | 5.2704 | 5.5476 | 211.4656 | 964.1859 | 14462.788
2020-12-16 18:00 | 5.366 | 5.6482 | 213.9362 | 1023.7222 | 15355.8329
2020-12-16 19:00 | 5.4873 | 5.7759 | 217.9277 | 1099.3342 | 16490.0128
2020-12-16 20:00 | 5.2601 | 5.5367 | 227.6261 | 957.7505 | 14366.2574
2020-12-16 21:00 | 4.9072 | 5.1653 | 237.277 | 767.9613 | 11519.4199
2020-12-16 22:00 | 4.6599 | 4.905 | 235.7963 | 644.9107 | 9673.6599
2020-12-16 23:00 | 4.5955 | 4.8372 | 236.6962 | 616.3172 | 9244.7575
2020-12-17 00:00 | 4.4794 | 4.715 | 239.2493 | 564.7246 | 8470.8691
2020-12-17 01:00 | 4.2026 | 4.4236 | 250.0865 | 447.1039 | 6706.5585
2020-12-17 02:00 | 3.7382 | 3.9348 | 255.3029 | 279.3657 | 4190.486
2020-12-17 03:00 | 3.5922 | 3.7811 | 255.6418 | 235.4081 | 3531.1215
2020-12-17 04:00 | 3.3917 | 3.5701 | 268.8173 | 175.0485 | 2625.7275
2020-12-17 05:00 | 3.0976 | 3.2605 | 275.9617 | 103.7529 | 1556.2931
2020-12-17 06:00 | 2.7787 | 2.9249 | 273.4491 | 0 | 0
2020-12-17 07:00 | 2.6105 | 2.7478 | 271.1408 | 0 | 0
2020-12-17 08:00 | 1.9541 | 2.0569 | 280.1168 | 0 | 0
2020-12-17 09:00 | 1.2951 | 1.3632 | 293.4341 | 0 | 0
2020-12-17 10:00 | 0.78062 | 0.82167 | 303.9507 | 0 | 0
2020-12-17 11:00 | 0.68794 | 0.72412 | 329.9096 | 0 | 0
2020-12-17 12:00 | 0.85143 | 0.89621 | 19.6611 | 0 | 0
2020-12-17 13:00 | 1.1816 | 1.2438 | 57.6425 | 0 | 0
2020-12-17 14:00 | 1.4323 | 1.5076 | 79.8868 | 0 | 0
2020-12-17 15:00 | 1.7068 | 1.7966 | 108.352 | 0 | 0
2020-12-17 16:00 | 1.9497 | 2.0522 | 129.1528 | 0 | 0
2020-12-17 17:00 | 2.0085 | 2.1141 | 149.052 | 0 | 0
2020-12-17 18:00 | 2.0053 | 2.1107 | 162.9451 | 0 | 0
2020-12-17 19:00 | 2.3907 | 2.5164 | 175.0706 | 0 | 0
2020-12-17 20:00 | 2.5587 | 2.6932 | 185.033 | 0 | 0
2020-12-17 21:00 | 1.7176 | 1.8079 | 187.2411 | 0 | 0
2020-12-17 22:00 | 2.1947 | 2.3101 | 170.1687 | 0 | 0
2020-12-17 23:00 | 2.2035 | 2.3194 | 169.242 | 0 | 0
2020-12-18 00:00 | 2.452 | 2.5809 | 158.8592 | 0 | 0
2020-12-18 01:00 | 3.1226 | 3.2869 | 155.5264 | 109.3894 | 1640.8415
2020-12-18 02:00 | 3.3797 | 3.5575 | 163.7713 | 171.4347 | 2571.5205
2020-12-18 03:00 | 3.1664 | 3.333 | 169.4901 | 119.2559 | 1788.838
2020-12-18 04:00 | 2.9814 | 3.1382 | 174.7949 | 77.5818 | 1163.7271
2020-12-18 05:00 | 3.0839 | 3.2461 | 182.1673 | 100.6581 | 1509.8717
2020-12-18 06:00 | 3.1629 | 3.3292 | 185.6552 | 118.4566 | 1776.8484
2020-12-18 07:00 | 3.4953 | 3.6792 | 183.7982 | 206.2422 | 3093.6325
2020-12-18 08:00 | 3.2143 | 3.3834 | 182.7534 | 130.0373 | 1950.5595
2020-12-18 09:00 | 2.9048 | 3.0576 | 190.1997 | 60.3303 | 904.9543
2020-12-18 10:00 | 2.8806 | 3.0322 | 203.0631 | 54.8805 | 823.2068
2020-12-18 11:00 | 2.7531 | 2.8979 | 215.088 | 0 | 0
2020-12-18 12:00 | 2.8831 | 3.0347 | 223.6355 | 55.4324 | 831.4859
2020-12-18 13:00 | 3.0209 | 3.1797 | 217.177 | 86.4637 | 1296.9562
2020-12-18 14:00 | 3.6357 | 3.8269 | 214.303 | 248.4887 | 3727.3306
2020-12-18 15:00 | 4.2471 | 4.4705 | 214.4492 | 463.6185 | 6954.2782
2020-12-18 16:00 | 4.5786 | 4.8194 | 224.3451 | 608.7735 | 9131.6025
2020-12-18 17:00 | 4.8005 | 5.053 | 236.2222 | 711.5935 | 10673.903
2020-12-18 18:00 | 4.877 | 5.1335 | 241.6336 | 751.9944 | 11279.9165
2020-12-18 19:00 | 4.9305 | 5.1898 | 249.953 | 780.2749 | 11704.1241
2020-12-18 20:00 | 4.9224 | 5.1813 | 265.1174 | 775.9939 | 11639.909
2020-12-18 21:00 | 4.8857 | 5.1426 | 278.1888 | 756.6027 | 11349.0411
2020-12-18 22:00 | 4.516 | 4.7535 | 290.2572 | 580.9646 | 8714.4684
2020-12-18 23:00 | 4.7294 | 4.9782 | 298.4649 | 675.7808 | 10136.7114
2020-12-19 00:00 | 4.9303 | 5.1896 | 305.0708 | 780.1938 | 11702.9065
2020-12-19 01:00 | 5.1583 | 5.4296 | 307.705 | 900.6744 | 13510.1161
2020-12-19 02:00 | 5.4221 | 5.7072 | 310.9563 | 1058.6755 | 15880.133
2020-12-19 03:00 | 5.3675 | 5.6498 | 316.2212 | 1024.6885 | 15370.3277
2020-12-19 04:00 | 4.9233 | 5.1823 | 318.2458 | 776.5023 | 11647.5348
2020-12-19 05:00 | 4.6485 | 4.893 | 315.8625 | 639.8305 | 9597.4578
2020-12-19 06:00 | 4.658 | 4.903 | 315.5803 | 644.0497 | 9660.7452
2020-12-19 07:00 | 4.3941 | 4.6252 | 314.7506 | 526.8241 | 7902.3612
2020-12-19 08:00 | 3.8489 | 4.0513 | 303.2811 | 316.0615 | 4740.923
2020-12-19 09:00 | 3.1928 | 3.3608 | 293.8367 | 125.2058 | 1878.0869
2020-12-19 10:00 | 2.8494 | 2.9993 | 283.4133 | 0 | 0
2020-12-19 11:00 | 2.7517 | 2.8964 | 271.9098 | 0 | 0
2020-12-19 12:00 | 2.9604 | 3.1161 | 274.4994 | 72.8461 | 1092.6918
2020-12-19 13:00 | 3.4393 | 3.6202 | 273.7442 | 189.3883 | 2840.8251
2020-12-19 14:00 | 3.8503 | 4.0528 | 274.3575 | 316.5712 | 4748.5678
2020-12-19 15:00 | 3.8173 | 4.018 | 280.6844 | 304.352 | 4565.2799
2020-12-19 16:00 | 3.8035 | 4.0035 | 292.1529 | 299.2314 | 4488.4711
2020-12-19 17:00 | 3.5747 | 3.7627 | 301.801 | 230.1325 | 3451.9876
2020-12-19 18:00 | 3.5691 | 3.7569 | 309.2661 | 228.4593 | 3426.8892
2020-12-19 19:00 | 3.6856 | 3.8794 | 315.9904 | 263.5096 | 3952.6445
2020-12-19 20:00 | 3.6586 | 3.851 | 322.1937 | 255.3962 | 3830.9431
2020-12-19 21:00 | 3.6823 | 3.876 | 331.6734 | 262.5352 | 3938.028
2020-12-19 22:00 | 3.454 | 3.6357 | 342.3376 | 193.8002 | 2907.0032
2020-12-19 23:00 | 3.2519 | 3.4229 | 340.1726 | 138.5015 | 2077.522
2020-12-20 00:00 | 2.773 | 2.9189 | 335.4612 | 0 | 0
2020-12-20 01:00 | 2.8078 | 2.9555 | 323.7332 | 0 | 0
2020-12-20 02:00 | 3.2109 | 3.3798 | 319.3349 | 129.2697 | 1939.0458
2020-12-20 03:00 | 3.2117 | 3.3806 | 324.113 | 129.4516 | 1941.7737
2020-12-20 04:00 | 2.8442 | 2.9938 | 329.7288 | 0 | 0
2020-12-20 05:00 | 2.3849 | 2.5103 | 330.3682 | 0 | 0
2020-12-20 06:00 | 2.0662 | 2.1749 | 322.2165 | 0 | 0
2020-12-20 07:00 | 1.8462 | 1.9433 | 309.2101 | 0 | 0
2020-12-20 08:00 | 1.7046 | 1.7943 | 301.0289 | 0 | 0
2020-12-20 09:00 | 1.5961 | 1.6801 | 302.0763 | 0 | 0
2020-12-20 10:00 | 1.0153 | 1.0687 | 291.7397 | 0 | 0
2020-12-20 11:00 | 1.5776 | 1.6606 | 278.7173 | 0 | 0
2020-12-20 12:00 | 1.8029 | 1.8977 | 293.48 | 0 | 0
2020-12-20 13:00 | 1.7271 | 1.8179 | 315.2506 | 0 | 0
2020-12-20 14:00 | 1.5339 | 1.6145 | 329.2266 | 0 | 0
2020-12-20 15:00 | 1.1768 | 1.2387 | 350.163 | 0 | 0
2020-12-20 16:00 | 0.63194 | 0.66518 | 8.53 | 0 | 0
2020-12-20 17:00 | 0.2989 | 0.31462 | 34.8267 | 0 | 0
2020-12-20 18:00 | 0.079976 | 0.084182 | 201.6065 | 0 | 0
2020-12-20 19:00 | 0.31547 | 0.33206 | 234.0242 | 0 | 0
2020-12-20 20:00 | 0.42859 | 0.45113 | 237.3029 | 0 | 0
2020-12-20 21:00 | 0.72619 | 0.76439 | 264.1267 | 0 | 0
2020-12-20 22:00 | 1.1948 | 1.2576 | 270.8869 | 0 | 0
2020-12-20 23:00 | 0.99411 | 1.0464 | 271.8181 | 0 | 0
2020-12-21 00:00 | 0.45227 | 0.47606 | 259.3948 | 0 | 0
2020-12-21 01:00 | 0.37873 | 0.39865 | 157.2233 | 0 | 0
2020-12-21 02:00 | 0.93902 | 0.9884 | 142.0867 | 0 | 0
2020-12-21 03:00 | 1.2918 | 1.3598 | 139.5922 | 0 | 0
2020-12-21 04:00 | 1.5616 | 1.6438 | 146.5074 | 0 | 0
2020-12-21 05:00 | 2.0447 | 2.1522 | 144.0341 | 0 | 0
2020-12-21 06:00 | 2.3716 | 2.4963 | 139.8106 | 0 | 0
2020-12-21 07:00 | 2.5153 | 2.6476 | 137.676 | 0 | 0
2020-12-21 08:00 | 1.9862 | 2.0907 | 140.4997 | 0 | 0
2020-12-21 09:00 | 2.1493 | 2.2624 | 149.1441 | 0 | 0
2020-12-21 10:00 | 2.4035 | 2.5299 | 136.1627 | 0 | 0
2020-12-21 11:00 | 2.3104 | 2.4319 | 139.9583 | 0 | 0
2020-12-21 12:00 | 2.301 | 2.422 | 135.86 | 0 | 0
2020-12-21 13:00 | 2.727 | 2.8704 | 125.5414 | 0 | 0
2020-12-21 14:00 | 3.1233 | 3.2875 | 122.457 | 109.5309 | 1642.9628
2020-12-21 15:00 | 3.2452 | 3.4159 | 128.7798 | 137.0091 | 2055.1362
2020-12-21 16:00 | 3.6236 | 3.8142 | 134.6245 | 244.8693 | 3673.039
2020-12-21 17:00 | 4.0378 | 4.2501 | 138.9623 | 386.0447 | 5790.6705
2020-12-21 18:00 | 4.0727 | 4.2869 | 143.9179 | 398.987 | 5984.8056
2020-12-21 19:00 | 4.4676 | 4.7026 | 143.495 | 559.4765 | 8392.1471
2020-12-21 20:00 | 4.7023 | 4.9496 | 144.7064 | 663.7465 | 9956.1979
2020-12-21 21:00 | 4.7951 | 5.0473 | 144.3424 | 708.7417 | 10631.1254
2020-12-21 22:00 | 4.922 | 5.1808 | 141.1881 | 775.7783 | 11636.6745
2020-12-21 23:00 | 4.8489 | 5.1039 | 141.8192 | 737.1649 | 11057.4733
2020-12-22 00:00 | 4.9479 | 5.2082 | 141.9912 | 789.4931 | 11842.3966
2020-12-22 01:00 | 5.5156 | 5.8056 | 141.14 | 1116.9431 | 16754.1463
2020-12-22 02:00 | 5.5358 | 5.8269 | 142.9536 | 1129.55 | 16943.2497
2020-12-22 03:00 | 5.6123 | 5.9075 | 144.4374 | 1177.2438 | 17658.657
2020-12-22 04:00 | 5.8904 | 6.2002 | 146.1744 | 1372.1057 | 20581.5849
2020-12-22 05:00 | 6.1097 | 6.4311 | 149.6413 | 1533.7534 | 23006.3007
2020-12-22 06:00 | 6.009 | 6.325 | 151.8431 | 1459.5249 | 21892.8733
2020-12-22 07:00 | 6.1083 | 6.4296 | 162.6427 | 1532.6885 | 22990.3279
2020-12-22 08:00 | 5.595 | 5.8892 | 170.6652 | 1166.4151 | 17496.2265
2020-12-22 09:00 | 5.3563 | 5.638 | 170.6126 | 1017.6891 | 15265.3364
2020-12-22 10:00 | 5.5132 | 5.8032 | 161.6192 | 1115.4682 | 16732.0224
2020-12-22 11:00 | 5.7208 | 6.0217 | 164.044 | 1247.2018 | 18708.0276
2020-12-22 12:00 | 5.9299 | 6.2418 | 164.5325 | 1401.2374 | 21018.5614
2020-12-22 13:00 | 5.9575 | 6.2709 | 165.7134 | 1421.616 | 21324.2403
2020-12-22 14:00 | 5.9227 | 6.2342 | 161.8713 | 1395.9388 | 20939.0818
2020-12-22 15:00 | 6.6204 | 6.9686 | 161.0001 | 1962.4926 | 29437.3897
2020-12-22 16:00 | 7.7327 | 8.1394 | 161.4368 | 3139.9905 | 47099.8575
2020-12-22 17:00 | 7.6614 | 8.0644 | 165.2368 | 3055.4937 | 45832.4061
2020-12-22 18:00 | 7.4695 | 7.8624 | 170.7265 | 2837.3673 | 42560.509
2020-12-22 19:00 | 7.3711 | 7.7588 | 175.1465 | 2727.836 | 40917.5407
2020-12-22 20:00 | 7.9569 | 8.3753 | 174.0035 | 3405.6336 | 51084.5042
2020-12-22 21:00 | 8.2226 | 8.655 | 172.8098 | 3720.8812 | 55813.2179
2020-12-22 22:00 | 8.2621 | 8.6966 | 176.3539 | 3767.7574 | 56516.3612
2020-12-22 23:00 | 8.3767 | 8.8173 | 169.1582 | 3903.8907 | 58558.3605
2020-12-23 00:00 | 8.577 | 9.0281 | 166.9922 | 4140.0312 | 62100.4685
2020-12-23 01:00 | 8.6109 | 9.0637 | 170.1325 | 4178.2052 | 62673.0779
2020-12-23 02:00 | 8.4282 | 8.8714 | 172.2525 | 3964.9815 | 59474.723
2020-12-23 03:00 | 9.3986 | 9.8929 | 174.7944 | 4967.9349 | 74519.0242
2020-12-23 04:00 | 10.2168 | 10.7542 | 178.1255 | 5445.0853 | 81676.2802
2020-12-23 05:00 | 10.1304 | 10.6632 | 182.1589 | 5410.3524 | 81155.2859
2020-12-23 06:00 | 10.4827 | 11.034 | 185.5573 | 5546.6945 | 83200.4174
2020-12-23 07:00 | 10.9482 | 11.5241 | 188.6089 | 5654.2619 | 84813.9279
2020-12-23 08:00 | 11.1277 | 11.713 | 191.3859 | 5672.0212 | 85080.3184
2020-12-23 09:00 | 8.8962 | 9.3641 | 194.1432 | 4499.5971 | 67493.9563
2020-12-23 10:00 | 8.7974 | 9.2601 | 194.0117 | 4388.3379 | 65825.0685
2020-12-23 11:00 | 8.8474 | 9.3127 | 200.9291 | 4444.5955 | 66668.9318
2020-12-23 12:00 | 7.9224 | 8.3391 | 209.2892 | 3364.8163 | 50472.2443
2020-12-23 13:00 | 6.8855 | 7.2476 | 217.4665 | 2218.8029 | 33282.0433
2020-12-23 14:00 | 6.1266 | 6.4489 | 224.5754 | 1546.1995 | 23192.993
2020-12-23 15:00 | 5.5165 | 5.8066 | 231.4827 | 1117.5325 | 16762.9872
2020-12-23 16:00 | 5.2891 | 5.5673 | 243.6598 | 975.8483 | 14637.7247
2020-12-23 17:00 | 5.0613 | 5.3275 | 256.4797 | 849.4196 | 12741.2943
2020-12-23 18:00 | 4.7829 | 5.0344 | 268.6964 | 702.2882 | 10534.3223
2020-12-23 19:00 | 5.2141 | 5.4883 | 279.5656 | 930.1183 | 13951.7747
2020-12-23 20:00 | 5.1968 | 5.4701 | 289.2971 | 920.9852 | 13814.7777
2020-12-23 21:00 | 4.5151 | 4.7526 | 294.4073 | 580.5909 | 8708.8631
2020-12-23 22:00 | 3.98 | 4.1893 | 286.8731 | 364.629 | 5469.4344
2020-12-23 23:00 | 4.2072 | 4.4285 | 280.6733 | 448.8186 | 6732.2793
2020-12-24 00:00 | 3.5807 | 3.769 | 272.9772 | 231.9412 | 3479.1174
2020-12-24 01:00 | 2.8125 | 2.9605 | 254.0918 | 0 | 0
2020-12-24 02:00 | 2.6404 | 2.7793 | 232.4169 | 0 | 0
2020-12-24 03:00 | 2.8571 | 3.0073 | 188.5393 | 49.5692 | 743.5385
2020-12-24 04:00 | 4.313 | 4.5398 | 178.4874 | 490.8041 | 7362.061
2020-12-24 05:00 | 4.4049 | 4.6366 | 182.0977 | 531.6542 | 7974.8135
2020-12-24 06:00 | 5.9203 | 6.2317 | 160.0386 | 1394.1571 | 20912.356
2020-12-24 07:00 | 6.3959 | 6.7323 | 160.9373 | 1770.6106 | 26559.1596
2020-12-24 08:00 | 7.4183 | 7.8084 | 167.4417 | 2780.3134 | 41704.7004
2020-12-24 09:00 | 8.0328 | 8.4553 | 173.5489 | 3495.6792 | 52435.1873
2020-12-24 10:00 | 8.5945 | 9.0466 | 171.6408 | 4159.8129 | 62397.1941
2020-12-24 11:00 | 8.6032 | 9.0557 | 177.4768 | 4169.5501 | 62543.2511
2020-12-24 12:00 | 9.1932 | 9.6767 | 182.5325 | 4790.2299 | 71853.4478
2020-12-24 13:00 | 9.1167 | 9.5961 | 189.2358 | 4724.0345 | 70860.5176
2020-12-24 14:00 | 8.7853 | 9.2473 | 187.8196 | 4374.6632 | 65619.9476
2020-12-24 15:00 | 9.0197 | 9.4941 | 189.2971 | 4638.6893 | 69580.3389
2020-12-24 16:00 | 8.721 | 9.1796 | 192.1558 | 4302.2234 | 64533.3511
2020-12-24 17:00 | 8.3653 | 8.8053 | 190.9553 | 3890.397 | 58355.9555
2020-12-24 18:00 | 8.2377 | 8.671 | 185.9813 | 3738.8983 | 56083.4744
2020-12-24 19:00 | 8.6259 | 9.0796 | 186.6486 | 4195.1761 | 62927.6422
2020-12-24 20:00 | 8.8841 | 9.3513 | 190.6293 | 4485.933 | 67288.9945
2020-12-24 21:00 | 8.8762 | 9.343 | 192.8164 | 4477.0036 | 67155.0538
2020-12-24 22:00 | 9.2692 | 9.7567 | 194.0203 | 4856.0039 | 72840.0592
2020-12-24 23:00 | 9.0961 | 9.5745 | 203.6678 | 4706.211 | 70593.1652
2020-12-25 00:00 | 8.7319 | 9.1912 | 216.6908 | 4314.5487 | 64718.2303
2020-12-25 01:00 | 8.1939 | 8.6248 | 231.9078 | 3686.8286 | 55302.4294
2020-12-25 02:00 | 7.5772 | 7.9757 | 243.8827 | 2957.2711 | 44359.0668
2020-12-25 03:00 | 6.9661 | 7.3325 | 249.2996 | 2297.8787 | 34468.1808
2020-12-25 04:00 | 6.8625 | 7.2234 | 252.9033 | 2196.1929 | 32942.8939
2020-12-25 05:00 | 6.7616 | 7.1172 | 254.601 | 2097.2393 | 31458.5892
2020-12-25 06:00 | 6.7523 | 7.1075 | 254.5407 | 2088.17 | 31322.5507
2020-12-25 07:00 | 6.9227 | 7.2868 | 254.4606 | 2255.3059 | 33829.5886
2020-12-25 08:00 | 6.8087 | 7.1667 | 254.763 | 2143.4098 | 32151.1466
2020-12-25 09:00 | 6.5342 | 6.8779 | 257.4867 | 1888.8364 | 28332.5456
2020-12-25 10:00 | 6.2156 | 6.5425 | 251.2896 | 1616.541 | 24248.1148
2020-12-25 11:00 | 6.9368 | 7.3017 | 255.3966 | 2269.1642 | 34037.4625
2020-12-25 12:00 | 6.9377 | 7.3025 | 260.9363 | 2269.9648 | 34049.4719
2020-12-25 13:00 | 6.8811 | 7.243 | 273.8094 | 2214.4784 | 33217.1758
2020-12-25 14:00 | 8.1017 | 8.5278 | 283.5421 | 3577.4093 | 53661.1393
2020-12-25 15:00 | 7.3807 | 7.7689 | 292.2024 | 2738.4747 | 41077.121
2020-12-25 16:00 | 6.6911 | 7.043 | 288.1117 | 2028.092 | 30421.3793
2020-12-25 17:00 | 6.3041 | 6.6357 | 288.0689 | 1692.1732 | 25382.5984
2020-12-25 18:00 | 6.1724 | 6.4971 | 289.1036 | 1579.9573 | 23699.3591
2020-12-25 19:00 | 5.9852 | 6.3 | 293.6531 | 1442.0161 | 21630.2416
2020-12-25 20:00 | 5.6946 | 5.9941 | 297.7652 | 1228.483 | 18427.2452
2020-12-25 21:00 | 5.6408 | 5.9375 | 304.8858 | 1195.0023 | 17925.0347
2020-12-25 22:00 | 6.1615 | 6.4855 | 306.0684 | 1571.869 | 23578.0354
2020-12-25 23:00 | 5.774 | 6.0777 | 302.5498 | 1286.3958 | 19295.9363
2020-12-26 00:00 | 5.2937 | 5.5721 | 299.4861 | 978.7059 | 14680.5892
2020-12-26 01:00 | 5.0705 | 5.3372 | 291.5882 | 854.2552 | 12813.8287
2020-12-26 02:00 | 5.142 | 5.4125 | 288.2631 | 892.0689 | 13381.0332
2020-12-26 03:00 | 5.3801 | 5.6631 | 287.7577 | 1032.5331 | 15487.9963
2020-12-26 04:00 | 5.6271 | 5.923 | 283.087 | 1186.4432 | 17796.6485
2020-12-26 05:00 | 5.5575 | 5.8498 | 283.6071 | 1143.064 | 17145.9606
2020-12-26 06:00 | 5.1935 | 5.4667 | 277.6893 | 919.2766 | 13789.1488
2020-12-26 07:00 | 5.6154 | 5.9108 | 271.34 | 1179.1845 | 17687.768
2020-12-26 08:00 | 6.146 | 6.4692 | 277.6951 | 1560.4381 | 23406.5708
2020-12-26 09:00 | 5.4852 | 5.7737 | 280.5979 | 1098.0535 | 16470.802
2020-12-26 10:00 | 6.5029 | 6.8449 | 281.7455 | 1862.0909 | 27931.3631
2020-12-26 11:00 | 6.5717 | 6.9173 | 278.3951 | 1920.8628 | 28812.942
2020-12-26 12:00 | 6.2134 | 6.5402 | 283.2515 | 1614.6231 | 24219.3471
2020-12-26 13:00 | 6.2861 | 6.6167 | 280.5216 | 1676.7978 | 25151.9671
2020-12-26 14:00 | 6.5765 | 6.9223 | 271.6251 | 1924.9386 | 28874.0792
2020-12-26 15:00 | 7.2545 | 7.6361 | 270.368 | 2597.9876 | 38969.8139
2020-12-26 16:00 | 7.3263 | 7.7116 | 271.5459 | 2677.921 | 40168.8145
2020-12-26 17:00 | 7.097 | 7.4703 | 267.1506 | 2426.3017 | 36394.5256
2020-12-26 18:00 | 7.1466 | 7.5225 | 264.7946 | 2477.7769 | 37166.653
2020-12-26 19:00 | 7.3571 | 7.744 | 265.5162 | 2712.1595 | 40682.3919
2020-12-26 20:00 | 7.2374 | 7.6181 | 270.7225 | 2578.9368 | 38684.0513
2020-12-26 21:00 | 6.7986 | 7.1562 | 275.6982 | 2133.5433 | 32003.15
2020-12-26 22:00 | 7.152 | 7.5281 | 276.6264 | 2483.7672 | 37256.5079
2020-12-26 23:00 | 6.9615 | 7.3277 | 274.3077 | 2293.3878 | 34400.8166
2020-12-27 00:00 | 6.8404 | 7.2001 | 278.5397 | 2174.537 | 32618.0546
2020-12-27 01:00 | 6.3264 | 6.6592 | 281.276 | 1711.2489 | 25668.7341
2020-12-27 02:00 | 5.4057 | 5.69 | 280.2519 | 1048.486 | 15727.2896
2020-12-27 03:00 | 4.5604 | 4.8003 | 276.9015 | 600.7144 | 9010.7164
2020-12-27 04:00 | 4.1013 | 4.317 | 270.4067 | 409.5861 | 6143.7912
2020-12-27 05:00 | 3.9939 | 4.2039 | 260.7827 | 369.7899 | 5546.8485
2020-12-27 06:00 | 3.8287 | 4.0301 | 252.7288 | 308.5794 | 4628.6912
2020-12-27 07:00 | 3.2315 | 3.4015 | 243.0131 | 133.9205 | 2008.8073
2020-12-27 08:00 | 2.5694 | 2.7045 | 228.4791 | 0 | 0
2020-12-27 09:00 | 2.5273 | 2.6602 | 202.2067 | 0 | 0
2020-12-27 10:00 | 2.8051 | 2.9526 | 180.412 | 0 | 0
2020-12-27 11:00 | 3.7931 | 3.9926 | 172.0601 | 295.8801 | 4438.2016
2020-12-27 12:00 | 4.4716 | 4.7067 | 164.9438 | 561.2424 | 8418.6366
2020-12-27 13:00 | 5.2994 | 5.5782 | 153.8461 | 982.2736 | 14734.1039
2020-12-27 14:00 | 6.6108 | 6.9584 | 146.8908 | 1954.2555 | 29313.8331
2020-12-27 15:00 | 7.778 | 8.1871 | 150.0215 | 3193.6461 | 47904.692
2020-12-27 16:00 | 8.1818 | 8.6122 | 153.239 | 3672.5257 | 55087.8858
2020-12-27 17:00 | 8.4963 | 8.9431 | 150.0014 | 4045.8525 | 60687.7868
2020-12-27 18:00 | 8.9191 | 9.3882 | 144.794 | 4525.39 | 67880.8494
2020-12-27 19:00 | 9.3994 | 9.8938 | 145.1534 | 4968.6843 | 74530.2638
2020-12-27 20:00 | 10.1436 | 10.6771 | 144.867 | 5415.6522 | 81234.7824
2020-12-27 21:00 | 10.5317 | 11.0856 | 145.1619 | 5558.3372 | 83375.0575
2020-12-27 22:00 | 10.783 | 11.3502 | 148.8146 | 5618.1343 | 84272.0139
2020-12-27 23:00 | 10.6247 | 11.1835 | 148.2773 | 5580.4637 | 83706.9554
2020-12-28 00:00 | 10.9443 | 11.5199 | 146.1241 | 5653.8698 | 84808.0472
2020-12-28 01:00 | 11.2318 | 11.8225 | 145.1154 | 5682.3174 | 85234.7611
2020-12-28 02:00 | 11.3448 | 11.9415 | 143.5189 | 5693.4997 | 85402.496
2020-12-28 03:00 | 11.4216 | 12.0223 | 142.1615 | 5699.0446 | 85485.6687
2020-12-28 04:00 | 11.4627 | 12.0656 | 139.2112 | 5699.1312 | 85486.9682
2020-12-28 05:00 | 11.5943 | 12.2041 | 137.6136 | 5699.4081 | 85491.1219
2020-12-28 06:00 | 11.8578 | 12.4815 | 136.8753 | 5699.963 | 85499.4451
2020-12-28 07:00 | 12.0988 | 12.7351 | 136.6232 | 5700 | 85500
2020-12-28 08:00 | 12.2212 | 12.864 | 136.3585 | 5700 | 85500
2020-12-28 09:00 | 12.4151 | 13.0681 | 137.6966 | 5700 | 85500
2020-12-28 10:00 | 10.4192 | 10.9672 | 139.0187 | 5526.4815 | 82897.2223
2020-12-28 11:00 | 10.7864 | 11.3537 | 137.0913 | 5618.9294 | 84283.9415
2020-12-28 12:00 | 12.5268 | 13.1857 | 137.2525 | 5700 | 85500
2020-12-28 13:00 | 11.9084 | 12.5347 | 140.337 | 5700 | 85500
2020-12-28 14:00 | 11.8788 | 12.5035 | 139.3511 | 5700 | 85500
2020-12-28 15:00 | 12.2708 | 12.9162 | 140.4256 | 5700 | 85500
2020-12-28 16:00 | 12.0984 | 12.7348 | 143.3133 | 5700 | 85500
2020-12-28 17:00 | 11.8605 | 12.4843 | 145.2053 | 5699.9686 | 85499.5284
2020-12-28 18:00 | 11.1886 | 11.7771 | 146.6465 | 5678.0479 | 85170.7188
2020-12-28 19:00 | 10.6281 | 11.1871 | 146.8954 | 5581.2764 | 83719.1462
2020-12-28 20:00 | 10.649 | 11.2091 | 144.9477 | 5586.2567 | 83793.8501
2020-12-28 21:00 | 10.7177 | 11.2814 | 144.0035 | 5602.6008 | 84039.0123
2020-12-28 22:00 | 10.1286 | 10.6613 | 145.9619 | 5409.6318 | 81144.477
2020-12-28 23:00 | 10.0747 | 10.6046 | 146.1788 | 5387.963 | 80819.445
2020-12-29 00:00 | 10.2789 | 10.8195 | 145.9774 | 5470.0658 | 82050.9874
2020-12-29 01:00 | 10.479 | 11.0301 | 148.6337 | 5545.8111 | 83187.1664
2020-12-29 02:00 | 10.9677 | 11.5446 | 147.8396 | 5656.1916 | 84842.8745
2020-12-29 03:00 | 11.5414 | 12.1484 | 144.9381 | 5699.2967 | 85489.451
2020-12-29 04:00 | 11.7836 | 12.4034 | 149.2578 | 5699.8067 | 85497.1005
2020-12-29 05:00 | 11.7733 | 12.3925 | 150.6025 | 5699.785 | 85496.7757
2020-12-29 06:00 | 12.0374 | 12.6705 | 147.2673 | 5700 | 85500
2020-12-29 07:00 | 12.2913 | 12.9377 | 148.2484 | 5700 | 85500
2020-12-29 08:00 | 12.2975 | 12.9442 | 151.6335 | 5700 | 85500
2020-12-29 09:00 | 12.1278 | 12.7656 | 153.8471 | 5700 | 85500
2020-12-29 10:00 | 10.2988 | 10.8404 | 160.5605 | 5478.0495 | 82170.7421
2020-12-29 11:00 | 10.2199 | 10.7574 | 162.7783 | 5446.3387 | 81695.08
2020-12-29 12:00 | 9.539 | 10.0407 | 169.2062 | 5079.7449 | 76196.1732
2020-12-29 13:00 | 8.8918 | 9.3594 | 173.6309 | 4494.6003 | 67419.0042
2020-12-29 14:00 | 7.7618 | 8.17 | 175.4642 | 3174.4665 | 47616.9971
2020-12-29 15:00 | 7.5544 | 7.9518 | 182.3622 | 2931.964 | 43979.4601
2020-12-29 16:00 | 7.5511 | 7.9483 | 192.7173 | 2928.2492 | 43923.7376
2020-12-29 17:00 | 6.743 | 7.0976 | 198.7166 | 2078.992 | 31184.8807
2020-12-29 18:00 | 6.4043 | 6.7412 | 202.1727 | 1777.8306 | 26667.459
2020-12-29 19:00 | 5.9769 | 6.2912 | 199.1611 | 1435.8472 | 21537.7078
2020-12-29 20:00 | 5.7188 | 6.0196 | 190.4688 | 1245.6985 | 18685.4777
2020-12-29 21:00 | 5.656 | 5.9535 | 184.8813 | 1204.4455 | 18066.6824
2020-12-29 22:00 | 4.5217 | 4.7595 | 185.5211 | 583.5001 | 8752.5012
2020-12-29 23:00 | 4.1485 | 4.3667 | 172.5549 | 427.0857 | 6406.286
2020-12-30 00:00 | 4.9306 | 5.1899 | 150.6508 | 780.3276 | 11704.9143
2020-12-30 01:00 | 5.5242 | 5.8148 | 143.9783 | 1122.3403 | 16835.1042
2020-12-30 02:00 | 5.4442 | 5.7305 | 137.7231 | 1072.4836 | 16087.2534
2020-12-30 03:00 | 5.8979 | 6.2081 | 135.1195 | 1377.6892 | 20665.3375
2020-12-30 04:00 | 6.2598 | 6.589 | 136.5859 | 1654.2669 | 24814.0037
2020-12-30 05:00 | 6.772 | 7.1282 | 141.7875 | 2107.456 | 31611.8405
2020-12-30 06:00 | 6.6713 | 7.0222 | 146.8893 | 2008.7056 | 30130.5845
2020-12-30 07:00 | 6.2795 | 6.6098 | 149.6708 | 1671.1589 | 25067.3834
2020-12-30 08:00 | 6.5186 | 6.8614 | 151.8537 | 1875.4561 | 28131.8421
2020-12-30 09:00 | 7.0342 | 7.4041 | 158.0458 | 2364.6552 | 35469.8283
2020-12-30 10:00 | 6.7348 | 7.089 | 158.022 | 2070.9393 | 31064.0895
2020-12-30 11:00 | 6.4624 | 6.8023 | 161.6931 | 1827.4904 | 27412.3557
2020-12-30 12:00 | 6.1988 | 6.5248 | 159.2513 | 1602.1455 | 24032.1823
2020-12-30 13:00 | 6.4739 | 6.8144 | 149.0211 | 1837.288 | 27559.3203
2020-12-30 14:00 | 7.4934 | 7.8876 | 148.6508 | 2864.0332 | 42960.4986
2020-12-30 15:00 | 7.9946 | 8.4151 | 156.5539 | 3450.3481 | 51755.2214
2020-12-30 16:00 | 7.8525 | 8.2655 | 169.4822 | 3281.9911 | 49229.867
2020-12-30 17:00 | 7.8655 | 8.2792 | 172.461 | 3297.4049 | 49461.0735
2020-12-30 18:00 | 7.7294 | 8.1359 | 174.947 | 3136.0639 | 47040.9587
2020-12-30 19:00 | 7.5557 | 7.9531 | 180.2244 | 2933.4098 | 44001.1465
2020-12-30 20:00 | 7.4109 | 7.8007 | 182.7971 | 2772.1619 | 41582.4283
2020-12-30 21:00 | 7.1994 | 7.5781 | 181.7278 | 2536.6043 | 38049.0648
2020-12-30 22:00 | 6.6407 | 6.99 | 175.5685 | 1979.8927 | 29698.3908
2020-12-30 23:00 | 6.6498 | 6.9995 | 173.0462 | 1987.596 | 29813.9399
2020-12-31 00:00 | 6.57 | 6.9155 | 172.0753 | 1919.402 | 28791.0307
2020-12-31 01:00 | 6.8147 | 7.1732 | 171.6602 | 2149.3838 | 32240.7575
2020-12-31 02:00 | 6.6486 | 6.9983 | 175.7125 | 1986.5873 | 29798.8088
2020-12-31 03:00 | 6.3383 | 6.6717 | 181.1162 | 1721.3881 | 25820.8216
2020-12-31 04:00 | 5.9846 | 6.2994 | 182.081 | 1441.5832 | 21623.7482
2020-12-31 05:00 | 5.9475 | 6.2603 | 191.1551 | 1414.1993 | 21212.9892
2020-12-31 06:00 | 5.2653 | 5.5422 | 199.8098 | 960.9812 | 14414.7186
2020-12-31 07:00 | 4.6273 | 4.8706 | 200.0182 | 630.407 | 9456.1046
2020-12-31 08:00 | 3.8481 | 4.0505 | 193.6621 | 315.7694 | 4736.5412
2020-12-31 09:00 | 3.984 | 4.1935 | 185.4754 | 366.113 | 5491.6943
2020-12-31 10:00 | 4.8154 | 5.0687 | 171.5711 | 719.4913 | 10792.3695
2020-12-31 11:00 | 4.5746 | 4.8152 | 166.1052 | 607.0119 | 9105.1791
2020-12-31 12:00 | 4.1306 | 4.3478 | 154.1062 | 420.4378 | 6306.5665
2020-12-31 13:00 | 4.3239 | 4.5513 | 146.5492 | 495.6523 | 7434.7843
2020-12-31 14:00 | 4.9022 | 5.1601 | 142.213 | 765.3539 | 11480.3082
2020-12-31 15:00 | 5.6789 | 5.9776 | 144.5001 | 1218.7423 | 18281.1344
2020-12-31 16:00 | 6.1945 | 6.5203 | 148.7328 | 1598.4813 | 23977.219
2020-12-31 17:00 | 6.5195 | 6.8624 | 150.8593 | 1876.275 | 28144.1252
2020-12-31 18:00 | 6.8682 | 7.2294 | 149.4124 | 2201.7968 | 33026.9516
2020-12-31 19:00 | 7.2822 | 7.6652 | 152.7657 | 2628.8073 | 39432.1089
2020-12-31 20:00 | 7.2088 | 7.5879 | 162.4343 | 2547.0094 | 38205.1411
2020-12-31 21:00 | 6.7725 | 7.1287 | 165.4378 | 2107.9721 | 31619.582
2020-12-31 22:00 | 6.8213 | 7.1801 | 155.934 | 2155.8616 | 32337.9246
2020-12-31 23:00 | 6.5402 | 6.8842 | 144.6867 | 1893.9537 | 28409.3055